## MCH- KTM GHDU -measurement
DETAILED MEASUREMENT
Name of work : CONVERSION OF WARD # 27 IN TO GERIATRIC HIGH DEPENDENCY UNIT AT MEDICAL COLLEGE KOTTAYAM DISTRICT.
Part I A
Item No | Code No. | Description of Item | Unit | Nos. | Length | Breadth | Height | Quantity | Rate | Amount | Remarks
SUB HEAD: I EARTH WORK
1 | 2.8.1 | Earth work in excavation in foundation trenches or drains ( not exceeding 1.5m in width or 10 sqm on plan ) including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of urplus excavated soil as directed, within a lead of 50 m :- All kinds of soil . | cum |  |  |  |  | 14.4 | 130.8 | 1883.52
|  | For new access from passage | cum | 1 | 1.75 | 0.6 | 1 | 1.05
|  | For new access from passage | cum | 1 | 3.25 | 0.6 | 1 | 1.95
|  | Vacuum plant | cum | 2 | 4.71 | 0.6 | 1 | 5.652
|  | Vacuum plant | cum | 2 | 2.51 | 0.6 | 1 | 3.012
|  | For new access from passage to gas storage | cum | 1 | 6.4 | 0.6 | 0.6 | 2.304 |  |  |  |  | 8972
|  | For new access from passage to gas storage | cum | 1 | 1.2 | 0.6 | 0.6 | 0.432
2 | 2.27 | Supplying and filling in plinth with river sand/quarry dust under floors including watering, ramming consolidating and dressing complete. | cum |  |  |  |  | 16.5359 | 749.3 | 12390.3709
|  | For new access from passage | cum | 1 | 7.25 | 3.6 | 0.38 | 9.918
|  | For new access from passage to gas storage | cum | 1 | 6.4 | 1.2 | 0.38 | 2.9184 |  |  |  |  | 8972
|  | Vacuum plant | cum | 1 | 3.66 | 2.66 | 0.38 | 3.6995
3 | 2.25 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth: consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m | cum |  |  |  |  | 8.1648 | 83.8 | 684.2102
|  | For new access from passage | cum | 1 | 1.75 | 0.6 | 0.7 | 0.735
|  | For new access from passage | cum | 1 | 3.25 | 0.6 | 0.7 | 1.365
|  | Vacuum plant | cum | 2 | 4.71 | 0.6 | 0.7 | 3.9564
|  | Vacuum plant | cum | 2 | 2.51 | 0.6 | 0.7 | 2.1084
|  | SUB HEAD : II PLAIN CEMENT CONCRETE | [7 empty] | 0
4 | 4.1.10 | Providing and laying in position cement concrete of specified grade excluding the cost of centring and shuttering - All work upto plinth : 1 : 5 : 10 (1 Cement : 5 coarse sand :10 graded stone aggregate 40mm nominal size) | cum |  |  |  |  | 9.4574 | 3357.4 | 31752.2748
|  | For new access from passage | cum | 1 | 1.75 | 0.6 | 0.1 | 0.105
|  | For new access from passage | cum | 1 | 3.25 | 0.6 | 0.1 | 0.195
|  | For new access from passage Floor | cum | 1 | 7.5 | 4 | 0.1 | 3
|  | Vacuum plant | cum | 2 | 4.71 | 0.6 | 0.1 | 0.5652
|  | Vacuum plant | cum | 2 | 2.51 | 0.6 | 0.1 | 0.3012
|  | Vacuum plant floor | cum | 1 | 3.9 | 3 | 0.1 | 1.17
| add | Cylinder storage passage floor | cum | 1 | 6.4 | 1.5 | 0.1 | 0.96
|  | cylinder store | cum | 1 | 4 | 2 | 0.1 | 0.8
| add | RO plant foundation | cum | 1 | 3.85 | 1.6 | 0.3 | 1.848
| add | RO plant foundation | cum | 1 | 1.9 | 0.9 | 0.3 | 0.513
5 | 11.3.1 | Cement concrete flooring 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate) finished with a floating coat of neat cement including cement slurry, but excluding the cost of nosing of steps etc. complete. 11.3.1 40mm thick with 20mm nominal size stone aggregate. | Sqm |  |  |  |  | 12 | 280.05 | 3360.6
|  | Vacuum plant floor | Sqm | 1 | 4 | 3 | 1 | 12
6 | 4.17 | Making plinth protection 50 mm thick of cement concrete 1:3:6 (1 cement :3 coarse sand: 6 graded stone aggregate 20 mm nominal size )over 75 mm bed of dry brick ballast 40 mm nominal size well rammed and consolidated and grouted with fine sand including finishing the top smooth. | Sqm |  |  |  |  | 8.04 | 338.75 | 2723.55
|  | Vacuum plant | Sqm | 2 | 5.2 | 0.6 | 1 | 6.24
|  | Vacuum plant floor | Sqm | 1 | 3 | 0.6 | 1 | 1.8
|  | SUB HEAD III : REINFORCED CEMENT CONCRETE | [7 empty] | 0
7 | 5.1.2 | Providing and laying in position specified grade of reinforced cement concrete excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level :1.5:3 (1 cement : 1.5 coarse sand : 3 graded stone aggregate 20 mm nominal size) | cum |  |  |  |  | 1.422 | 5094.85 | 7244.8767
|  | Plinth level concrete | cum | 2 | 4.9 | 0.45 | 0.2 | 0.882
|  | Plinth level concrete | cum | 2 | 3 | 0.45 | 0.2 | 0.54
8 | 5.1.2+ (5.3- 5.1.3) | Reinforced cement concrete work in beams, suspended floors, roofs having slope upto 15°, landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases upto floor five level including the cost of centring, shuttering, finishing and excluding the cost of reinforcement with 1:1.5:3 (1 cement : 1.5 coarse sand: 3 graded stone aggregate 20 mm nominal size). | cum |  |  |  |  | 7.0063 | 5885.5 | 41235.6964
|  | Vacuum plant wall top concrete | cum | 2 | 4.46 | 0.23 | 0.2 | 0.41032
|  | Vacuum plant wall top concrete | cum | 2 | 3 | 0.23 | 0.2 | 0.276
|  | Plinth level concrete | cum | 2 | 4.9 | 1 | 0.2 | 1.96
|  | Plinth level concrete | cum | 2 | 4 | 1 | 0.2 | 1.6
|  | Plinth level concrete | cum | 2 | 3.9 | 1 | 0.2 | 1.56
|  | Plinth level concrete | cum | 2 | 3 | 1 | 0.2 | 1.2
9 | 5.9.5 | Centering and shuttering including strutting, propping etc. and removal of form for : Lintels, beams, plinth beams, girders, bressumers and cantilevers | Sqm |  |  |  |  | 9.917 | 262.25 | 2600.7333
|  | Vacuum plant wall top concrete | Sqm | 2 | 4.46 | 1 | 0.2 | 1.784
|  | Vacuum plant wall top concrete | Sqm | 2 | 3.46 | 1 | 0.2 | 1.384
|  | Vacuum plant wall top concrete | Sqm | 2 | 4 | 1 | 0.2 | 1.6
|  | Vacuum plant wall top concrete | Sqm | 2 | 3 | 1 | 0.2 | 1.2
|  | Vacuum plant lintel over door | Sqm | 2 | 1.96 | 1 | 0.2 | 0.784
|  | Vacuum plant lintel over door bottom | Sqm | 1 | 1.5 | 1 | 0.23 | 0.345
|  | Vacuum plant lintel over window | Sqm | 6 | 1.66 | 1 | 0.2 | 1.992
|  | Vacuum plant lintel over door bottom | Sqm | 3 | 1.2 | 1 | 0.23 | 0.828
10 | 5.22.6 | Reinforcement for reinforced cement concrete works including straightening, cutting, bending, binding and placing in position all complete:- TMT bars | kg | 8.4283 | 120 |  |  | 1011.3984 | 62.25 | 62959.5504 |  |  | 23136.3 | 29224.9
|  | SUB HEAD IV : BRICK WORK | [7 empty] | 0 |  |  | 4.1529
11 | 6.4.2 | Brick work with bricks of class designation 75 in superstructure above plinth level upto floor V level.cement mortar 1 : 6 ( 1 cement : 6 coarse sand ). | cum |  |  |  |  | 33.9862 | 3876.15 | 131735.5316
|  | Vacuum plant wall | cum | 2 | 4.5 | 0.23 | 2.5 | 5.175
|  | Vacuum plant wall | cum | 2 | 3 | 0.23 | 2.5 | 3.45
|  | deduction for door Vacuum plant wall | cum | 1 | 1 | 0.23 | -2 | -0.46
|  | deduction for window Vacuum plant wall | cum | 3 | 1.2 | 0.23 | -1.3 | -1.0764
|  | connection passage | cum | 1 | 1.7 | 0.23 | 3.2 | 1.2512
|  | Vacuum plant wall | cum | 2 | 3.25 | 0.23 | 3.2 | 4.784
|  | Vacuum plant gable wall | cum | 2 | 3.46 | 0.23 | 0.5 | 0.7958
|  | Partition wall for dialisys room | cum | 1 | 5.1 | 0.23 | 3.2 | 3.7536
|  | deduction for door | cum | 1 | 1 | 0.23 | -2.1 | -0.483
|  | Partition wall for cylinder room | cum | 1 | 5 | 0.23 | 3.2 | 3.68
|  | deduction for door | cum | 1 | 1 | 0.23 | -2.1 | -0.483
|  | Passage wall for cylinder room | cum | 1 | 6.4 | 0.23 | 1.2 | 1.7664
|  | Passage wall for cylinder room | cum | 1 | 1.2 | 0.23 | 1.2 | 0.3312
|  | Passage wall for cylinder room piller | cum | 4 | 0.23 | 0.23 | 2.3 | 0.48668
|  | ICU ward partiotion for passage | cum | 1 | 15.64 | 0.23 | 3.25 | 11.6909
|  | ICU ward partiotion for passage deduct for door | cum | 2 | 1.2 | 0.23 | -2.1 | -1.1592
|  | closing door opening doctors room | cum | 1 | 1 | 0.23 | 2.1 | 0.483
12 | 6.13.2 | Half brick masonry with bricks of class designation 75 in super structure & above plinth up to floor V level in cement mortar 1 : 4 ( 1 cement : 4 coarse sand ). | Sqm |  |  |  |  | 27.04 | 476.85 | 12894.024
|  | closing door opening doctors room, RO plant | Sqm | 5 | 1.6 | 1 | 2.1 | 16.8
|  | closing ventilator opening dialysis room, RO plant | Sqm | 4 | 1.6 | 1 | 1.6 | 10.24
13 | 6.15 | Extra for providing and placing in position 2 Nos 6 mm dia M.S. bars at every third course of half brick masonary ( with F.P.S. bricks). | Sqm |  |  |  |  | 27.04 | 63.3 | 1711.632
|  | closing door opening doctors room, RO plant | Sqm | 5 | 1.6 | 1 | 2.1 | 16.8
|  | closing ventilator opening dialysis room, RO plant | Sqm | 4 | 1.6 | 1 | 1.6 | 10.24
|  | SUB HEAD :V MARBLE WORK | [7 empty] | 0
14 | 8.2.2.2 | Providing and fixing 18 mm thick mirror polished, machine cut for kitchen platforms, vanity counters facias and similar locations of required size of approved shade, colour and texture laid over 20 mm thick base cement mortar 1 : 4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing etc. complete at all levels :- Granite black area of slab : | Sqm |  |  |  |  | 15.97 | 3083.4 | 49241.898
| add | Sink bottom | Sqm | 1 | 2 | 1 | 0.5 | 1
| add | Sink side | Sqm | 2 | 2 | 1 | 0.9 | 3.6
| add | Sink side | Sqm | 2 | 0.6 | 1 | 0.9 | 1.08
| add | Dialisys counter slab at north | Sqm | 1 | 5.5 | 1 | 0.9 | 4.95
| add | top | Sqm | 1 | 2 | 1 | 0.2 | 0.4
| add | top | Sqm | 2 | 0.75 | 1 | 0.2 | 0.3
| add | Nurses station counter top | Sqm | 1 | 4.6 | 1 | 0.8 | 3.68
| add | Nurses station counter top | Sqm | 1 | 1.2 | 1 | 0.8 | 0.96
15 | 8.3.2 | Extra for providing edge moulding to 18mm thick marble counters, Vanities etc. including machine polishing to dege to give high gloss finish etc. complete as per design approved by Engineer-in-charge:- Granite work | mtr. |  |  |  |  | 24.18 | 178.75 | 4322.175
| add | top out side | mtr. | 2 | 2 | 1 | 1 | 4
| add | top inside | mtr. | 2 | 0.75 | 1 | 1 | 1.5
| add | top inside | mtr. | 2 | 1 | 1 | 1 | 2
| add | top out side | mtr. | 2 | 0.95 | 1 | 1 | 1.9
| add | Dialisys counter slab at north | mtr. | 1 | 5.5 | 1 | 1 | 5.5
| add | Nurses station counter top | mtr. | 2 | 4.6 | 1 | 0.8 | 7.36
| add | Nurses station counter top | mtr. | 2 | 1.2 | 1 | 0.8 | 1.92
|  | SUB HEAD VI : STONE WORK | [7 empty] | 0
16 | 7.1.1 | Random rubble masonry with hard stone in foundation and plinth including levelling up with cement concrete 1:6:12 (1 cement : 6 coarse sand : 12 graded stone aggregate 20 mm nominal size) upto plinth level with : Cement mortar 1:6 (1 cement : 6 coarse sand | cum |  |  |  |  | 15.4246 | 3059.2 | 47187.0893
|  | For new access from passage | cum | 1 | 1.75 | 0.6 | 0.6 | 0.63
|  | For new access from passage | cum | 1 | 3.25 | 0.6 | 0.6 | 1.17
|  | Vacuum plant | cum | 2 | 4.71 | 0.6 | 0.6 | 3.3912
|  | Vacuum plant | cum | 2 | 2.51 | 0.6 | 0.6 | 1.8072
|  | For new access from passage basement | cum | 1 | 2 | 0.45 | 0.45 | 0.405
|  | For new access from passage basement | cum | 1 | 3.5 | 0.45 | 0.45 | 0.70875
|  | Vacuum plant basement | cum | 2 | 4.8 | 0.45 | 0.45 | 1.944
|  | Vacuum plant basement | cum | 2 | 2.7 | 0.45 | 0.45 | 1.0935 |  |  |  |  | 5833
|  | For new access from passage to gas storage | cum | 1 | 6.4 | 0.6 | 0.6 | 2.304 |  |  |  |  | 8972
|  | For new access from passage to gas storage | cum | 1 | 1.2 | 0.6 | 0.6 | 0.432
|  | For new access from passage to gas storage | cum | 1 | 6.4 | 0.45 | 0.45 | 1.296
|  | For new access from passage to gas storage | cum | 1 | 1.2 | 0.45 | 0.45 | 0.243
|  | SUB HEAD VII : STEEL WORK | [7 empty] | 0
17 | 9.48.2 | Providing and fixing M.S. grills of required pattern in frames of windows etc. with M.S. flats, square or round bars etc. including priming coat with approved steel primer all complete. 9.48.2 Fixed to openings /wooden frames with rawl plugs screws etc. | kg |  |  |  |  | 715.05 | 98.2 | 70217.91
|  | Window for vacuum plant | kg | 3 | 1.2 | 1.3 | 21 | 98.28
|  | Window for new passage | kg | 2 | 1.2 | 1.3 | 21 | 65.52
|  | door for vacuum plant | kg | 1 | 1.5 | 2.1 | 21 | 66.15
|  | door for new passage | kg | 1 | 3 | 2.1 | 21 | 132.3
|  | For new access from passage to gas storage | kg | 1 | 4.8 | 2 | 21 | 201.6
|  | For new access from passage to gas storage | kg | 1 | 1.2 | 2 | 21 | 50.4
|  | For new gate from passage to gas storage | kg | 2 | 1.2 | 2 | 21 | 100.8
18 | 10.16.1 | Steel work in built up tubular ( round, square or rectangular hollow tubes etc.) trusses etc., including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer, including welding and bolted with special shaped washers etc. complete. 10.16.1 Hot finished welded type tubes | kg |  |  |  |  | 352.7784 | 85.1 | 30021.4418
|  | 25 dia. Pipe | kg | 12 | 2.4 | 1 | 2 | 57.6
|  | 25 dia. Pipe | kg | 12 | 1.9 | 1 | 2 | 45.6
|  | 25 dia. Pipe | kg | 3 | 2.8 | 1 | 2 | 16.8
|  | 25 dia. Pipe | kg | 3 | 4.5 | 1 | 2 | 27
|  | 32 dia. Pipe purlin | kg | 6 | 6 | 1 | 2.57 | 92.52
|  | 20 dia. Pipe cross pipe rafter | kg | 42 | 0.18 | 1 | 1.39 | 10.5084
|  | 20 dia. Pipe diagonal pipe rafter | kg | 36 | 0.35 | 1 | 1.39 | 17.514
|  | 20 dia. Pipe cross pipe brazing | kg | 30 | 0.18 | 1 | 1.39 | 7.506
|  | 20 dia. Pipe diagonal pipe brazing | kg | 3 | 0.6 | 1 | 1.39 | 2.502
|  | Flat 50x6mm | kg | 12 | 0.4 | 1 | 2.4 | 11.52
|  | Angle 50x50x6 | kg | 18 | 0.1 | 1 | 4.5 | 8.1
|  | Base plate 300x300x12mm thick | kg | 6 | 0.3 | 0.3 | 94.2 | 50.868
|  | Anchor bar16mm dia.300mm | kg | 6 | 0.5 | 1 | 1.58 | 4.74
|  | SUB HEAD VIII : FLOORING | [7 empty] | 0
19 | LMR | Providing and fixing Ist quality ceramic glazed joint free wall tiles minimum thickness 8MM of approved make JOHNSON, NITCO, ORIENT, , KAJARIA or approved make, in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete. Size 450x300mm | Sqm |  |  |  |  | 483.7976 | 1363 | 659416.1288
|  | Ward wall | Sqm | 2 | 15.7 | 1 | 3.2 | 100.48
|  | Ward wall | Sqm | 2 | 10.7 | 1 | 3.2 | 68.48
|  | ICU ward partiotion for passage | Sqm | 2 | 15.64 | 1 | 3.2 | 100.096
|  | ICU ward partiotion for passage deduct for door | Sqm | 4 | 1.2 | 0.23 | -2.1 | -2.3184
|  | Ward columns | Sqm | 12 | 0.5 | 1 | 3.2 | 19.2
|  | Ward columns projection | Sqm | 16 | 0.2 | 1 | 3.2 | 10.24
|  | deduction for door | Sqm | 2 | 1.2 | 1 | -2.1 | -5.04
|  | deduction for window | Sqm | 6 | 1.5 | 1 | -1.3 | -11.7
|  | Ward entrance reception room wall | Sqm | 2 | 4.9 | 1 | 3.2 | 31.36
|  | Ward entrance reception room wall | Sqm | 2 | 5.2 | 1 | 3.2 | 33.28
|  | dialisys room | Sqm | 2 | 4 | 1 | 3.2 | 25.6
|  | dialisys room | Sqm | 2 | 5.3 | 1 | 3.2 | 33.92
|  | deduction for door | Sqm | 1 | 1 | 1 | -2.1 | -2.1
|  | deduction for window | Sqm | 4 | 1.5 | 1 | -1.3 | -7.8
|  | Isolation / VIP room | Sqm | 2 | 7.7 | 1 | 3.2 | 49.28
|  | Isolation / VIP room | Sqm | 2 | 5.3 | 1 | 3.2 | 33.92
|  | Isolation / VIP room toilet wall | Sqm | 2 | 2.3 | 1 | 1.5 | 6.9
20 | 11.36 | Providing and fixing Ist quality ceramic glazed joint free wall tiles conforming to IS: 15622 Of thickness 5MM of approved make JOHNSON, NITCO, ORIENT, , KAJARIA or approved make, in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) sand jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete. Size | Sqm |  |  |  |  | 258.295 | 724.25 | 187070.1537 | rate Rs 1363 |  | 1540
|  | Bystanders room | Sqm | 2 | 4 | 1 | 1.7 | 13.6 |  |  |  |  | 100 | 4304
|  | Bystanders room | Sqm | 2 | 3 | 1 | 1.7 | 10.2 |  |  |  |  | 200
|  | Nurses rest room | Sqm | 2 | 3.8 | 1 | 1.7 | 12.92 |  |  |  |  | 400
|  | Nurses rest room | Sqm | 2 | 3 | 1 | 1.7 | 10.2 |  |  |  |  | 700 | 9100 | 6370000
|  | Nurses rest room toilet | Sqm | 2 | 1.45 | 1 | 1.7 | 4.93 |  |  |  |  | 700 | 286 | 200200
|  | Nurses rest room toilet | Sqm | 2 | 1.35 | 1 | 1.7 | 4.59 |  |  |  |  | total |  | 6570200
|  | Cilinder storage area | Sqm | 2 | 5 | 1 | 1.7 | 17 |  |  |  |  | water spply | 12% | 788424
|  | Cilinder storage area | Sqm | 2 | 3.8 | 1 | 1.7 | 12.92 |  |  |  |  | inter electr | 12.5% | 821275
|  | dialisys R O Plant room | Sqm | 2 | 3.6 | 1 | 1.7 | 12.24
|  | dialisys R O Plant room | Sqm | 2 | 5.3 | 1 | 1.7 | 18.02
|  | toilet block | Sqm | 12 | 1.5 | 1 | 1.7 | 30.6 |  |  |  |  | telephone | 0.5% | 32851
|  | toilet block | Sqm | 12 | 1.3 | 1 | 1.7 | 26.52 |  |  |  |  | tank | 3000 | 27000
|  | toilet block passage | Sqm | 2 | 4.15 | 1 | 1.7 | 14.11 |  |  |  |  | total |  | 8239750
|  | toilet block door deduction | Sqm | 6 | 0.75 | 1 | -1.7 | -7.65 |  |  |  |  | add 25% | 25% | 2059937.5
|  | Passage near nurses room | Sqm | 1 | 12 | 1 | 1.7 | 20.4 |  |  |  |  | total |  | 10299687.5
|  | Passage near nurses room | Sqm | 1 | 8.35 | 1 | 1.7 | 14.195 |  |  |  |  | add 5%contigency | 5% | 514984.375
|  | New Passage | Sqm | 2 | 7.5 | 1 | 1.7 | 25.5 |  |  |  |  | total |  | 10814671.875
|  | deduction for window | Sqm | 15 | 0.8 | 1 | -0.5 | -6 |  |  |  |  | add consultancy8% | 8% | 865173.75
|  | New Passage to gas storage area | Sqm | 2 | 6.4 | 1 | 1.5 | 19.2 |  |  |  |  | total |  | 11329656.25
|  | New Passage to gas storage area | Sqm | 1 | 1.2 | 1 | 1.5 | 1.8 |  |  |  |  | total |  | 12194830
|  | Wash sink outer wall | Sqm | 1 | 2 | 1 | 1.5 | 3 |  |  |  |  | total |  | 23009501.875
21 | 11.37 | Providing and laying Ceramic glazed joint free floor tiles of size 400x400 mm (thickness to be pecified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make JOHNSON, NITCO, ORIENT, , KAJARIA etc in colours such as White, Ivory, Grey, Fume Red Brown, laid on 20 mm thick cement mortar 1:4 (1 Cement : 4 Coarse sand), including pointing the joints with white cement and matching pigment etc., complete | Sqm |  |  |  |  | 42.4 | 764.55 | 32416.92
|  | Bystanders room | Sqm | 1 | 3 | 4 | 1 | 12
|  | Nurses rest room | Sqm | 1 | 3 | 3.8 | 1 | 11.4
|  | Cilinder storage area & toilet | Sqm | 1 | 5 | 3.8 | 1 | 19
22 | 11.37 | Providing and laying Ceramic Unglazed joint free floor tiles of size 300x300 mm (thickness to be pecified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make JOHNSON, NITCO, ORIENT, , KAJARIA in colours such as White, Ivory, Grey, Fume Red Brown, laid on 20 mm thick cement mortar 1:4 (1 Cement : 4 Coarse sand), including pointing the joints with white cement and matching pigment etc., complete | Sqm |  |  |  |  | 41.8 | 764.55 | 31958.19
|  | toilet block | Sqm | 1 | 5 | 4.15 | 1 | 20.75
|  | Isolation / VIP room toilet | Sqm | 1 | 1.5 | 1.3 | 1 | 1.95
|  | RO plant foundation top | Sqm | 1 | 5.3 | 2.5 | 1 | 13.25
|  | RO plant foundation and trench side | Sqm | 3 | 4 | 0.3 | 1 | 3.6
|  | RO plant foundation top | Sqm | 3 | 2.5 | 0.3 | 1 | 2.25
23 | 11.41.2 | Providing and laying vitrified floor tiles in different sizes (thickness to be specified by the manufacturer) 10mm with water absorption less than 0.08% and conforming to IS : 15622, of approved make JOHNSON, NITCO, ORIENT, , KAJARIA , in all colours and shades, laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand),or 5mm thick tile adhesive including grouting the joints with white cement and matching pigments etc., complete as directed by the Engineer in Charge. lobby- size 600x600mm | Sqm |  |  |  |  | 326.34 | 1337.1 | 436349.214
|  | ward | Sqm | 1 | 16 | 11 | 1 | 176
|  | dialysis room | Sqm | 1 | 5.5 | 4 | 1 | 22
|  | Isolation / VIP room | Sqm | 1 | 5.5 | 8 | 1 | 44
|  | Passage near nurses room | Sqm | 1 | 12 | 1.9 | 1 | 22.8
|  | Ward entrance/ reception area | Sqm | 1 | 5.2 | 4.85 | 1 | 25.22
|  | new Passage | Sqm | 1 | 7.6 | 3.6 | 1 | 27.36
|  | New Passage to gas storage area | Sqm | 1 | 6.4 | 1.4 | 1 | 8.96
|  | SUB HEAD IX : ROOFING | [7 empty] | 0
24 | 12.1.3 | Providing corrugated G.S. sheet roofing including vertical / curved surface fixed with polymer coated J or L hooks, bolts and nuts 8 mm diameter with bitumen and G.I. limpet washers or with G.I. limpet washers filled with white lead, including a coat of approved steel primer and two coats of approved paint on overlapping of sheets complete (up to any pitch in horizontal/ vertical or curved surfaces), excluding the cost of purlins, rafters and trusses and including cutting to size and shape wherever required:- 0.63 mm thick with zinc coating not less than 275 gm/ m² | Sqm |  |  |  |  | 48.8 | 627.25 | 30609.8
|  | New Passage to gas storage area | Sqm | 1 | 8 | 2.1 | 1 | 16.8
|  | New Passage to entrance | Sqm | 1 | 8 | 4 | 1 | 32
25 | 12.4.2 | Providing ridges or hips of width 60 cm overall width plain G.S. sheet fixed with polymer coated J. or L hooks, bolts and nuts 8 mm dia G.I. limpet and bitumen washers complete:- 0.63 mm thick with zinc coating not less than 275 gm/m² | mtr. |  |  |  |  | 7.5 | 411.4 | 3085.5
|  | New Passage to entrance | mtr. | 1 | 1 | 7.5 | 1 | 7.5
26 | 12.41.2 | Providing and fixing on wall face unplasticised - Rigid P.V.C rain water pipes conforming to IS : 13592 Type - A including jointing with seal ring conforming to IS : 5382 leaving 10 mm gap for thermal expansion :- 4kg/m 110 mm diameter single socketed pipes . | mtr. |  |  |  |  | 20 | 206.9 | 4138
|  | ward | Sqm | 2 | 5 | 1 | 1 | 10
|  | New Passage | Sqm | 2 | 5 | 1 | 1 | 10
27 | 12.43.2 | Providing and fixing unplasticised-P.V.C pipes clips of approved design to unplasticised-P.V.C rain water pipes by means of 50 x 50 x 50 mm hard wood plugs, screwed with M.S screws of required length including cutting brick work and fixing in cement mortar 1 : 4 ( 1 cement : 4 coarse sand ) and making good the walls etc. complete :- a) 110 mm . | each |  |  |  |  | 12 | 144.6 | 1735.2
|  | ward | each | 2 | 3 | 1 | 1 | 6
|  | New Passage | each | 2 | 3 | 1 | 1 | 6
28 | 12.42 | Providing and fixing on wall face unplasticised -P.V.C moulded fittings / accessories for unplasticised - Rigid P.V.C rain water pipes conforming to IS : 13592 Type A including jointing with seal ring conforming to IS 5382 leaving 10 mm gap for thermal expansion :- | [7 empty] | 0
| 12.42.5. | a. Bend 87.5 degree: | [7 empty] | 0
| 12.42.5.2 | 2. 110mm T / Y Bend " | Each | 2 | 6 | 1 | 1 | 12 | 156.95 | 1883.4
| 12.42.6 | b. Shoe plain :- " | [7 empty] | 0
| 12.42.6.2 | 2. 110 mm shoe. " | Each | 2 | 5 | 1 | 1 | 10 | 287.05 | 2870.5
29 | 12.53 | Providing and Fixing 15 mm thick densified tegular edged eco friendly light weight calcium silicate false ceiling tiles of approved texture spintone/cosmos / Hexa or equivalent of size 595 x 595 mm in true horizontal level, suspended on inter locking metal grid of hot dipped galvanised steel sections (galvanising @ 120 grams per sqm including both side) consisting of main 'T' runner suitably spaced at joints to get required length and of size 24x38 mm made from 0.33 mm thick (minimum) sheet, spaced 1200 mm centre to centre, and cross "T" of size 24x28 mm made out of 0.33 mm (Minimum) sheet, 1200 mm long spaced between main'T' at 600 mm centre to centre to form a grid of 1200x600 mm and secondary cross 'T' of length 600 mm and size 24 x28 mm made of 0.33 mm thick (Minimum) sheet to be inter locked at middle of the 1200x 600 mm panel to from grid of size 600x600 mm, resting on periphery walls /partitions on a Perimeter wall angle pre-coated steel of ize(24x24X3000 mm made of 0.40 mm thick (minimum) sheet with the help of rawl plugs at 450 mm centre to centre with 25 mm long dry wall screws @ 230 mm interval and laying 15 mm thick densified edges calicum silicate ceiling tiles of approved texture (Spintone / Cosmos/hexa) in the grid, including, | Sqm |  |  |  |  | 275 | 1566 | 430650 |  |  | 69687
cutting/ making opening for services like diffusers, grills, light fittings, fixtures, smoke detectors etc., wherever required. Main 'T' runners to be suspended from ceiling using G.I. slotted cleats of size 25x35x1.6 mm fixed to ceiling with 12.5 mm dia and 50 mm long dash fasteners, 4 mm G.I. adjustable rods with galvanised steel level clips of size 85 x 30 x 0.8 mm, spaced at 1200 mm centre to centre along main 'T' , bottom exposed with 24 mm of all T-sections shall be pre-painted with polyster baked paint, for all heights, as per specifications, drawings and as directed by engineer-in-charge. Note :- Only calcium silicate false ceiling area will be measured from wall to wall. No deduction shall be made for exposed frames/opening (cut outs) having area less than 0.30 sqm.The calcium silicate ceiling tile shall have NRC value of 0.50 (Minimum), light reflection > 85%, non - combustible as per B.S. 476 part IV, 100% humidity resistance and also having thermal conductivity <0.043 w/m 0 KC.
|  | ward | Sqm | 1 | 16 | 11 | 1 | 176
|  | dialysis room | Sqm | 1 | 5.5 | 5 | 1 | 27.5
|  | Isolation / VIP room | Sqm | 1 | 5.5 | 8 | 1 | 44
|  | ward entrance reception room | Sqm | 1 | 5.5 | 5 | 1 | 27.5
|  | SUB HEAD X : FINISHING | [7 empty] | 0
30 | 13.1.1 | 12mm cement plaster of mix in fine sand, 1:4(1cement : 4 fine sand) | Sqm |  |  |  |  | 227.5625 | 123.5 | 28103.9688
|  | Door closing brick wall | Sqm | 4 | 1.5 | 2.1 | 1 | 12.6
|  | all existing MS window remove and refixing area plastering inside - ward area | Sqm | 7 | 6 | 1 | 1 | 42
|  | dialysis room partition | Sqm | 1 | 5.3 | 3.25 | 1 | 17.225
|  | all existing MS window remove and refixing area plastering inside - dialysis, VIP room | Sqm | 6 | 6 | 1 | 1 | 36
|  | cylinder store | Sqm | 2 | 5 | 3.25 | 1 | 32.5
|  | New Passage | Sqm | 1 | 1.7 | 3.25 | 1 | 5.525
|  | New Passage | Sqm | 1 | 3.25 | 3.25 | 1 | 10.5625
|  | New Passage to gas storage area | Sqm | 1 | 8 | 3.25 | 1 | 26
|  | dialysis room wall after demolishing tiles | Sqm | 2 | 7.8 | 1.75 | 1 | 27.3
|  | dialysis room wall after demolishing tiles | Sqm | 2 | 5.1 | 1.75 | 1 | 17.85
31 | 13.2.2 | 15mm cement plaster on rough sides of single or half brick wall plaster of mix in1:6 (1 cement:6 coarse sand | Sqm |  |  |  |  | 284.0125 | 130.2 | 36978.4275
|  | Door closing brick wall | Sqm | 6 | 1.5 | 2.1 | 1 | 18.9
|  | all existing MS window remove and refixing area plastering inside - ward area | Sqm | 7 | 6 | 1 | 1 | 42
|  | dialysis room partition | Sqm | 1 | 5.3 | 3.25 | 1 | 17.225
|  | all existing MS window remove and refixing area plastering inside - dialysis, VIP room | Sqm | 6 | 6 | 1 | 1 | 36
|  | cylinder store | Sqm | 2 | 5 | 3.25 | 1 | 32.5
|  | New Passage | Sqm | 1 | 1.7 | 3.25 | 1 | 5.525
|  | New Passage | Sqm | 1 | 3.25 | 3.25 | 1 | 10.5625
|  | New Passage to gas storage area | Sqm | 1 | 8 | 3.25 | 1 | 26
|  | vacuum plant out side | Sqm | 2 | 4.5 | 3 | 1 | 27
|  | vacuum plant out side | Sqm | 2 | 4.5 | 3 | 1 | 27
|  | vacuum plant gable out side | Sqm | 2 | 3.5 | 0.5 | 1 | 3.5
|  | vacuum plant in side | Sqm | 2 | 4 | 3 | 1 | 24
|  | vacuum plant in side | Sqm | 2 | 3 | 3 | 1 | 18
|  | vacuum plant gable in side | Sqm | 2 | 3 | 0.5 | 1 | 3
|  | deduction for window | Sqm | 3 | 1.2 | -1.3 | 1 | -4.68
|  | deduction for door | Sqm | 1 | 1.2 | -2.1 | 1 | -2.52
32 | 13.60.1 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade :-Two or more coats on new work . | Sqm |  |  |  |  | 113.7125 | 60.25 | 6851.1781
|  | Door closing brick wall | Sqm | 8 | 1.5 | 1 | 1 | 12
|  | dialysis room partition | Sqm | 2 | 5.3 | 1.75 | 1 | 18.55
|  | cylinder store | Sqm | 2 | 5 | 1.75 | 1 | 17.5
|  | New Passage | Sqm | 1 | 1.7 | 1.75 | 1 | 2.975
|  | New Passage | Sqm | 1 | 3.25 | 1.75 | 1 | 5.6875
|  | New Passage to gas storage area | Sqm | 1 | 8 | 1.5 | 1 | 12
|  | vacuum plant in side | Sqm | 2 | 4 | 3 | 1 | 24
|  | vacuum plant in side | Sqm | 2 | 3 | 3 | 1 | 18
|  | vacuum plant gable in side | Sqm | 2 | 3 | 0.5 | 1 | 3
33 | 13.43.1 | Applying one coat of cement primer of approved brand and manufacture on wall surface for plastic emulsion | Sqm |  |  |  |  | 113.7125 | 27.55 | 3132.7794
|  | Door closing brick wall | Sqm | 8 | 1.5 | 1 | 1 | 12
|  | dialysis room partition | Sqm | 2 | 5.3 | 1.75 | 1 | 18.55
|  | cylinder store | Sqm | 2 | 5 | 1.75 | 1 | 17.5
|  | New Passage | Sqm | 1 | 1.7 | 1.75 | 1 | 2.975
|  | New Passage | Sqm | 1 | 3.25 | 1.75 | 1 | 5.6875
|  | New Passage to gas storage area | Sqm | 1 | 8 | 1.5 | 1 | 12
|  | vacuum plant in side | Sqm | 2 | 4 | 3 | 1 | 24
|  | vacuum plant in side | Sqm | 2 | 3 | 3 | 1 | 18
|  | vacuum plant gable in side | Sqm | 2 | 3 | 0.5 | 1 | 3
34 | 13.47.1 | Finishing walls with Premium Acrylic Smooth exterior paint with Silicone additives of required shade 13.47.1 New work (Two or more coats applied @ 1.43 ltr/ 10 sqm. over and including base coat of water proofing cement paint applied @ 2.20 kg/ 10 sqm | Sqm |  |  |  |  | 482 | 80.45 | 38776.9
|  | existing building out side | Sqm | 2 | 21 | 3.5 | 1 | 147
|  | existing building out side | Sqm | 2 | 16.5 | 3.5 | 1 | 115.5
|  | existing building out side toilet area | Sqm | 2 | 12 | 3.5 | 1 | 84
|  | existing building out side | Sqm | 2 | 12 | 3.5 | 1 | 84
|  | vacuum plant out side | Sqm | 2 | 4.5 | 3 | 1 | 27
|  | vacuum plant out side | Sqm | 2 | 3.5 | 3 | 1 | 21
|  | vacuum plant gable out side | Sqm | 2 | 3.5 | 0.5 | 1 | 3.5
35 | 13.50.3 | Applying priming coat :With ready mixed red oxide zinc chromate primer of approved brand and manufacture on steel galvanised iron/steel works | Sqm |  |  |  |  | 22.2573 | 20.7 | 460.7261
|  | Window for vacuum plant | Sqm | 3 | 1.2 | 1.3 | 1 | 4.68
|  | Window for new passage | Sqm | 2 | 1.2 | 1.3 | 1 | 3.12
|  | grill door for vacuum plant | Sqm | 1 | 1.2 | 2.1 | 1 | 2.52
|  | Grill door for new passage | Sqm | 1 | 1.5 | 2.1 | 1 | 3.15
|  | tubular truss for vacuum plant | Sqm | 6 | 2.15 | 0.25 | 1 | 3.225
|  | tubular truss for new passage | Sqm | 4 | 2.15 | 0.25 | 1 | 2.15
|  | purlin for vacuum plant | Sqm | 6 | 5.66 | 0.10048 | 1 | 3.4123
36 | 13.61.1 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade : Two or more coats on new work | Sqm |  |  |  |  | 51.3273 | 53.85 | 2763.9751
|  | Window | Sqm | 15 | 1.5 | 1.5 | 1 | 33.75
|  | Window for new passage | Sqm | 2 | 1.2 | 1.3 | 1 | 3.12
|  | grill door for vacuum plant | Sqm | 1 | 1.2 | 2.1 | 1 | 2.52
|  | Grill door for new passage | Sqm | 1 | 1.5 | 2.1 | 1 | 3.15
|  | tubular truss for vacuum plant | Sqm | 6 | 2.15 | 0.25 | 1 | 3.225
|  | tubular truss for new passage | Sqm | 4 | 2.15 | 0.25 | 1 | 2.15
|  | purlin for vacuum plant | Sqm | 6 | 5.66 | 0.10048 | 1 | 3.4123
|  | SUB HEAD XI : PVC WORKS MISCELLANEOUS | [7 empty] | 0
37 | 9.117.1 | Providing and fixing factory made uPVC door frame made of uPVC extruded sections having an overall dimension as below (tolerance ±1mm), with wall thickness 2.0 mm (± 0.2 mm), corners of the door frame to be Jointed with galvanized brackets and stainless steel screws, joints mitred and Plastic welded. The hinge side vertical of the frames reinforced by galvanized M.S. tube of size 19 X 19 mm and 1mm (± 0.1 mm) wall thickness and 3 nos. stainless steel hinges fixed to the frame complete as per manufacturer’s specification and direction of Engineer-in-charge : - Extruded section profile size 48x40 mm | mtr. |  |  |  |  | 39.6 | 185.15 | 7331.94
|  | Toilet door V (VIP room/nurses/ toilet block | Sqm | 16 | 2.1 | 1 | 1 | 33.6
|  | Toilet door H (VIP room/nurses/ toilet block | Sqm | 8 | 0.75 | 1 | 1 | 6
38 | 9.120.2 | Providing and fixing factory made panel PVC door shutter consisting of frame made out of M.S. tubes of 19 gauge thickness and size of 19 mm x 19 mm for styles and 15x15 mm for top & bottom rails. M.S. frame shall have a coat of steel primers of approved make and manufacture . M.S. frame covered with 5 mm thick heat moulded PVC 'C' channel of size 30 mm thickness, 70 mm width out of which 50 mm shall be flat and 20 mm shall be tapered in 45 degree angle on both side forming styles and 5 mm thick, 95 mm wide PVC sheet out of which 75 mm shall be flat and 20 mm shall be tapered in 45 degree on the inner side to form top and bottom rail and 115 mm wide PVC sheet out of which 75 mm shall be flat and 20 mm shall be tapered on both sides to form lock rail. Top, bottom and lock rails shall be provided both side of the panel. 10 mm (5 mm x 2 ) thick, 20 mm wide cross PVC sheet be provided as gap insert for top rail & bottom rail, paneling of 5 mm thick both side PVC sheet to be fitted in the M.S. frame welded/ sealed to the styles & rails with 7 mm (5 mm+2 mm) thick x 15 mm wide PVC sheet beading on inner side, and joined together with solvent cement adhesive. An additional 5 mm thick PVC strip of 20 mm width is to be stuck on the interior side of the 'C' Channel using PVC solvent adhesive etc. complete as per direction of Engineer-in-charge, manufacturer's specification & drawing. :- 30 mm thick pre laminated PVC door shutters | Sqm |  |  |  |  | 12.6 | 2958 | 37270.8
|  | Toilet door (VIP room/nurses/ toilet block | Sqm | 8 | 2.1 | 0.75 | 1 | 12.6
|  | SUB HEAD XII : SERVICES | [7 empty] | 0
|  | SANITARY INSTALLATIONS | [7 empty] | 0
39 | 17.2.1 | Providing and fixing white vitreous china pedestal type water closet (European type W.C. pan) with seat and lid, 10 litre low level white P.V.C. flushing cistern, including flush pipe, with manually controlled device (handle lever), conforming to IS : 7231, with all fittings and fixtures complete, including cutting and making good the walls and floors wherever required : W.C. pan with ISI marked white solid plastic seat and lid | Each |  |  |  |  | 5 | 2885.1 | 14425.5
|  | Toilet (VIP room/nurses/ toilet block | Each | 5 | 1 | 1 | 1 | 5
40 | 17.7.4 | Providing and fixing wash basin with C.I. brackets, 15 mm C.P. brass pillar taps, 32 mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever require :White Vitreous China Flat back wash basin size 550x 400 mm with single 15 mm C.P. brass pillar tap | Each |  |  |  |  | 2 | 1460 | 2920
|  | Toilet block | Each | 2 | 1 | 1 | 1 | 2
41 | 17.31 | Providing and fixing 600x450 mm beveled edge mirror of superior glass (of approved quality) complete with 6 mm thick hard board ground fixed to wooden cleats with C.P. brass screws and washers complete | each |  |  |  |  | 2 | 674.05 | 1348.1
|  | Toilet block | Each | 2 | 1 | 1 | 1 | 2
42 | 18.65 | Providing and fixing PTMT soap Dish Holder having length of 138mm,breadth 102mm, height of 75mm with concealed fitting arrangements, weighing not less than 106 gms | each |  |  |  |  | 7 | 151.1 | 1057.7
|  | Toilet VIP room | Each | 1 | 1 | 1 | 1 | 1
|  | Toilet Nurses | Each | 1 | 1 | 1 | 1 | 1
|  | Toilet block | Each | 4 | 1 | 1 | 1 | 4
|  | Toilet doctors | Each | 1 | 1 | 1 | 1 | 1
43 | 17.73.2 | Providing and fixing PTMT towel rail complete with brackets fixed to wooden cleats with CP brass screws with concealed fittings arrangement of approved quality and colour:. 600 mm long towel rail with total length of 645 mm, width 78 mm and effective height of 88 mm, weighting not less than 190 gms. | each |  |  |  |  | 10 | 415.2 | 4152
|  | Toilet VIP room | Each | 1 | 1 | 1 | 1 | 1
|  | Toilet Nurses | Each | 1 | 1 | 1 | 1 | 1
|  | Toilet block | Each | 7 | 1 | 1 | 1 | 7
|  | Toilet doctors | Each | 1 | 1 | 1 | 1 | 1
44 | 17.28.2.1 | Providing and fixing P.V.C. waste pipe for sink or wash basin including P.V.C. waste fittings complete :-Flexible pipe :-32 mm dia. | each |  |  |  |  | 7 | 65.3 | 457.1
|  | Toilet VIP room | Each | 1 | 1 | 1 | 1 | 1
|  | Toilet Nurses | Each | 1 | 1 | 1 | 1 | 1
|  | Toilet block | Each | 4 | 1 | 1 | 1 | 4
|  | Toilet doctors | Each | 1 | 1 | 1 | 1 | 1
45 | 12.41 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion,(i) Single socketed pipes | [7 empty] | 0
a | 12.41.1 | 75 mm diameter | mtr. | 1 | 30 | 1 | 1 | 30 | 124.9 | 3747
b | 12.41.2 | 110 mm diameter | mtr. | 1 | 30 | 1 | 1 | 30 | 206.9 | 6207
46 | LMR | Providing & fixing bend of required degree with acess door,insertion rubber washer 3 mm thick bolts,nuts complete | [7 empty] | 0
a | LMR | 75 mm | Each | 6 | 1 | 1 | 1 | 6 | 230 | 1380
b | LMR | 110 mm | Each | 5 | 1 | 1 | 1 | 5 | 329.1 | 1645.5
47 | 2.10.1.2 | excavating trenches of required width for pipes ,cables,etcincluding excavation for sockets and dressing of sides ramming of bottom depth up to 1.5 mincluding getting out the excavated soil and then returning the soil as required in layers not exceeding 20 cm in depth including consolidating each deposited layer by ramming watering etc and desposing of surplus ecavated soilas directed within a lead of 50 m. all kinds of soil . | mtr. |  |  |  |  | 60 | 165.6 | 9936
| LMR | 50 mm diameter dialysis room | mtr. | 1 | 18 | 1 | 1 | 18 |  | 0
|  | 75 mm diameter | mtr. | 1 | 30 | 1 | 1 | 30 |  | 0
|  | 110 mm diameter | mtr. | 1 | 30 | 1 | 1 | 30 |  | 0
48 | 19.2 | providing and laying c.c 1:5:10 all round p v c pipes including bed concrete as per standard design. | [7 empty] | 0
b | 19.2.1 | 100 mm | mtr. | 1 | 30 | 1 | 1 | 30 | 496.9 | 14907
49 | LMR | Providing and fixing PVC pipe including cutting chasng in walls and making good the walls etc complete. (Concealed)10kg/m | [7 empty] | 0
| LMR | a 20 mm pipe | mtr. | 1 | 45 | 1 | 1 | 45 | 236.4 | 10638
| LMR | b 25 mm pipe | mtr. | 1 | 24 | 1 | 1 | 24 | 268.7 | 6448.8
| LMR | c 32mmpipe | mtr. | 1 | 10 | 1 | 1 | 10 | 313.3 | 3133
50 | LMR | Providing and fixing PVC pipe including cutting chasng in walls and making good the walls etc complete. (External) 10kg/m | [7 empty] | 0
| LMR | 20mm( OD ) pipe external | mtr. | 1 | 20 | 1 | 1 | 20 | 240 | 4800
| LMR | 25 mm( OD ) pipe | mtr. | 1 | 15 | 1 | 1 | 15 | 270 | 4050
| LMR | 32 mm( OD ) pipe | mtr. | 1 | 10 | 1 | 1 | 10 | 320 | 3200
51 | 18.7 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer in Charge: Internal work - Exposed on wall | [7 empty] | 0
| 18.7.2 | 20mm( OD ) pipe external | mtr. | 1 | 17 | 1 | 1 | 17 | 133.1 | 2262.7
| 18.7.3 | 25 mm( OD ) pipe | mtr. | 1 | 17 | 1 | 1 | 17 | 135.4 | 2301.8
| 18.7.4 | 32 mm( OD ) pipe | mtr. | 1 | 17 | 1 | 1 | 17 | 156.9 | 2667.3
52 | 18.51.1 | Providing and fixing C.P. brass long body bib cock of approved quality conforming to IS standards and weighing not less than 690 gms. 15 mm nominal bore | each |  |  |  |  | 11 | 430.6 | 4736.6 |  |  | 2012 up to item 61
|  | Toilet VIP room | Each | 1 | 1 | 1 | 1 | 1
|  | Toilet Nurses | Each | 1 | 1 | 1 | 1 | 1
|  | Toilet block | Each | 2 | 3 | 1 | 1 | 6
|  | RO plant wash | Each | 3 | 1 | 1 | 1 | 3
53 | 18.16.2 | Providing and fixing C.P. brass stop cock (concealed) of standard design and of approved make conforming to IS 8931 :- 15 mm nominal bore | each |  |  |  |  | 19 | 266.65 | 5066.35
|  | Toilet VIP room | Each | 1 | 2 | 1 | 1 | 2
|  | Toilet Nurses | Each | 1 | 2 | 1 | 1 | 2
|  | Toilet block | Each | 3 | 2 | 1 | 1 | 6
|  | Dialysis | Each | 3 | 3 | 1 | 1 | 9
54 | 18.17 | Providing and fixing gun metal valve with C I wheel of approved quality (screwed end ):- | [7 empty] | 0
| LMR | 20mm dia nominal bore | each | 1 | 5 | 1 | 1 | 5 | 850 | 4250
| 18.17.1 | 25mm dia nominal bore | each | 1 | 5 | 1 | 1 | 5 | 372.95 | 1864.75
| 18.17.2 | 32 mm dia nominal bore | each | 1 | 3 | 1 | 1 | 3 | 450.9 | 1352.7
55 | 18.21.2.2 | Providing and fixing unplasticised P.V.C connection pipe with brass unions :- 20 mm nominal bore. | each |  |  |  |  | 9 | 73.35 | 660.15
|  | Toilet VIP room | Each | 1 | 2 | 1 | 1 | 2
|  | Toilet Nurses | Each | 1 | 2 | 1 | 1 | 2
|  | Toilet block | Each | 5 | 1 | 1 | 1 | 5
56 | 17.60.2.1 | Providing and fixing PVC trap of self cleansing design with PVC screwed down or hinged CP grating with or without vent arm complete including cutting and making good the walls and floors. a)100mm inlet and 75mm outlet. | each |  |  |  |  | 12 | 838.85 | 10066.2
|  | Toilet VIP room | Each | 1 | 1 | 1 | 1 | 1
|  | Toilet Nurses | Each | 1 | 1 | 1 | 1 | 1
|  | Toilet block | Each | 3 | 2 | 1 | 1 | 6
|  | RO plant wash and tank area | Each | 4 | 1 | 1 | 1 | 4
57 | 19.7.1.1 | Constructing brick masonry manhole in cement mortar 1 : 4 (1 cement : 4 coarse sand) R.C.C. top slab with 1 : 2 : 4 mix ( 1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), foundation concrete 1 : 4 : 8 mix (1 cement : 4 coarse sand : 8 graded stone aggregate 40 mm nominal size) inside plastering 12mm thick with cement mortar 1 : 3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1: 2 : 4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design Inside size 90 x 80 cm and 45 cm deep including C.I. cover with frame ( light duty ) 455 x 610 mm internal dimensions, total weight of cover and frame to be not less than 38 kg (weight of cover 23 kg and weight of frame 15 kg) With F.P.S bricks with class designation. | each |  |  |  |  | 9 | 7132 | 64188
|  | Toilet VIP room | Each | 1 | 1 | 1 | 1 | 1
|  | Toilet Nurses | Each | 1 | 1 | 1 | 1 | 1
|  | Toilet block | Each | 3 | 1 | 1 | 1 | 3
|  | R O plant drainages | Each | 4 | 1 | 1 | 1 | 4
58 | 19.8.1.1 | Extra for depth for manholes :-With F.P.S bricks with class designation. | mtr. |  |  |  |  | 2 | 4061.7 | 8123.4
59 | 19.33 | Constructing soak pit 1.20 x 1.20 x 1.20 m filled with brickbats including S.W. drain pipe 100 mm diameter and 1.20 m long complete as per standard design. | each |  |  |  |  | 5 | 1591.35 | 7956.75
|  | Toilet VIP room | Each | 1 | 1 | 1 | 1 | 1
|  | Toilet Nurses | Each | 1 | 1 | 1 | 1 | 1
|  | from dialysis room | Each | 2 | 1 | 1 | 1 | 2
|  | Toilet block | Each | 1 | 1 | 1 | 1 | 1
60 | 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank ISI : 12701 marked indicating the BIS License No. with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank [Sintex, Electroplast, Star, Lotus or equivalent having valid ISI license]. | Litre |  |  |  |  | 4000 | 6.1 | 24400
|  | SUB HEAD XIII : ALUMINIUM WORK | [7 empty] | 0
61 | 21.1.1.2 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS : 1285, fixed with rawl plugs and screws or with fixing clips, or with expansion hold fasteners including necessary filling up of gaps at junctions, at top, bottom and sides with required PVC/neoprene felt etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing and paneling to be paid for separately) : For fixed portion Powder coated aluminium (minimum thickness of powder coating 50 micron) | kg |  |  |  |  | 554.3364 | 358.3 | 198618.7321
|  | Partition vertical- nurses station | kg | 7 | 3.25 | 1.094 |  | 24.8885
|  | Partition horizontal T & middile- nurses station | kg | 3 | 4.9 | 1.094 |  | 16.0818
|  | Partition horizontal bottom - nurses station | kg | 1 | 4.9 | 1.619 |  | 7.9331 |  |  |  |  | 341
|  | Partition vertical snapon beading- nurses station | Kg | 28 | 3.25 | 0.175 |  | 15.925
|  | Partition vertical snapon beading | Kg | 12 | 5 | 0.175 |  | 10.5
|  | Partition for Isolation/VIP room vertical | kg | 7 | 3.25 | 1.094 |  | 24.8885 |  | 13 |  |  | 63 | 5.4127
|  | Partition Isolation/VIP room horizontal T & middile | kg | 3 | 5.5 | 1.094 |  | 18.051 | [5 empty] | 9.8727
|  | Partition Isolation/VIP room horizontal bottom | kg | 1 | 5.5 | 1.619 |  | 8.9045
|  | Partition Isolation/VIP room vertical snapon beading | Kg | 24 | 3.25 | 0.175 |  | 13.65
|  | Partition Isolation/VIP room horizontal snapon beading | Kg | 12 | 5.5 | 0.175 |  | 11.55
|  | Cleat angle | Kg | 320 | 0.07 | 0.281 |  | 6.2944
|  | Partition ward nurses station south -vertical | Kg | 7 | 3.25 | 1.094 |  | 24.8885
|  | Partition ward nurses station north -vertical | Kg | 7 | 3.25 | 1.094 |  | 24.8885
|  | Partition ward nurses station south -horizontal T & middile | Kg | 4 | 6 | 1.094 |  | 26.256
|  | Partition ward nurses station north -horizontal T & middile | Kg | 4 | 5.5 | 1.094 |  | 24.068
|  | Partition ward nurses station south -bottom | Kg | 1 | 6 | 1.094 |  | 6.564
|  | Partition ward nurses station north -bottom | Kg | 1 | 5.5 | 1.619 |  | 8.9045
|  | Partition ward nurses station south -vertical snapon beading | Kg | 24 | 3.25 | 0.175 |  | 13.65
|  | Partition ward nurses station north -vertical snapon beading | Kg | 20 | 3.25 | 0.175 |  | 11.375
|  | Partition ward nurses station south -horizontal snapon beading | Kg | 12 | 6 | 0.175 |  | 12.6
|  | Partition ward nurses station north -horizontal snapon beading | Kg | 12 | 5.5 | 0.175 |  | 11.55
|  | Partition at entrance room south -vertical | Kg | 5 | 3.25 | 1.094 |  | 17.7775
|  | Partition at entrance room south -bottom | Kg | 1 | 3.85 | 1.094 |  | 4.2119
|  | Partition at entrance room south-horizontal T & middile | Kg | 3 | 3.85 | 1.094 |  | 12.6357
|  | Partition at entrance room south -vertical snapon beading | Kg | 20 | 3.25 | 0.175 |  | 11.375
|  | Partition at entrance room south -horizontal snapon beading | Kg | 12 | 3.85 | 0.175 |  | 8.085
|  | Door top | kg | 5 | 2 | 1.094 |  | 10.94 |  |  |  | 8.4 | 3.0076 |  | 21
|  | Door vertical | kg | 20 | 2.1 | 1.094 |  | 45.948 |  |  |  | 10.08 |  |  | 12.6
|  | Door top | kg | 5 | 1.2 | 1.094 |  | 6.564 | [6 empty] | 1.8884
|  | Window verticals | kg | 22 | 1.5 | 1.718 |  | 56.694 |  |  |  |  | 24.75
|  | Window Horizontals at top | kg | 11 | 1.5 | 1.718 |  | 28.347 |  |  |  |  | 4.6061 | 7.383
|  | Window Horizontals at bottom | kg | 11 | 1.5 | 1.718 |  | 28.347
62 | 21.1.2.1 | For shutters of doors, windows & ventilators including providing and fixing hinges/ pivots and making provision for fixing of fittings wherever required including the cost of PVC / neoprene gasket required (Fittings shall be paid for separately). Anodised aluminium (anodised transparent or dyed to required shade according to IS: 1868, Minimum anodic coating of grade AC 15) | kg |  |  |  |  | 408.4901 | 406.5 | 166051.237 |  | 173
|  | Door vertical | Kg | 40 | 2.1 | 1.052 |  | 88.368 |  |  |  | 12.6 | 21
|  | Door top & middle (double panel) | Kg | 20 | 1 | 1.052 |  | 21.04 |  |  |  | 12.6 | 12.6
|  | Door top & middle | Kg | 10 | 1.2 | 1.052 |  | 12.624 |  |  |  | 25.2 | 6.719
|  | Door continues handle (double panel) | Kg | 20 | 1 | 1.093 |  | 21.86 |  |  |  | 6.8651
|  | Door continues handle | Kg | 10 | 1.2 | 1.093 |  | 13.116
|  | Door bottom (double panel) | Kg | 10 | 1 | 1.519 |  | 15.19
|  | Door bottom | Kg | 5 | 1.2 | 1.519 |  | 9.114
|  | Door vertical snapon beading | Kg | 40 | 2.1 | 0.175 |  | 14.7
|  | Door top & middle snapon beading | Kg | 80 | 1 | 0.175 |  | 14
|  | Door vertical snapon beading | Kg | 20 | 2.1 | 0.175 |  | 7.35
|  | Door top & middle snapon beading | Kg | 40 | 1.2 | 0.175 |  | 8.4
|  | Window verticals | kg | 66 | 1.436 | 0.431 |  | 40.8485
|  | Window verticals locking | kg | 66 | 1.436 | 0.51 |  | 48.3358
|  | Window Horizontals at top | kg | 66 | 1.436 | 0.42 |  | 39.8059
|  | Window Horizontals at bottom | kg | 66 | 1.436 | 0.567 |  | 53.738
63 | 21.2.2 | Providing and fixing 12mm thick prelaminated particle board flat pressed three layer or graded wood particle board conforming to IS: 12823 Grade l Type ll, in panelling fixed in aluminum doors, windows shutters and partition frames with C.P. brass / stainless steel screws etc. complete as per architectural drawings and directions of engineer-in-charge. Pre-laminated particle board with decorative lamination on both sides. | Sqm |  |  |  |  | 28.55 | 969.95 | 27692.0725
|  | Partition ward nurses station south | sqm | 1 | 6 | 0.75 |  | 4.5
|  | Partition ward nurses station north | sqm | 1 | 5.6 | 0.75 |  | 4.2
|  | Partition at entrance room south -vertical | sqm | 1 | 3.85 | 1 |  | 3.85
|  | Door | sqm | 10 | 1 | 1 |  | 10
|  | Door | sqm | 5 | 1.2 | 1 |  | 6
64 | 21.3.2 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with PVC/ neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.50 mm thickness | Sqm |  |  |  |  | 96.2125 | 905.75 | 87144.4719
|  | Partition ward nurses station south | sqm | 1 | 6 | 2.5 | 1 | 15
|  | Partition ward nurses station north | sqm | 1 | 5.6 | 2.5 | 1 | 14
|  | Partition at entrance room south -vertical | sqm | 1 | 3.85 | 2.25 |  | 8.6625
|  | Partition Isolation/ VIP room | sqm | 1 | 5.5 | 2.1 | 1 | 11.55
|  | Door | sqm | 10 | 1 | 1.1 | 1 | 11
|  | Door | sqm | 5 | 1.2 | 1.1 | 1 | 6.6
|  | Window | sqm | 15 | 1.4 | 1.4 | 1 | 29.4
65 | 21.4.1 | Providing and fixing double action hydraulic floor spring of approved brand and manufacture IS : 6315 marked, Hardwyn make (model 3000) or equivalent for doors including cost of cutting floors as required, embedding in floors and cover plates with brass pivot and single piece M.S. sheet outer box with slide plate etc. complete as per the direction of Engineer-in-charge With Stainless Steel cover plate | each |  |  |  |  | 10 | 1953.1 | 19531
|  | Door | Each | 10 | 1 | 1 |  | 10
66 | 9.97 | providing and fixing aluminium tower bolt ISI markedanodised (anodise coating not less than grade AC 10 as per IS:1868) transperent dyed to required color or shade with ss screws etc complete | [7 empty] | 0
a | 9.97.3 | 200 x 10 mm | each |  |  |  |  | 11 | 71.05 | 781.55
|  | Door | Each | 11 | 1 | 1 |  | 11
b | 9.97.2 | 250 x 10 mm | each |  |  |  |  | 11 | 86.45 | 950.95
|  | Door | Each | 11 | 1 | 1 |  | 11
67 | 21.8.1 | Filling the gap in between aluminium frame & adjacent RCC/ Brick/ Stone work by providing weather silicon sealant over backer rod of approved quality as per architectural drawings and direction of Engineer-in-charge complete. : Upto 5mm depth and 5 mm width | mtr. |  |  |  |  | 91.2 | 75.1 | 6849.12
|  | Door | metre | 16 | 2.1 | 2 |  | 67.2
|  | Door | metre | 6 | 1 | 2 |  | 12
|  | Door | metre | 5 | 1.2 | 2 |  | 12
68 | 21.13 | providing and fixing 100 mm brass lock (best make of approved quality) for aluminium door including necessary cutting and macking good etc complete as per the direction of engineer in charge.Anodized | each |  |  |  |  | 11 | 356.1 | 3917.1
|  | Door | Each | 11 | 1 | 1 |  | 11
69 | LMR | Providing and fixing non reflective polyster film of approved make and clour with self adhesive to glazed windows/doors (to make opaque) | Sqm |  |  |  |  | 107.9247 | 675 | 72849.1428
|  | Partition ward | sqm | 1 | 15.7 | 2.1 | 1 | 32.97
|  | Partition ward nurses station south | sqm | 1 | 6 | 2.5 | 1 | 15
|  | Partition ward nurses station north | sqm | 1 | 5.6 | 2.5 | 1 | 14
|  | Partition Isolation/ VIP room | sqm | 1 | 5.5 | 2.1 | 1 | 11.55
|  | Door | sqm | 10 | 1 | 1.1 | 1 | 11
|  | Door | sqm | 5 | 1.2 | 1.1 | 1 | 6.6
|  | Window | sqm | 11 | 1.236 | 1.236 | 1 | 16.8047
70 | LMR | Removing and refixing the existing aluminum door after rectification with new pivot/ hinge ,weather strip etc complete | Sqm |  |  |  |  | 10.92 | 550 | 6006
|  | Door | sqm | 4 | 1.3 | 2.1 |  | 10.92
71 | 9.84 | Providing and fixing aluminium extruded section body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 36 kg to 80 kg and door width from 701 mm to 1000 mm), with double speed adjustment with necessary accessories and screws etc. complete | each |  |  |  |  | 10 | 981.75 | 9817.5
|  | Door | Each | 10 | 1 | 1 |  | 10
|  | SUB HEAD : XIV: WATER PROOFING | [7 empty] | 0
72 | 22.5 | Providing and laying water proofing treatment in sunken portion of WCs, bathroom etc., by applying cement slurry mixed with water proofing cement compound consisting of applying : a) First layer of slurry of cement @ 0.488 kg/sqm mixed with water proofing cement compound @ 0.253 kg/sqm. This layer will be allowed to air cure for 4 hours. b) Second layer of slurry of cement @ 0.242 kg/sqm mixed with water proofing cement compound @ 0.126 kg/sqm. This layer will be allowed to air cure for 4 hours followed with water curing for 48 hours. The rate includes preparation of surface, treatment and sealing of all joints, corners, junctions of pipes and masonry with polymer mixed slurry. | Sqm |  |  |  |  | 38.5225 | 215.15 | 8288.1159 |  |  | 626.01
|  | Toilet at VIP room | Sqm | 1 | 1.5 | 1.3 |  | 1.95 |  | 0
|  | Toilet at nurses room | Sqm | 1 | 1.5 | 1.3 |  | 1.95
|  | toilet block | Sqm | 1 | 5.15 | 4.15 |  | 21.3725
|  | RO Plant floor | Sqm | 1 | 5.3 | 2.5 |  | 13.25
|  | SUB HEAD XV : REPAIR AND MAINTENANCE | [7 empty] | 0
73 | 14.12 | Providing and fixing 16 mm M.S. Fan clamps of standard shape and size in existing R.C.C. slab, including cutting chase, anchoring clamp to reinforcement bar, including cleaning, refilling, making good the chase with matching concrete, plastering and painting the exposed portion of the clamps complete | [5 empty] | 10 | 190.1 | 1901
|  | ward | each | 8 | 1 | 1 | 1 | 8
|  | dialisys room | each | 2 | 1 | 1 | 1 | 2
74 | 14.1.1 | Repairs to plaster of thickness 12 mm to 20 mm in patches of area 2.5 sq. meters and under, including cutting the patch in proper shape, raking out joints and preparing and plastering the surface of the walls complete, including disposal of rubbish to the dumping ground within 50 metres lead : 14.1.1 With cement mortar 1:4 (1 cement : 4 fine sand) | [5 empty] | 94.05 | 186.4 | 17530.92
|  | ward | sqm | 15 | 1.5 | 1.3 | 1 | 29.25
|  | dialisys room | sqm | 8 | 1.2 | 2 | 1 | 19.2
|  | Toilet room | sqm | 12 | 1.2 | 1.5 | 1 | 21.6
|  | cylinder room | sqm | 8 | 2 | 1.5 | 1 | 24
75 | 14.4.1 | Making the opening in brick masonry including dismantling in floor or walls by cutting masonry and making good the damages to walls, flooring and jambs complete, to match existing surface i/c disposal of mulba/ rubbish to the nearest municipal dumping ground. 14.4.1 For door/ window/ clerestory window | [5 empty] | 5 | 366.65 | 1833.25
|  | Doctors room | each | 1 | 1 | 1 | 1 | 1
|  | dialisys room | each | 1 | 1 | 1 | 1 | 1
|  | VIP room | each | 1 | 1 | 1 | 1 | 1
|  | New passage | each | 2 | 1 | 1 | 1 | 2
76 | 14.5.1 | Renewing glass panes, with putty and nails wherever necessary including racking out the old putty: 14.5.1 Float glass panes of thickness 4 mm | sqm |  |  |  |  | 28.44 | 585.2 | 16643.088
|  | dialisys room | sqm | 5 | 1.2 | 0.45 | 1 | 2.7
|  | VIP room | sqm | 6 | 1.2 | 0.45 | 1 | 3.24
|  | Ward | sqm | 10 | 1.5 | 1.5 | 1 | 22.5
77 | 14.43 | Removing white or colour wash by scrapping and sand papering and preparing the surface smooth including necessary repairs to scratches etc. complete | sqm |  |  |  |  | 136.8 | 5.7 | 779.76
|  | New connection passage | sqm | 2 | 5.2 | 3 | 1 | 31.2
|  | doctors room | sqm | 4 | 3 | 3 | 1 | 36
|  | Nurses room | sqm | 4 | 3 | 3 | 1 | 36
|  | New connection passage ceiling | sqm | 1 | 5.2 | 3 | 1 | 15.6
|  | doctors room ceiling | sqm | 1 | 3 | 3 | 1 | 9
|  | Nurses room ceiling | sqm | 1 | 3 | 3 | 1 | 9
78 | 13.8 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete | Sqm |  |  |  |  | 460.05 | 16.7 | 7682.835
|  | Entrance reception room | Sqm | 2 | 4.85 | 2.1 | 1 | 20.37
|  | Entrance reception room | Sqm | 2 | 5.2 | 2.1 | 1 | 21.84
|  | doctors room | Sqm | 2 | 4.85 | 2.1 | 1 | 20.37
|  | doctors room | Sqm | 2 | 5.35 | 2.1 | 1 | 22.47
|  | doctors room toilet | Sqm | 2 | 5.15 | 2.1 | 1 | 21.63
|  | Bystanders room | Sqm | 2 | 4 | 2.1 | 1 | 16.8
|  | Bystanders room | Sqm | 2 | 3 | 2.1 | 1 | 12.6
|  | VIP room | Sqm | 2 | 5.1 | 2.1 | 1 | 21.42
|  | VIP room | Sqm | 2 | 7.65 | 2.1 | 1 | 32.13
|  | cylinder store | Sqm | 2 | 3.4 | 2.1 | 1 | 14.28
|  | cylinder store | Sqm | 2 | 3.8 | 2.1 | 1 | 15.96
|  | Passage near nurses room | Sqm | 2 | 18 | 2.1 | 1 | 75.6
|  | Passage new | Sqm | 2 | 7.5 | 2.1 | 1 | 31.5
|  | toilet block | Sqm | 2 | 5 | 2.1 | 1 | 21
|  | toilet block | Sqm | 12 | 1.2 | 2.1 | 1 | 30.24
|  | toilet block | Sqm | 12 | 1.5 | 2.1 | 1 | 37.8
|  | Dialysis room | Sqm | 2 | 7.8 | 0.6 | 1 | 9.36
|  | Dialysis room | Sqm | 2 | 5.1 | 0.6 | 1 | 6.12
|  | Nurses room | Sqm | 2 | 3.8 | 2.1 | 1 | 15.96
|  | Nurses room | Sqm | 2 | 3 | 2.1 | 1 | 12.6
79 | 14.53.1 | Wall painting with plastic emulsion paint of approved brand and manufacture to give an even shade : 14.53.1 One or more coats on old work | Sqm |  |  |  |  | 460.05 | 39.3 | 18079.965
|  | Entrance reception room | Sqm | 2 | 4.85 | 2.1 | 1 | 20.37
|  | Entrance reception room | Sqm | 2 | 5.2 | 2.1 | 1 | 21.84
|  | doctors room | Sqm | 2 | 4.85 | 2.1 | 1 | 20.37
|  | doctors room | Sqm | 2 | 5.35 | 2.1 | 1 | 22.47
|  | doctors room toilet | Sqm | 2 | 5.15 | 2.1 | 1 | 21.63
|  | Bystanders room | Sqm | 2 | 4 | 2.1 | 1 | 16.8
|  | Bystanders room | Sqm | 2 | 3 | 2.1 | 1 | 12.6
|  | VIP room | Sqm | 2 | 5.1 | 2.1 | 1 | 21.42
|  | VIP room | Sqm | 2 | 7.65 | 2.1 | 1 | 32.13
|  | cylinder store | Sqm | 2 | 3.4 | 2.1 | 1 | 14.28
|  | cylinder store | Sqm | 2 | 3.8 | 2.1 | 1 | 15.96
|  | Passage near nurses room | Sqm | 2 | 18 | 2.1 | 1 | 75.6
|  | Passage new | Sqm | 2 | 7.5 | 2.1 | 1 | 31.5
|  | toilet block | Sqm | 2 | 5 | 2.1 | 1 | 21
|  | toilet block | Sqm | 12 | 1.2 | 2.1 | 1 | 30.24
|  | toilet block | Sqm | 12 | 1.5 | 2.1 | 1 | 37.8
|  | Dialysis room | Sqm | 2 | 7.8 | 0.6 | 1 | 9.36
|  | Dialysis room | Sqm | 2 | 5.1 | 0.6 | 1 | 6.12
|  | Nurses room | Sqm | 2 | 3.8 | 2.1 | 1 | 15.96
|  | Nurses room | Sqm | 2 | 3 | 2.1 | 1 | 12.6
80 | 14.54.1 | Painting with synthetic enamel paint of approved brand and manufacture of required colour to give an even shade : 14.54.1 One or more coats on old work | Sqm |  |  |  |  | 96 | 35.2 | 3379.2
|  | Window- ward west | Sqm | 7 | 2 | 1.5 | 1.6 | 33.6
|  | Window- dialysis | Sqm | 3 | 2 | 1.5 | 1.6 | 14.4
|  | Window- VIP Room | Sqm | 3 | 2 | 1.5 | 1.6 | 14.4
|  | Entrance reception room | Sqm | 1 | 2 | 1.5 | 1.6 | 4.8
|  | doctors room | Sqm | 1 | 2 | 1.5 | 1.6 | 4.8
|  | Passage | Sqm | 1 | 2 | 1.5 | 1.6 | 4.8
|  | Bystanders room | Sqm | 2 | 2 | 1.5 | 1.6 | 9.6
|  | Nurses room | Sqm | 2 | 2 | 1.5 | 1.6 | 9.6
81 | 14.67.1 | Finishing walls with Premium Acrylic Smooth exterior paint with Silicone additives of required shade :- Old work (Two or more coats applied @ 1.43 ltr/ 10 sqm) over existing cement paint surface | Sqm |  |  |  |  | 542.25 | 62.2 | 33727.95
|  | Exterior area | Sqm | 2 | 33.25 | 4.5 | 1 | 299.25
|  | Exterior area | Sqm | 2 | 16.5 | 4.5 | 1 | 148.5
|  | bystanders room projection | Sqm | 2 | 10.5 | 4.5 | 1 | 94.5
82 | 15.2.1 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge.:- Nominal concrete 1:3:6 or richer mix (i/c equivalent design mix) | cum |  |  |  |  | 5.85 | 671.05 | 3925.6425
|  | Toilet area | cum | 1 | 5 | 3.8 | 0.15 | 2.85
|  | cylinder storage area | cum | 1 | 5 | 4 | 0.15 | 3
83 | 15.3.1 | Demolishing R.C.C. work manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per direction of Engineer - in- charge | cum |  |  |  |  | 4.1175 | 978.95 | 4030.8266
|  | Ward entrance reception room counter | cum | 1 | 5 | 0.75 | 0.15 | 0.5625
|  | Proposed dialysis room counter slab | cum | 1 | 6 | 0.75 | 0.15 | 0.675
|  | RO Plant floor / toilet | cum | 1 | 4 | 3 | 0.16 | 1.92
|  | passage | cum | 1 | 6 | 1 | 0.16 | 0.96
84 | 15.5 | Extra for cutting reinforcement bars manually/ by mechanical means in R.C.C. or R.B. work (Payment shall be made on the cross sectional area of R.C.C. or R.B. work) as per direction of Engineer - in -charge. | Sqm |  |  |  |  | 30 | 325.15 | 9754.5
|  | RO Plant floor / toilet | Sqm | 2 | 4 | 3 | 1 | 24
|  | Proposed dialysis room counter slab | Sqm | 2 | 5 | 0.6 | 1 | 6
85 | 15.7.4 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge | cum |  |  |  |  | 13.6486 | 566.6 | 7733.2968
|  | Proposed dialysis room door opening | cum | 1 | 1 | 0.23 | 2.1 | 0.483
|  | Doctors room door opening | cum | 1 | 1 | 0.23 | 2.1 | 0.483
|  | VIP room door opening | cum | 1 | 1 | 0.23 | 2.1 | 0.483
|  | New passage connection | cum | 1 | 3.6 | 0.23 | 2.1 | 1.7388
|  | New passage connection from passage east | cum | 1 | 3.6 | 0.23 | 2.1 | 1.7388
|  | Toilet wall | cum | 5 | 1.5 | 0.18 | 3 | 4.05
|  | Toilet wall | cum | 1 | 2.3 | 0.18 | 3 | 1.242
|  | RO Plant sink / toilet | cum | 1 | 2 | 0.2 | 3 | 1.2
|  | RO Plant door to wash area | cum | 1 | 2 | 0.23 | 2.5 | 1.15
|  | RO Plant sink / toilet | cum | 3 | 1.5 | 0.2 | 1.2 | 1.08
86 | 15.23.1 | Dismantling tile work in floors and roofs laid in cement mortar including stacking material within 50 metres lead.: For thickness of tiles 10 mm to 25 mm | sqm |  |  |  |  | 123.714 | 20.3 | 2511.3942
|  | VIP room | sqm | 1 | 7.64 | 5.1 | 1 | 38.964
|  | Passage near nurses room | sqm | 1 | 12 | 1.8 | 1 | 21.6
|  | Nurses room | sqm | 1 | 3.8 | 3 | 1 | 11.4
|  | Bystanders room | sqm | 1 | 4 | 3 | 1 | 12
|  | cylinder store | sqm | 1 | 3.8 | 5 | 1 | 19
|  | toilet block | sqm | 1 | 5 | 4.15 | 1 | 20.75
87 | LMR | Dismantling mosaic / tile work in dado laid in cement mortar including12mm thick cement plaster stacking material within 50 metres lead.: For thickness of tiles 5 mm to 10 mm | sqm |  |  |  |  | 308.35 | 80 | 24668
|  | Proposed dialysis room wall | sqm | 2 | 8 | 3.2 | 1 | 51.2
|  | Proposed dialysis room wall | sqm | 2 | 5.5 | 3.2 | 1 | 35.2
|  | Ward skirting | sqm | 2 | 11 | 0.2 | 1 | 4.4
|  | Ward skirting | sqm | 2 | 16 | 0.2 | 1 | 6.4
|  | VIP room dado | sqm | 2 | 8 | 3 | 1 | 48
|  | VIP room dado | sqm | 1 | 5.5 | 3 | 1 | 16.5
|  | Passage near nurses room dado | sqm | 2 | 12 | 1.5 | 1 | 36
|  | Passage near nurses room | sqm | 1 | 2 | 1.5 | 1 | 3
|  | Nurses room skirting | sqm | 2 | 4 | 0.2 | 1 | 1.6
|  | Nurses room | sqm | 2 | 3 | 0.2 | 1 | 1.2
|  | Nurses room toilet | sqm | 2 | 3.8 | 1.5 | 1 | 11.4
|  | Nurses room toilet | sqm | 4 | 1.3 | 1.5 | 1 | 7.8
|  | Bystanders room skirting | sqm | 1 | 4 | 1.5 | 1 | 6
|  | Bystanders room skirting | sqm | 1 | 3 | 1.5 | 1 | 4.5
|  | Toilet block dado east portion | sqm | 2 | 4 | 1.5 | 1 | 12
|  | Toilet block dado | sqm | 2 | 3.6 | 1.5 | 1 | 10.8
|  | Toilet block dado west portion | sqm | 2 | 5 | 1.5 | 1 | 15
|  | toilet block | sqm | 6 | 4.15 | 1.5 | 1 | 37.35
88 | 15.48 | Taking out C.I. cover with frame from R.C.C. top slab of manholes of various sizes including demolishing of R.C.C. work manually/ by mechanical means and stacking of useful materials near the site and disposal of unserviceable materials within 50 metres lead as per direction of Engineer-in-charge | each |  |  |  |  | 2 | 198.25 | 396.5
|  | New passage area | each | 1 | 2 | 1 | 1 | 2
89 | 15.56 | Dismantling old plaster or skirting raking out joints and cleaning the surface for plaster including disposal of rubbish to the dumping ground within 50 metres lead. | Sqm |  |  |  |  | 250.5 | 15 | 3757.5
|  | Ward wall | Sqm | 2 | 1 | 16 | 3.25 | 104
|  | Ward wall | Sqm | 2 | 1 | 11 | 3.25 | 71.5
|  | Ward columns | Sqm | 12 | 1 | 0.5 | 3.25 | 19.5
|  | Dining room wall | Sqm | 2 | 1 | 4 | 1.6 | 12.8
|  | Dining room wall | Sqm | 2 | 1 | 3 | 1.6 | 9.6
|  | Nurses room wall | Sqm | 2 | 1 | 3.8 | 1.6 | 12.16
|  | Nurses room wall | Sqm | 2 | 1 | 3 | 1.6 | 9.6
|  | Doctors room door opening | Sqm | 2 | 1 | 0.6 | 2.1 | 2.52
|  | VIP room door opening | Sqm | 2 | 1 | 0.6 | 2.1 | 2.52
|  | toilet block | Sqm | 6 | 1 | 0.5 | 2.1 | 6.3
90 | 15.57 | Dismantling aluminium/ Gypsum partitions, doors, windows, fixed glazing and false ceiling including disposal of unserviceable surplus material and stacking of serviceable material with in 50 meters lead as directed by Engineer-in-charge | Sqm |  |  |  |  | 117.1 | 15.9 | 1861.89
|  | Proposed dialysis room false ceiling | Sqm | 1 | 8 | 5.5 | 1 | 44
|  | VIP room aluminum door | Sqm | 1 | 1 | 2.2 | 1 | 2.2
|  | ward aluminum partitions | Sqm | 1 | 16 | 2.5 | 1 | 40
|  | ward aluminum partitions | Sqm | 1 | 4 | 2.5 | 1 | 10
|  | dialysis room aluminum door | Sqm | 1 | 1 | 2.2 | 1 | 2.2
|  | PVC toilet door | Sqm | 10 | 0.75 | 2.2 | 1 | 16.5
|  | doctors room aluminum door | Sqm | 1 | 1 | 2.2 | 1 | 2.2
91 | 15.12.1 | Dismantling doors, windows and clerestory windows (steel or wood) shutter including chowkhats, architrave, holdfasts etc. complete and stacking within 50 metres lead as directed by Engineer-in-charge | cum |  |  |  |  | 29 | 15.9 | 461.1
|  | Proposed dialysis room window | cum | 2 | 1 | 1 | 1 | 2
|  | VIP room steel window | cum | 3 | 1 | 1 | 1 | 3
|  | ward steel window | cum | 6 | 1 | 1 | 1 | 6
|  | Window at new conection passage | cum | 3 | 1 | 1 | 1 | 3
|  | ventilator at proposed sink room/ dialysis | cum | 4 | 1 | 1 | 1 | 4
|  | PVC toilet door | cum | 10 | 1 | 1 | 1 | 10
|  | doctors room aluminum door | cum | 1 | 1 | 1 | 1 | 1
92 | 14.2.2 | Fixing steel windows in existing opening including embedding in floors or walls cutting masonry for hold fasts,embedding hold fasts in cement concrete blocks of size 15 x 10 x 10 cm with cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size), and making good the damages to walls and floors as required complete, including disposal of rubbish to the dumping ground within 50 meters lead | each |  |  |  |  | 14 | 15.9 | 222.6
|  | Proposed dialysis room window | each | 2 | 1 | 1 | 1 | 2
|  | VIP room steel window | each | 3 | 1 | 1 | 1 | 3
|  | ward steel window | each | 6 | 1 | 1 | 1 | 6
|  | Window at new conection passage | each | 3 | 1 | 1 | 1 | 3
93 | 15.6 | Disposal of building rubbish / malba / similar unserviceable, dismantled or waste materials by mechanical means, including loading, transporting, unloading to approved municipal dumping ground or as approved by Engineer-in-charge, beyond 50 m initial lead, for all leads including all lifts involved | cum |  |  |  |  | 33.6695 | 101.75 | 3425.8716
|  | Total demolished materials floor | cum | 1 | 16 | 10 | 0.05 | 8
|  | Total demolished materials wall passage | cum | 2 | 3.6 | 0.23 | 2.1 | 3.4776
|  | Total demolished materials toilet floor | cum | 1 | 10 | 9 | 0.05 | 4.5
|  | Total demolished materials toilet wall | cum | 3 | 1.3 | 0.18 | 2.1 | 1.4742
|  | Ward wall | cum | 2 | 0.025 | 15.7 | 1.5 | 1.1775
|  | Ward wall | cum | 2 | 0.025 | 10.6 | 1.5 | 0.795
|  | Ward columns | cum | 12 | 0.025 | 0.5 | 1.5 | 0.225
|  | Dining room wall | cum | 2 | 0.025 | 4 | 1.5 | 0.3
|  | Dining room wall | cum | 2 | 0.025 | 3 | 1.5 | 0.225
|  | Nurses room wall | cum | 2 | 0.025 | 3.8 | 1.5 | 0.285
|  | Nurses room wall | cum | 2 | 0.025 | 3 | 1.5 | 0.225
|  | Doctors room door opening | cum | 2 | 0.025 | 0.6 | 2.1 | 0.063
|  | VIP room door opening | cum | 2 | 0.025 | 0.6 | 2.1 | 0.063
|  | toilet block | cum | 6 | 0.025 | 0.5 | 2.1 | 0.1575
|  | Total demolished materials toilet wall | cum | 1 | 2.5 | 0.18 | 2.1 | 0.945
|  | Proposed dialysis room wall | cum | 2 | 7.8 | 3 | 0.035 | 1.638
|  | Proposed dialysis room wall | cum | 2 | 5.1 | 3 | 0.035 | 1.071
|  | Ward skirting | cum | 2 | 10.7 | 0.15 | 0.035 | 0.11235
|  | Ward skirting | cum | 2 | 15.7 | 0.15 | 0.035 | 0.16485
|  | VIP room dado | cum | 2 | 7.64 | 3 | 0.035 | 1.6044
|  | VIP room dado | cum | 1 | 5.1 | 3 | 0.035 | 0.5355
|  | Passage near nurses room dado | cum | 2 | 12 | 1.5 | 0.035 | 1.26
|  | Passage near nurses room | cum | 1 | 1.8 | 1.5 | 0.035 | 0.0945
|  | Nurses room skirting | cum | 2 | 3.8 | 0.15 | 0.035 | 0.0399
|  | Nurses room | cum | 2 | 3 | 0.15 | 0.035 | 0.0315
|  | Nurses room toilet | cum | 2 | 3.8 | 0.15 | 0.035 | 0.0399
|  | Nurses room toilet | cum | 4 | 1.3 | 0.15 | 0.035 | 0.0273
|  | Bystanders room skirting | cum | 1 | 4 | 0.15 | 0.035 | 0.021
|  | Bystanders room skirting | cum | 1 | 3 | 0.15 | 0.035 | 0.01575
|  | Toilet block dado east portion | cum | 2 | 3.8 | 1.5 | 0.035 | 0.399
|  | Toilet block dado | cum | 2 | 3.4 | 1.5 | 0.035 | 0.357
|  | Toilet block dado west portion | cum | 2 | 5 | 1.5 | 0.035 | 0.525
|  | toilet block | cum | 6 | 4.15 | 1.5 | 0.035 | 1.3073
|  | Proposed dialysis room counter slab-RCC | cum | 1 | 5 | 0.6 | 0.1 | 0.3
|  | Ward entrance reception room -RCC | cum | 1 | 5 | 0.6 | 0.1 | 0.3
|  | VIP room foor | cum | 1 | 7.5 | 5.1 | 0.05 | 1.9125
94 | 19.21.1 | 19.21 Making connection of drain or sewer line with existing manhole including breaking into and making good the walls, floors with cement concrete 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) cement plastered on both sides with cement mortar 1:3 (1 cement : 3 coarse sand), finished with a floating coat of neat cement and making necessary channels for the drain etc. complete : 19.21.1 For pipes 100 to 250 mm diameter | each |  |  |  |  | 5 | 275 | 1375
|  | Drain from dialysis room | each | 2 | 1 | 1 | 1 | 2
|  | Drain from toilet | each | 3 | 1 | 1 | 1 | 3
95 | 19.26.1 | Raising manhole cover and frame slab to required level including dismantling existing slab and making good the damage as required (Raising depth of manhole to be paid eparately) : Rectangular manhole 90x80 cm with rectangular cover 600x450 mm of grade LD - 2.5 | each |  |  |  |  | 4 | 1239.7 | 4958.8
|  | New passage | each | 1 | 1 | 1 | 1 | 1
|  | Drain from toilet | cum | 3 | 1 | 1 | 1 | 3
96 | 19.8.1.1 | Extra for depth for manholes : 19.8.1 Size 90x80 cm:- With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | metre |  |  |  |  | 2 | 4061.7 | 8123.4
|  | New passage | metre | 2 | 1 | 1 | 1 | 2
97 | 19.15.2 | Providing M.S. foot rests including fixing in manholes with 20x20x10 cm cement concrete blocks 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) as per standard design : With 20 mm diameter round bar | each |  |  |  |  | 10 | 193.15 | 1931.5
|  | New passage | each | 2 | 5 | 1 | 1 | 10
|  | Total (SR+LMR) | [7 empty] | 3521575.9678
|  | Total SR Amount | [7 empty] | 2844679.4278
|  | Total LMR Amount | [7 empty] | 676896.54
| Assistant Project Engineer |  |  |  |  | Project Manager
| HLL Lifecare Ltd. |  |  |  |  | HLL Lifecare Ltd.

## PART A -CIVIL WORK
CONVERSION OF WARD # 27 IN TO GERIATRIC HIGH DEPENDENCY UNIT AT MEDICAL COLLEGE KOTTAYAM DISTRICT.
Part A - CIVIL WORKS
Item No | Code No. | Description of Item | Quantity | Unit | Rate in figures & words Rs | Amount Rs
SUB HEAD: I EARTH WORK
1 | 2.8.1 | Earth work in excavation in foundation trenches or drains ( not exceeding 1.5m in width or 10 sqm on plan ) including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of urplus excavated soil as directed, within a lead of 50 m :- All kinds of soil . | 14.4 | cum
2 | 2.27 | Supplying and filling in plinth with river sand/quarry dust under floors including watering, ramming consolidating and dressing complete. | 16.5359 | cum
3 | 2.25 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth: consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m | 8.1648 | cum
SUB HEAD : II PLAIN CEMENT CONCRETE
4 | 4.1.10 | Providing and laying in position cement concrete of specified grade excluding the cost of centring and shuttering - All work upto plinth : 1 : 5 : 10 (1 Cement : 5 coarse sand :10 graded stone aggregate 40mm nominal size) | 9.4574 | cum
5 | 11.3.1 | Cement concrete flooring 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate) finished with a floating coat of neat cement including cement slurry, but excluding the cost of nosing of steps etc. complete. 11.3.1 40mm thick with 20mm nominal size stone aggregate. | 12 | Sqm
6 | 4.17 | Making plinth protection 50 mm thick of cement concrete 1:3:6 (1 cement :3 coarse sand: 6 graded stone aggregate 20 mm nominal size )over 75 mm bed of dry brick ballast 40 mm nominal size well rammed and consolidated and grouted with fine sand including finishing the top smooth. | 8.04 | Sqm
SUB HEAD III : REINFORCED CEMENT CONCRETE
7 | 5.1.2 | Providing and laying in position specified grade of reinforced cement concrete excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level :1.5:3 (1 cement : 1.5 coarse sand : 3 graded stone aggregate 20 mm nominal size) | 1.422 | cum
8 | 5.1.2+ (5.3- 5.1.3) | Reinforced cement concrete work in beams, suspended floors, roofs having slope upto 15°, landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases upto floor five level including the cost of centring, shuttering, finishing and excluding the cost of reinforcement with 1:1.5:3 (1 cement : 1.5 coarse sand: 3 graded stone aggregate 20 mm nominal size). | 7.0063 | cum
9 | 5.9.5 | Centering and shuttering including strutting, propping etc. and removal of form for : Lintels, beams, plinth beams, girders, bressumers and cantilevers | 9.917 | Sqm
10 | 5.22.6 | Reinforcement for reinforced cement concrete works including straightening, cutting, bending, binding and placing in position all complete:- TMT bars | 1011.3984 | kg
SUB HEAD IV : BRICK WORK
11 | 6.4.2 | Brick work with bricks of class designation 75 in superstructure above plinth level upto floor V level.cement mortar 1 : 6 ( 1 cement : 6 coarse sand ). | 33.99 | cum
12 | 6.13.2 | Half brick masonry with bricks of class designation 75 in super structure & above plinth up to floor V level in cement mortar 1 : 4 ( 1 cement : 4 coarse sand ). | 27.04 | Sqm
13 | 6.15 | Extra for providing and placing in position 2 Nos 6 mm dia M.S. bars at every third course of half brick masonary ( with F.P.S. bricks). | 27.04 | Sqm
SUB HEAD :V MARBLE WORK
14 | 8.2.2.2 | Providing and fixing 18 mm thick mirror polished, machine cut for kitchen platforms, vanity counters facias and similar locations of required size of approved shade, colour and texture laid over 20 mm thick base cement mortar 1 : 4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing etc. complete at all levels :- Granite black area of slab : | 15.97 | Sqm
15 | 8.3.2 | Extra for providing edge moulding to 18mm thick marble counters, Vanities etc. including machine polishing to dege to give high gloss finish etc. complete as per design approved by Engineer-in-charge:- Granite work | 24.18 | Rm
SUB HEAD VI : STONE WORK
16 | 7.1.1 | Random rubble masonry with hard stone in foundation and plinth including levelling up with cement concrete 1:6:12 (1 cement : 6 coarse sand : 12 graded stone aggregate 20 mm nominal size) upto plinth level with : Cement mortar 1:6 (1 cement : 6 coarse sand | 15.4246 | cum
SUB HEAD VII : STEEL WORK
17 | 9.48.2 | Providing and fixing M.S. grills of required pattern in frames of windows etc. with M.S. flats, square or round bars etc. including priming coat with approved steel primer all complete. Fixed to openings /wooden frames with rawl plugs screws etc. | 715.05 | kg
18 | 10.16.1 | Steel work in built up tubular ( round, square or rectangular hollow tubes etc.) trusses etc., including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer, including welding and bolted with special shaped washers etc. complete. 10.16.1 Hot finished welded type tubes | 352.7784 | kg
SUB HEAD VIII : FLOORING
19 | LMR | Providing and fixing Ist quality ceramic glazed joint free wall tiles minimum thickness 8MM of approved make JOHNSON, NITCO, ORIENT, , KAJARIA or approved make, in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete. Size 450x300mm | 483.7976 | Sqm
20 | 11.36 | Providing and fixing Ist quality ceramic glazed joint free wall tiles conforming to IS: 15622 Of thickness 5MM of approved make JOHNSON, NITCO, ORIENT, , KAJARIA or approved make, in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) sand jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete. Size | 258.295 | Sqm
21 | 11.37 | Providing and laying Ceramic glazed joint free floor tiles of size 400x400 mm (thickness to be pecified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make JOHNSON, NITCO, ORIENT, , KAJARIA etc in colours such as White, Ivory, Grey, Fume Red Brown, laid on 20 mm thick cement mortar 1:4 (1 Cement : 4 Coarse sand), including pointing the joints with white cement and matching pigment etc., complete | 42.4 | Sqm
22 | 11.37 | Providing and laying Ceramic Unglazed joint free floor tiles of size 300x300 mm (thickness to be pecified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make JOHNSON, NITCO, ORIENT, , KAJARIA in colours such as White, Ivory, Grey, Fume Red Brown, laid on 20 mm thick cement mortar 1:4 (1 Cement : 4 Coarse sand), including pointing the joints with white cement and matching pigment etc., complete | 41.8 | Sqm
23 | 11.41.2 | Providing and laying vitrified floor tiles in different sizes (thickness to be specified by the manufacturer) 10mm with water absorption less than 0.08% and conforming to IS : 15622, of approved make JOHNSON, NITCO, ORIENT, , KAJARIA , in all colours and shades, laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand),or 5mm thick tile adhesive including grouting the joints with white cement and matching pigments etc., complete as directed by the Engineer in Charge. lobby- size 600x600mm | 326.34 | Sqm
SUB HEAD IX : ROOFING
24 | 12.1.3 | Providing corrugated G.S. sheet roofing including vertical / curved surface fixed with polymer coated J or L hooks, bolts and nuts 8 mm diameter with bitumen and G.I. limpet washers or with G.I. limpet washers filled with white lead, including a coat of approved steel primer and two coats of approved paint on overlapping of sheets complete (up to any pitch in horizontal/ vertical or curved surfaces), excluding the cost of purlins, rafters and trusses and including cutting to size and shape wherever required:- 0.63 mm thick with zinc coating not less than 275 gm/ m² | 48.8 | Sqm
25 | 12.4.2 | Providing ridges or hips of width 60 cm overall width plain G.S. sheet fixed with polymer coated J. or L hooks, bolts and nuts 8 mm dia G.I. limpet and bitumen washers complete:- 0.63 mm thick with zinc coating not less than 275 gm/m² | 7.5 | Rm
26 | 12.41.2 | Providing and fixing on wall face unplasticised - Rigid P.V.C rain water pipes conforming to IS : 13592 Type - A including jointing with seal ring conforming to IS : 5382 leaving 10 mm gap for thermal expansion :- 4kg/m 110 mm diameter single socketed pipes . | 20 | Rm
27 | 12.43.2 | Providing and fixing unplasticised-P.V.C pipes clips of approved design to unplasticised-P.V.C rain water pipes by means of 50 x 50 x 50 mm hard wood plugs, screwed with M.S screws of required length including cutting brick work and fixing in cement mortar 1 : 4 ( 1 cement : 4 coarse sand ) and making good the walls etc. complete :- a) 110 mm . | 12 | each
28 | 12.42 | Providing and fixing on wall face unplasticised -P.V.C moulded fittings / accessories for unplasticised - Rigid P.V.C rain water pipes conforming to IS : 13592 Type A including jointing with seal ring conforming to IS 5382 leaving 10 mm gap for thermal expansion :-
a | 12.42.5. | Bend 87.5 degree:
| 12.42.5.2 | 110mm T / Y Bend " | 12 | Each
b | 12.42.6 | Shoe plain :- "
| 12.42.6.2 | 110 mm shoe. " | 10 | Each
29 | 12.53 | Providing and Fixing 15 mm thick densified tegular edged eco friendly light weight calcium silicate false ceiling tiles of approved texture spintone/cosmos / Hexa or equivalent of size 595 x 595 mm in true horizontal level, suspended on inter locking metal grid of hot dipped galvanised steel sections (galvanising @ 120 grams per sqm including both side) consisting of main 'T' runner suitably spaced at joints to get required length and of size 24x38 mm made from 0.33 mm thick (minimum) sheet, spaced 1200 mm centre to centre, and cross "T" of size 24x28 mm made out of 0.33 mm (Minimum) sheet, 1200 mm long spaced between main'T' at 600 mm centre to centre to form a grid of 1200x600 mm and secondary cross 'T' of length 600 mm and size 24 x28 mm made of 0.33 mm thick (Minimum) sheet to be inter locked at middle of the 1200x 600 mm panel to from grid of size 600x600 mm, resting on periphery walls /partitions on a Perimeter wall angle pre-coated steel of ize(24x24X3000 mm made of 0.40 mm thick (minimum) sheet with the help of rawl plugs at 450 mm centre to centre with 25 mm long dry wall screws @ 230 mm interval and laying 15 mm thick densified edges calicum silicate ceiling tiles of approved texture (Spintone / Cosmos/hexa) in the grid, including, | 275 | Sqm
cutting/ making opening for services like diffusers, grills, light fittings, fixtures, smoke detectors etc., wherever required. Main 'T' runners to be suspended from ceiling using G.I. slotted cleats of size 25x35x1.6 mm fixed to ceiling with 12.5 mm dia and 50 mm long dash fasteners, 4 mm G.I. adjustable rods with galvanised steel level clips of size 85 x 30 x 0.8 mm, spaced at 1200 mm centre to centre along main 'T' , bottom exposed with 24 mm of all T-sections shall be pre-painted with polyster baked paint, for all heights, as per specifications, drawings and as directed by engineer-in-charge. Note :- Only calcium silicate false ceiling area will be measured from wall to wall. No deduction shall be made for exposed frames/opening (cut outs) having area less than 0.30 sqm.The calcium silicate ceiling tile shall have NRC value of 0.50 (Minimum), light reflection > 85%, non - combustible as per B.S. 476 part IV, 100% humidity resistance and also having thermal conductivity <0.043 w/m 0 KC.
SUB HEAD X : FINISHING
30 | 13.1.1 | 12mm cement plaster of mix in fine sand, 1:4(1cement : 4 fine sand) | 227.5625 | Sqm
31 | 13.2.2 | 15mm cement plaster on rough sides of single or half brick wall plaster of mix in1:6 (1 cement:6 coarse sand | 284.0125 | Sqm
32 | 13.60.1 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade :-Two or more coats on new work . | 113.7125 | Sqm
33 | 13.43.1 | Applying one coat of cement primer of approved brand and manufacture on wall surface for plastic emulsion | 113.7125 | Sqm
34 | 13.47.1 | Finishing walls with Premium Acrylic Smooth exterior paint with Silicone additives of required shade 13.47.1 New work (Two or more coats applied @ 1.43 ltr/ 10 sqm. over and including base coat of water proofing cement paint applied @ 2.20 kg/ 10 sqm | 482 | Sqm
35 | 13.50.3 | Applying priming coat :With ready mixed red oxide zinc chromate primer of approved brand and manufacture on steel galvanised iron/steel works | 22.2573 | Sqm
36 | 13.61.1 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade : Two or more coats on new work | 51.3273 | Sqm
SUB HEAD XI : PVC WORKS MISCELLANEOUS
37 | 9.117.1 | Providing and fixing factory made uPVC door frame made of uPVC extruded sections having an overall dimension as below (tolerance ±1mm), with wall thickness 2.0 mm (± 0.2 mm), corners of the door frame to be Jointed with galvanized brackets and stainless steel screws, joints mitred and Plastic welded. The hinge side vertical of the frames reinforced by galvanized M.S. tube of size 19 X 19 mm and 1mm (± 0.1 mm) wall thickness and 3 nos. stainless steel hinges fixed to the frame complete as per manufacturer’s specification and direction of Engineer-in-charge : - Extruded section profile size 48x40 mm | 39.6 | Rm
38 | 9.120.2 | Providing and fixing factory made panel PVC door shutter consisting of frame made out of M.S. tubes of 19 gauge thickness and size of 19 mm x 19 mm for styles and 15x15 mm for top & bottom rails. M.S. frame shall have a coat of steel primers of approved make and manufacture . M.S. frame covered with 5 mm thick heat moulded PVC 'C' channel of size 30 mm thickness, 70 mm width out of which 50 mm shall be flat and 20 mm shall be tapered in 45 degree angle on both side forming styles and 5 mm thick, 95 mm wide PVC sheet out of which 75 mm shall be flat and 20 mm shall be tapered in 45 degree on the inner side to form top and bottom rail and 115 mm wide PVC sheet out of which 75 mm shall be flat and 20 mm shall be tapered on both sides to form lock rail. Top, bottom and lock rails shall be provided both side of the panel. 10 mm (5 mm x 2 ) thick, 20 mm wide cross PVC sheet be provided as gap insert for top rail & bottom rail, paneling of 5 mm thick both side PVC sheet to be fitted in the M.S. frame welded/ sealed to the styles & rails with 7 mm (5 mm+2 mm) thick x 15 mm wide PVC sheet beading on inner side, and joined together with solvent cement adhesive. An additional 5 mm thick PVC strip of 20 mm width is to be stuck on the interior side of the 'C' Channel using PVC solvent adhesive etc. complete as per direction of Engineer-in-charge, manufacturer's specification & drawing. :- 30 mm thick pre laminated PVC door shutters | 12.6 | Sqm
SUB HEAD XII : SERVICES
SANITARY INSTALLATIONS
39 | 17.2.1 | Providing and fixing white vitreous china pedestal type water closet (European type W.C. pan) with seat and lid, 10 litre low level white P.V.C. flushing cistern, including flush pipe, with manually controlled device (handle lever), conforming to IS : 7231, with all fittings and fixtures complete, including cutting and making good the walls and floors wherever required : W.C. pan with ISI marked white solid plastic seat and lid | 5 | Each
40 | 17.7.4 | Providing and fixing wash basin with C.I. brackets, 15 mm C.P. brass pillar taps, 32 mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever require :White Vitreous China Flat back wash basin size 550x 400 mm with single 15 mm C.P. brass pillar tap | 2 | Each
41 | 17.31 | Providing and fixing 600x450 mm beveled edge mirror of superior glass (of approved quality) complete with 6 mm thick hard board ground fixed to wooden cleats with C.P. brass screws and washers complete | 2 | each
42 | 18.65 | Providing and fixing PTMT soap Dish Holder having length of 138mm,breadth 102mm, height of 75mm with concealed fitting arrangements, weighing not less than 106 gms | 7 | each
43 | 17.73.2 | Providing and fixing PTMT towel rail complete with brackets fixed to wooden cleats with CP brass screws with concealed fittings arrangement of approved quality and colour:. 600 mm long towel rail with total length of 645 mm, width 78 mm and effective height of 88 mm, weighting not less than 190 gms. | 10 | each
44 | 17.28.2.1 | Providing and fixing P.V.C. waste pipe for sink or wash basin including P.V.C. waste fittings complete :-Flexible pipe :-32 mm dia. | 7 | each
45 | 12.41 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion,(i) Single socketed pipes
a | 12.41.1 | 75 mm diameter | 30 | Rm
b | 12.41.2 | 110 mm diameter | 30 | Rm
46 | LMR | Providing & fixing bend of required degree with acess door,insertion rubber washer 3 mm thick bolts,nuts complete
a | LMR | 75 mm | 6 | Each
b | LMR | 110 mm | 5 | Each
47 | 2.10.1.2 | excavating trenches of required width for pipes ,cables,etcincluding excavation for sockets and dressing of sides ramming of bottom depth up to 1.5 mincluding getting out the excavated soil and then returning the soil as required in layers not exceeding 20 cm in depth including consolidating each deposited layer by ramming watering etc and desposing of surplus ecavated soilas directed within a lead of 50 m. all kinds of soil . | 60 | Rm
48 | 19.2 | providing and laying c.c 1:5:10 all round p v c pipes including bed concrete as per standard design.
a | 19.2.1 | 100 mm | 30 | Rm
49 | LMR | Providing and fixing PVC pipe including cutting chasng in walls and making good the walls etc complete. (Concealed)10kg/m
a | LMR | 20 mm pipe | 45 | Rm
b | LMR | 25 mm pipe | 24 | Rm
c | LMR | 32mmpipe | 10 | Rm
50 | LMR | Providing and fixing PVC pipe including cutting chasng in walls and making good the walls etc complete. (External) 10kg/m
a | LMR | 20mm( OD ) pipe external | 20 | Rm
b | LMR | 25 mm( OD ) pipe | 15 | Rm
c | LMR | 32 mm( OD ) pipe | 10 | Rm
51 | 18.7 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer in Charge: Internal work - Exposed on wall
a | 18.7.2 | 20mm( OD ) pipe external | 17 | Rm
b | 18.7.3 | 25 mm( OD ) pipe | 17 | Rm
c | 18.7.4 | 32 mm( OD ) pipe | 17 | Rm
52 | 18.51.1 | Providing and fixing C.P. brass long body bib cock of approved quality conforming to IS standards and weighing not less than 690 gms.15 mm nominal bore | 11 | each
53 | 18.16.1 | Providing and fixing C.P. brass stop cock (concealed) of standard design and of approved make conforming to IS 8931 :- 15 mm nominal bore | 19 | each
54 | 18.17 | Providing and fixing gun metal valve with C I wheel of approved quality (screwed end ):-
a | LMR | 20mm dia nominal bore | 5 | each
b | 18.17.1 | 25mm dia nominal bore | 5 | each
c | 18.17.2 | 32 mm dia nominal bore | 3 | each
55 | 18.21.2.2 | Providing and fixing unplasticised P.V.C connection pipe with brass unions :- 20 mm nominal bore. | 9 | each
56 | 17.60.2.1 | Providing and fixing PVC trap of self cleansing design with PVC screwed down or hinged CP grating with or without vent arm complete including cutting and making good the walls and floors. a)100mm inlet and 75mm outlet. | 12 | each
57 | 19.7.1.1 | Constructing brick masonry manhole in cement mortar 1 : 4 (1 cement : 4 coarse sand) R.C.C. top slab with 1 : 2 : 4 mix ( 1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), foundation concrete 1 : 4 : 8 mix (1 cement : 4 coarse sand : 8 graded stone aggregate 40 mm nominal size) inside plastering 12mm thick with cement mortar 1 : 3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1: 2 : 4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design Inside size 90 x 80 cm and 45 cm deep including C.I. cover with frame ( light duty ) 455 x 610 mm internal dimensions, total weight of cover and frame to be not less than 38 kg (weight of cover 23 kg and weight of frame 15 kg) With F.P.S bricks with class designation 50 | 9 | each
58 | 19.8.1.1 | Extra for depth for manholes :-With F.P.S bricks with class designation 50 | 2 | Rm
59 | 19.33 | Constructing soak pit 1.20 x 1.20 x 1.20 m filled with brickbats including S.W. drain pipe 100 mm diameter and 1.20 m long complete as per standard design. | 5 | each
60 | 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank ISI : 12701 marked indicating the BIS License No. with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank [Sintex, Electroplast, Star, Lotus or equivalent having valid ISI license]. | 4000 | Litre
SUB HEAD XIII : ALUMINIUM WORK
61 | 21.1.1.2 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS : 1285, fixed with rawl plugs and screws or with fixing clips, or with expansion hold fasteners including necessary filling up of gaps at junctions, at top, bottom and sides with required PVC/neoprene felt etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing and paneling to be paid for separately) : For fixed portion Powder coated aluminium (minimum thickness of powder coating 50 micron) | 554.3364 | kg
62 | 21.1.2.1 | For shutters of doors, windows & ventilators including providing and fixing hinges/ pivots and making provision for fixing of fittings wherever required including the cost of PVC / neoprene gasket required (Fittings shall be paid for separately). Anodised aluminium (anodised transparent or dyed to required shade according to IS: 1868, Minimum anodic coating of grade AC 15) | 408.4901 | kg
63 | 21.2.2 | Providing and fixing 12mm thick prelaminated particle board flat pressed three layer or graded wood particle board conforming to IS: 12823 Grade l Type ll, in panelling fixed in aluminum doors, windows shutters and partition frames with C.P. brass / stainless steel screws etc. complete as per architectural drawings and directions of engineer-in-charge. Pre-laminated particle board with decorative lamination on both sides. | 28.55 | Sqm
64 | 21.3.2 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with PVC/ neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.50 mm thickness | 96.2125 | Sqm
65 | 21.4.1 | Providing and fixing double action hydraulic floor spring of approved brand and manufacture IS : 6315 marked, Hardwyn make (model 3000) or equivalent for doors including cost of cutting floors as required, embedding in floors and cover plates with brass pivot and single piece M.S. sheet outer box with slide plate etc. complete as per the direction of Engineer-in-charge With Stainless Steel cover plate | 10 | each
66 | 9.97 | providing and fixing aluminium tower bolt ISI markedanodised (anodise coating not less than grade AC 10 as per IS:1868) transperent dyed to required color or shade with ss screws etc complete
a | 9.97.3 | 200 x 10 mm | 11 | each
b | 9.97.2 | 250 x 10 mm | 11 | each
67 | 21.8.1 | Filling the gap in between aluminium frame & adjacent RCC/ Brick/ Stone work by providing weather silicon sealant over backer rod of approved quality as per architectural drawings and direction of Engineer-in-charge complete. : Upto 5mm depth and 5 mm width | 91.2 | Rm
68 | 21.13 | providing and fixing 100 mm brass lock (best make of approved quality) for aluminium door including necessary cutting and macking good etc complete as per the direction of engineer in charge.Anodized | 11 | each
69 | LMR | Providing and fixing non reflective polyster film of approved make and clour with self adhesive to glazed windows/doors (to make opaque) | 107.9247 | Sqm
70 | LMR | Removing and refixing the existing aluminum door after rectification with new pivot/ hinge ,weather strip etc complete | 10.92 | Sqm
71 | 9.84 | Providing and fixing aluminium extruded section body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 36 kg to 80 kg and door width from 701 mm to 1000 mm), with double speed adjustment with necessary accessories and screws etc. complete | 10 | each
SUB HEAD : XIV: WATER PROOFING
72 | 22.5 | Providing and laying water proofing treatment in sunken portion of WCs, bathroom etc., by applying cement slurry mixed with water proofing cement compound consisting of applying : a) First layer of slurry of cement @ 0.488 kg/sqm mixed with water proofing cement compound @ 0.253 kg/sqm. This layer will be allowed to air cure for 4 hours. b) Second layer of slurry of cement @ 0.242 kg/sqm mixed with water proofing cement compound @ 0.126 kg/sqm. This layer will be allowed to air cure for 4 hours followed with water curing for 48 hours. The rate includes preparation of surface, treatment and sealing of all joints, corners, junctions of pipes and masonry with polymer mixed slurry. | 38.5225 | Sqm
SUB HEAD XV : REPAIR AND MAINTENANCE
73 | 14.12 | Providing and fixing 16 mm M.S. Fan clamps of standard shape and size in existing R.C.C. slab, including cutting chase, anchoring clamp to reinforcement bar, including cleaning, refilling, making good the chase with matching concrete, plastering and painting the exposed portion of the clamps complete | 10 | Each
74 | 14.1.1 | Repairs to plaster of thickness 12 mm to 20 mm in patches of area 2.5 sq. meters and under, including cutting the patch in proper shape, raking out joints and preparing and plastering the surface of the walls complete, including disposal of rubbish to the dumping ground within 50 metres lead : 14.1.1 With cement mortar 1:4 (1 cement : 4 fine sand) | 94.05 | Sqm
75 | 14.4.1 | Making the opening in brick masonry including dismantling in floor or walls by cutting masonry and making good the damages to walls, flooring and jambs complete, to match existing surface i/c disposal of mulba/ rubbish to the nearest municipal dumping ground. 14.4.1 For door/ window/ clerestory window | 5 | Each
76 | 14.5.1 | Renewing glass panes, with putty and nails wherever necessary including racking out the old putty: 14.5.1 Float glass panes of thickness 4 mm | 28.44 | sqm
77 | 14.43 | Removing white or colour wash by scrapping and sand papering and preparing the surface smooth including necessary repairs to scratches etc. complete | 136.8 | sqm
78 | 13.8 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete | 460.05 | Sqm
79 | 14.53.1 | Wall painting with plastic emulsion paint of approved brand and manufacture to give an even shade : 14.53.1 One or more coats on old work | 460.05 | Sqm
80 | 14.54.1 | Painting with synthetic enamel paint of approved brand and manufacture of required colour to give an even shade : 14.54.1 One or more coats on old work | 96 | Sqm
81 | 14.67.1 | Finishing walls with Premium Acrylic Smooth exterior paint with Silicone additives of required shade :- Old work (Two or more coats applied @ 1.43 ltr/ 10 sqm) over existing cement paint surface | 542.25 | Sqm
82 | 15.2.1 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge.:- Nominal concrete 1:3:6 or richer mix (i/c equivalent design mix) | 5.85 | cum
83 | 15.3.1 | Demolishing R.C.C. work manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per direction of Engineer - in- charge | 4.1175 | cum
84 | 15.5 | Extra for cutting reinforcement bars manually/ by mechanical means in R.C.C. or R.B. work (Payment shall be made on the cross sectional area of R.C.C. or R.B. work) as per direction of Engineer - in -charge. | 30 | Sqm
85 | 15.7.4 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge : in cement mortar | 13.6486 | cum
86 | 15.23.1 | Dismantling tile work in floors and roofs laid in cement mortar including stacking material within 50 metres lead.: For thickness of tiles 10 mm to 25 mm | 123.714 | sqm
87 | LMR | Dismantling mosaic / tile work in dado laid in cement mortar including12mm thick cement plaster stacking material within 50 metres lead.: For thickness of tiles 5 mm to 10 mm | 308.35 | sqm
88 | 15.48 | Taking out C.I. cover with frame from R.C.C. top slab of manholes of various sizes including demolishing of R.C.C. work manually/ by mechanical means and stacking of useful materials near the site and disposal of unserviceable materials within 50 metres lead as per direction of Engineer-in-charge | 2 | each
89 | 15.56 | Dismantling old plaster or skirting raking out joints and cleaning the surface for plaster including disposal of rubbish to the dumping ground within 50 metres lead. | 250.5 | Sqm
90 | 15.57 | Dismantling aluminium/ Gypsum partitions, doors, windows, fixed glazing and false ceiling including disposal of unserviceable surplus material and stacking of serviceable material with in 50 meters lead as directed by Engineer-in-charge | 117.1 | Sqm
91 | 15.12.1 | Dismantling doors, windows and clerestory windows (steel or wood) shutter including chowkhats, architrave, holdfasts etc. complete and stacking within 50 metres lead as directed by Engineer-in-charge : - Of area 3 sq. metres and below | 29 | cum
92 | 14.2.2 | Fixing steel windows in existing opening including embedding in floors or walls cutting masonry for hold fasts,embedding hold fasts in cement concrete blocks of size 15 x 10 x 10 cm with cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size), and making good the damages to walls and floors as required complete, including disposal of rubbish to the dumping ground within 50 meters lead | 14 | each
93 | 15.6 | Disposal of building rubbish / malba / similar unserviceable, dismantled or waste materials by mechanical means, including loading, transporting, unloading to approved municipal dumping ground or as approved by Engineer-in-charge, beyond 50 m initial lead, for all leads including all lifts involved | 33.6695 | cum
94 | 19.21.1 | 19.21 Making connection of drain or sewer line with existing manhole including breaking into and making good the walls, floors with cement concrete 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) cement plastered on both sides with cement mortar 1:3 (1 cement : 3 coarse sand), finished with a floating coat of neat cement and making necessary channels for the drain etc. complete : 19.21.1 For pipes 100 to 250 mm diameter | 5 | each
95 | 19.26.1 | Raising manhole cover and frame slab to required level including dismantling existing slab and making good the damage as required (Raising depth of manhole to be paid eparately) : Rectangular manhole 90x80 cm with rectangular cover 600x450 mm of grade LD - 2.5 | 4 | each
96 | 19.8.1.1 | Extra for depth for manholes : 19.8.1 Size 90x80 cm:- With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 2 | Rm
97 | 19.15.2 | Providing M.S. foot rests including fixing in manholes with 20x20x10 cm cement concrete blocks 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) as per standard design : With 20 mm diameter round bar | 10 | each
TOTAL (PART A - CIVIL WORKS)

## SUMMARY -MCH-KTM Geriatric (hidden)
SUMMARY
Name of work: CONVERSION OF WARD # 27 TO GERIATRIC HIGH DEPENDENCY UNIT AT MEDICAL COLLEGE KOTTAYAM DISTRICT.
Item No | Description of Item | SR | LMR | Amount | Remarks
1 | #REF! |  |  | 0 |  | 11955.7798
2 | SUB HEAD : II PLAIN CEMENT CONCRETE |  |  | 0 |  | 20554.779
3 | SUB HEAD III : REINFORCED CEMENT CONCRETE |  |  | 0 |  | 77737.6035
4 | SUB HEAD IV : BRICK WORK |  |  | 0 |  | 84712.1054
5 | SUB HEAD :V MARBLE WORK |  |  | 0 |  | 11612.812
6 | SUB HEAD VI : STONE WORK |  |  | 0 |  | 59098.4618
7 | SUB HEAD VII : STEEL WORK |  |  | 0 |  | 746094.7283
8 | SUB HEAD VIII : FLOORING |  |  | 0 |  | 408545.2
9 | SUB HEAD IX : ROOFING |  |  | 0 |  | 48633.5289
10 | SUB HEAD X : FINISHING |  |  | 0 |  | 44602.74
11 | SUB HEAD XI : PVC WORKS MISCELLANEOUS |  |  | 0 |  | 147399.05
12 | SUB HEAD XII : SERVICES |  |  | 0 |  | 326757.508
13 | SUB HEAD XIII : ALUMINIUM WORK |  |  | 0 |  | 5437.3784
14 | SUB HEAD : XIV: WATER PROOFING |  |  | 0 |  | 5437.3784
15 | SUB HEAD XV : REPAIR AND MAINTENANCE |  |  | 0 |  | 5437.3784
16 | PART II A Internal Electrification |  |  | 1134314.5 |  | 1040158.35
17 | PART II B SITC of Air Conditioning Works |  |  | 1387397.2022 |  | 1450692
18 | PART II C SITC of Medical Gas Pipe Line System Works |  |  | 1302500 |  | 1450692
| Total |  |  | 3824211.7022
a | TOTAL CIVIL | #REF! | 0 |  |  | 2494250.35
b | TOTAL ELECTRICAL | 348472.5 | 785842 |  |  | 2521711.7022
c | TOTAL HVAC |  | 1387397.2022 |  |  | -27461.3522
d | TOTAL Medical Gas Pipe Line System |  | 1302500 |  |  | 2549173.0545
e | TOTAL (a+b+c+d) | #REF! | 3475739.2022
| Adding Cost Index=39.60% for S.R items ie (Rs) |  |  |  | #REF!
A | Total adding Cost Index +SR |  |  |  | #REF!
B | Add LMR items |  |  |  | 3475739.2022
| Total (A+B) |  |  |  | #REF! | 2996500
| Add 4.5% Contingencies |  |  |  | #REF! | 3221500
D | Total after adding Contingencies |  |  |  | #REF! | 3196500
| Add 7.0% Consultancy Charges |  |  |  | #REF!
| Add 12.36% on Consultancy as service Charges |  |  |  | #REF! | #REF!
| TOTAL |  |  |  | #REF! | 15687261.0844
Say (Rupees Ninety Seven Lakhs Thirty Two Thousand Five Hundred and Ninety Three Only)

## LMR (hidden)
19 | LMR | Providing and fixing Ist quality ceramic glazed joint free wall tiles minimum thickness 8MM of approved make JOHNSON, NITCO, ORIENT, , KAJARIA or approved make, in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete. Size 450x300mm
| Code | Description | Unit | Quantity | Rate | Amount
Details of cost for 1 sqm
| Materials- | [7 empty] | Code | Discription | Unit | Quantity | Rate | Amount
Ceramic Glazed tiles = 1.00 sqm
| Add for wastage & breakage @ 2.5 % = 0.025 sqm = 1.025 sqm | [7 empty] | Details of cost for 1 cum
| 7800 | Tiles | Sqm. | 1.025 | 585 | 599.625 |  |  | MATERIALS
| 9999 | Carriage of tiles | L.S. | 1 | 35 | 35 |  |  | (0.357 cum. of cement = 0.51 tonne)
| 12 mm thick cement mortar 1:3 (1 cement: 3 |  | cum | 0.014 | 6621.6489 | 92.7031 |  |  | 367 | Cement | tonne | 0.51 | 7200 | 3672
| coarse sand (Rate as per item No. 3.8) |  |  |  |  | 0 |  |  | 2209 | Carriage of Cement | tonne | 0.51 | 150 | 76.5
| 9999 | Mortar for pointing in white cement | L.S. | 1 | 47.4 | 47.4 |  |  | 982 | Coarse sand | cum | 1.07 | 2048.27 | 2191.6489
| 367 | Cement for slurry over bed @ 3.3 kg per sqm | tonne | 0.0033 | 7200 | 23.76 |  |  | 2203 | Carriage of Coarse sand | cum | 1.07 | 150 | 160.5
| Labour: |  |  |  |  | 0 |  |  | LABOUR |  |  |  |  | 0
| 123 | Mason 1 st class | Day | 0.25 | 750 | 187.5 |  |  | For measuring, carrying, depositing and |  |  |  |  | 0
| 115 | Coolie | Day | 0.25 | 550 | 137.5 |  |  | mixing- |  |  |  |  | 0
| 9999 | Sundries including carriage of cement etc | L.S. | 1 | 50 | 50 |  |  | 114 | Beldar | Day | 0.75 | 550 | 412.5
| TOTAL |  |  |  |  | 1173.4881 |  |  | 101 | Bhisti | Day | 0.07 | 550 | 38.5
| Add for water charges @ 1 % |  |  |  |  | 11.7349 |  |  | 9999 | Hire and running charges of mechanical mixer | L.S. | 1 | 50 | 50
| TOTAL |  |  |  |  | 1185.223 |  |  | 9999 | Sundries | L.S. | 1 | 20 | 20
| Add for contractor’s profit and overheads @ 15% |  |  |  |  | 177.7834 |  | 7200 | Cost of 1.00 cum |  |  |  |  | 6621.6489
| Cost for 1 sqm |  |  |  |  | 1363.0064 |  |  | Say
| Say |  |  |  | Rs | 1363.01 | [5 empty] | 2048.27
46 | LMR | Providing & fixing bend of required degree with acess door,insertion rubber washer 3 mm thick bolts,nuts complete |  |  |  | 0
c |  | 110mm dia door elbow | Quantity | unit | Rate | Amount
Observed data and LMR
Details for 5nos
Materials
|  | 110mm pvc door elbow(LMR) | 5 | Each | 216 | 1080
Labour
|  | Fitter(LMR) | 0.25 | Each | 750 | 187.5
|  | Assistant fitter(LMR) | 0.25 | Each | 550 | 137.5
|  | Conveyance |  | LS |  | 20
|  | Cost of solvent cement |  | LS |  | 6
1431
|  | Add 15%CP |  |  |  | 214.65
|  | Total |  |  |  | 1645.65
329.13
For one No Rs 329.10/-
d |  | 75mm dia door elbow
Observed data
Details for 10nos
|  | Materials | Quantity | unit | Rate | Amount
|  | 75mm door elbow(LMR) | 5 | Each | 130 | 650
Labour
|  | Fitter(LMR) | 0.25 | Each | 750 | 187.5
|  | Assistant fitter(LMR) | 0.25 | Each | 550 | 137.5
|  | Conveyance |  | LS |  | 20
|  | Cost of solvent cement |  | LS |  | 5
1000
|  | Add 15% CP |  |  |  | 150
|  | Total |  |  |  | 1150
|  | For one No Rs 230.00/- |  |  |  | 230
49 | LMR | Providing and fixing PVC pipe including cutting chasng in walls and making good the walls etc complete. (Concealed) 10 kg/m
a | LMR | a 20 mm pipe
a | 18.7.2 | 20 mm nominal outer dia .Pipes.
| Code | Description | Unit | Quantity | Rate | Amount
Details of cost for 10 metre
MATERIALS
| 8637 | (A) 20 mm outer dia PVC pipe , | metre | 10 | 26 | 260
| Add 30% for fitting and wastage etc on (A) |  | metre | 3 | 26 | 78
| 9999 | Cement, sand and grit etc. | L.S. | 1 | 22 | 22
| LABOUR |  |  |  |  | 0
| 116 | Fitter | Day | 0.33 | 750 | 247.5
| 116 | Assit. Fitter | Day | 0.33 | 650 | 214.5
| 117 | Beldar | Day | 0.66 | 550 | 363
Making chases upto 7.5x7.5 cm in wails including making good and finishing with matching surface after fixing pipe etc
|  | Mason | Day | 0.4 | 750 | 300
|  | Beldar | Day | 1 | 550 | 550
| TOTAL |  |  |  |  | 2035
| Add 1% for water charges |  |  |  |  | 20.35
| TOTAL |  |  |  |  | 2055.35
| Add 15% for contractor’s profit and overheads |  |  |  |  | 308.3025
| Cost for 10 metre |  |  |  |  | 2363.6525
| Cost for 1 metre |  |  |  |  | 236.3653
| Say |  |  |  |  | 236.4
b | LMR | b 25 mm pipe
b | 18.7.2 | 25 mm nominal outer dia .Pipes.
| Code | Description | Unit | Quantity | Rate | Amount
Details of cost for 10 metre
MATERIALS
| 8637 | (A) 25 mm outer dia PVC pipe , | metre | 10 | 44 | 440
| Add 30% for fitting and wastage etc on (A) |  | metre | 3 | 44 | 132
| 9999 | Cement, sand and grit etc. | L.S. | 1 | 65 | 65
| LABOUR |  |  |  |  | 0
| 116 | Fitter | Day | 0.33 | 750 | 247.5
| 116 | Assit. Fitter | Day | 0.33 | 650 | 214.5
| 117 | Beldar | Day | 0.66 | 550 | 363
Making chases upto 7.5x7.5 cm in wails including making good and finishing with matching surface after fixing pipe etc
|  | Mason | Day | 0.4 | 750 | 300
|  | Beldar | Day | 1 | 550 | 550
| TOTAL |  |  |  |  | 2312
| Add 1% for water charges |  |  |  |  | 23.12
| TOTAL |  |  |  |  | 2335.12
| Add 15% for contractor’s profit and overheads |  |  |  |  | 350.268
| Cost for 10 metre |  |  |  |  | 2685.388
| Cost for 1 metre |  |  |  |  | 268.5388
| Say |  |  |  |  | 268.5
c | LMR | c 32mmpipe
c | 18.7.2 | 32 mm nominal outer dia .Pipes.
| Code | Description | Unit | Quantity | Rate | Amount
Details of cost for 10 metre
MATERIALS
| 8637 | (A) 25 mm outer dia PVC pipe , | metre | 10 | 73 | 730
| Add 30% for fitting and wastage etc on (A) |  | metre | 3 | 73 | 219
| 9999 | Cement, sand and grit etc. | L.S. | 1 | 74 | 74
| LABOUR |  |  |  |  | 0
| 116 | Fitter | Day | 0.33 | 750 | 247.5
| 116 | Assit. Fitter | Day | 0.33 | 650 | 214.5
| 117 | Beldar | Day | 0.66 | 550 | 363
Making chases upto 7.5x7.5 cm in wails including making good and finishing with matching surface after fixing pipe etc
|  | Mason | Day | 0.4 | 750 | 300
|  | Beldar | Day | 1 | 550 | 550
| TOTAL |  |  |  |  | 2698
| Add 1% for water charges |  |  |  |  | 26.98
| TOTAL |  |  |  |  | 2724.98
| Add 15% for contractor’s profit and overheads |  |  |  |  | 408.747
| Cost for 10 metre |  |  |  |  | 3133.727
| Cost for 1 metre |  |  |  |  | 313.3727
| Say |  |  |  |  | 313.4
50 | LMR | Providing and fixing PVC pipe including cutting chasng in walls and making good the walls etc complete. (External) 10 kg/m
a | LMR | a 20 mm pipe
a | 18.7.2 | 20 mm nominal outer dia .Pipes.
| Code | Description | Unit | Quantity | Rate | Amount
Details of cost for 10 metre
MATERIALS
| 8637 | (A) 20 mm outer dia PVC pipe , | metre | 10 | 26 | 260
| Add 30% for fitting and wastage etc on (A) |  | metre | 3 | 26 | 78
| 9999 | Cement, sand and grit etc. | L.S. | 1 | 53 | 53
| LABOUR |  |  |  |  | 0
| 116 | Fitter | Day | 0.33 | 750 | 247.5
| 116 | Assit. Fitter | Day | 0.33 | 650 | 214.5
| 117 | Beldar | Day | 0.66 | 550 | 363
Making chases upto 7.5x7.5 cm in wails including making good and finishing with matching surface after fixing pipe etc
|  | Mason | Day | 0.4 | 750 | 300
|  | Beldar | Day | 1 | 550 | 550
| TOTAL |  |  |  |  | 2066
| Add 1% for water charges |  |  |  |  | 20.66
| TOTAL |  |  |  |  | 2086.66
| Add 15% for contractor’s profit and overheads |  |  |  |  | 312.999
| Cost for 10 metre |  |  |  |  | 2399.659
| Cost for 1 metre |  |  |  |  | 239.9659
| Say |  |  |  |  | 240
b | LMR | b 25 mm pipe
b | 18.7.2 | 25 mm nominal outer dia .Pipes.
| Code | Description | Unit | Quantity | Rate | Amount
Details of cost for 10 metre
MATERIALS
| 8637 | (A) 25 mm outer dia PVC pipe , | metre | 10 | 44 | 440
| Add 30% for fitting and wastage etc on (A) |  | metre | 3 | 44 | 132
| 9999 | Cement, sand and grit etc. | L.S. | 1 | 78 | 78
| LABOUR |  |  |  |  | 0
| 116 | Fitter | Day | 0.33 | 750 | 247.5
| 116 | Assit. Fitter | Day | 0.33 | 650 | 214.5
| 117 | Beldar | Day | 0.66 | 550 | 363
Making chases upto 7.5x7.5 cm in wails including making good and finishing with matching surface after fixing pipe etc
|  | Mason | Day | 0.4 | 750 | 300
|  | Beldar | Day | 1 | 550 | 550
| TOTAL |  |  |  |  | 2325
| Add 1% for water charges |  |  |  |  | 23.25
| TOTAL |  |  |  |  | 2348.25
| Add 15% for contractor’s profit and overheads |  |  |  |  | 352.2375
| Cost for 10 metre |  |  |  |  | 2700.4875
| Cost for 1 metre |  |  |  |  | 270.0487
| Say |  |  |  |  | 270
c | LMR | c 32mmpipe
c | 18.7.2 | 32 mm nominal outer dia .Pipes.
| Code | Description | Unit | Quantity | Rate | Amount
Details of cost for 10 metre
MATERIALS
| 8637 | (A) 25 mm outer dia PVC pipe , | metre | 10 | 73 | 730
| Add 30% for fitting and wastage etc on (A) |  | metre | 3 | 73 | 219
| 9999 | Cement, sand and grit etc. | L.S. | 1 | 131 | 131
| LABOUR |  |  |  |  | 0
| 116 | Fitter | Day | 0.33 | 750 | 247.5
| 116 | Assit. Fitter | Day | 0.33 | 650 | 214.5
| 117 | Beldar | Day | 0.66 | 550 | 363
Making chases upto 7.5x7.5 cm in wails including making good and finishing with matching surface after fixing pipe etc
|  | Mason | Day | 0.4 | 750 | 300
|  | Beldar | Day | 1 | 550 | 550
| TOTAL |  |  |  |  | 2755
| Add 1% for water charges |  |  |  |  | 27.55
| TOTAL |  |  |  |  | 2782.55
| Add 15% for contractor’s profit and overheads |  |  |  |  | 417.3825
| Cost for 10 metre |  |  |  |  | 3199.9325
| Cost for 1 metre |  |  |  |  | 319.9932
| Say |  |  |  |  | 320
54 | 18.17 | Providing and fixing gun metal valve with C I wheel of approved quality (screwed end ):-
| LMR | 20mm dia nominal bore | each
a | LMR | 20mm dia. Nominal bore
| Code | Description | Unit | Quantity | Rate | Amount
Details of cost for one no.
Materials :-
|  | 20mm dia. Gun metal gate valve with wheel | each | 1 | 655 | 655
|  | Carriage of materials and fixing charges | L.S. | 1 | 77 | 77
| TOTAL |  |  |  |  | 732
| Add 1 % for water charges |  |  |  |  | 7.32
| TOTAL |  |  |  |  | 739.32
| Add 15% for contractor’s profit and overheads |  |  |  |  | 110.898
| Cost of one no. |  |  |  |  | 850.218
| Say |  |  |  |  | 850.2
69 | LMR | Providing and fixing non reflective polyster film of approved make and clour with self adhesive to glazed windows/doors (to make opaque)
| LMR | Observed data
| Code | Description | Unit | Quantity | Rate | Amount
Details of cost for 10.00 sqm
| non reflective polyster film |  | Sqm | 10 | 527.24 | 5272.4
| non reflective polyster film wastage 5% |  | Sqm | 0.5 | 527.24 | 263.62
| Labour: | cutting in required size & fixing | Day | 0.25 | 750 | 187.5
|  | Carriage of materials | L.S. | 1 | 50 | 50
|  | Sundries Blades & cottonwaste etc. | L.S. | 1 | 40 | 40
| TOTAL |  |  |  |  | 5813.52
| Add 1 % for water charges |  |  |  |  | 58.1352
| TOTAL |  |  |  |  | 5871.6552
| Add 15% for contractor’s profit and overheads |  |  |  |  | 880.7483
| Cost for 10 metre |  |  |  |  | 6752.4035
| Cost per metre |  |  |  |  | 675.2403
| Say |  | Sqm |  |  | 675.2
70 | LMR | Removing and refixing the existing aluminum door after rectification with new pivot/ hinge ,weather strip etc complete | Sqm
Observed data
| Code | Description |  | Unit | Quantity | Rate | Amount
Details of cost 5.0 sqm.
Labour:
|  | Aluminium fabricator |  | each | 2 | 750 | 1500
|  | Aluminium fabricator |  | each | 1.5 | 550 | 825
|  | T & P etc. |  | L.S. | 1 | 45 | 45
| TOTAL | [5 empty] | 2370
| Add 1 % for water charges | [5 empty] | 23.7
| TOTAL | [5 empty] | 2393.7
| Add 15% for contractor’s profit and overheads | [5 empty] | 359.055
| Cost for 5 sqm | [5 empty] | 2752.755
| Cost for 1 sqm | [5 empty] | 550.551
| Say | [5 empty] | 550.6 |  |  | 550.6
87 | LMR | Dismantling mosaic / tile work in dado laid in cement mortar including12mm thick cement plaster stacking material within 50 metres lead.: For thickness of tiles 5 mm to 10 mm | sqm | 308.35 | 80
| Code | Description | Unit | Quantity | Rate | Amount
Detail of cost for 10 sqm
LABOUR
|  | Mason 2nd class | Day | 0.5 | 750 | 375
|  | Coolie | Day | 0.5 | 550 | 275
|  | Sundries | L.S | 1 | 39 | 39
| TOTAL |  |  |  |  | 689
| Add 1 % for water charges |  |  |  |  | 6.89
| TOTAL |  |  |  |  | 695.89
| Add 15% for contractor’s profit and overheads |  |  |  |  | 104.3835
| Cost of 10.00 sqm |  |  |  |  | 800.2735
| Cost of 1.00 sqm |  |  |  |  | 80.0273
| Say |  |  |  |  | 80