## ICU MCH Ktym Electrical
Name of work : CONVERSION OF WARD # 27 IN TO GERIATRIC HIGH DEPENDENCY UNIT AT MEDICAL COLLEGE KOTTAYAM DISTRICT.
Part II A Internal Electrification
Sl. No. | Description of item | Unit | Qty | SR-2012 / LMR Rate in Rs | Amount in Rs
1 | Supply of 1x28W Tube light made of powder coated CRCA sheet channel with all accessories like electronic ballast, lamp holder, 28W lamp etc prewired complete. (Philips TMS 095xTL5-28W / Wipro WDF 9128 SG / ) | Each | 8 | 419 | 3352
2 | Supply of ceiling fan 1200 mm sweep, double ball bearing, approved colour and quality with original down rod,suspension shackle,canopy etc with out regulator complete with all accessories as required. | Each | 7 | 1694 | 11858
3 | Supply of exhaust fan 300 mm sweep, metal blades of approved colour and quality complete with all accessories as required. | Each | 6 | 1830 | 10980
4 | Supply and installation of 400 mm sweep, wall fan, swinging type with speed control, necessary adapter, of approved colour, for single phase 230 volt, 50Hz AC supply complete with motor, capacitor all accessories as required complete. | Each | 8 | 2008 | 16064
5 | Supply and fixing ISI marked Compact Fluroscent Lamp (CFL), 15 watts of approved quality. | Each | 10 | 161 | 1610
6 | Supply and fixing ISI marked Compact Fluroscent Lamp (CFL), 20 watts of approved quality. | Each | 4 | 207 | 828
7 | Supply & fixing Vertical down lights, white powder coated CRCA ring, bright finish aluminium reflector wire with commercial HF ballast for individual lamps, 18W CFL lamp etc with all required accessories as required. (Bajaj BJDR 118 WEB1 VI / Wipro GCP 15118 SGW) | Each | 10 | 864 | 8640
8 | Supply and fixing of 3x36W CFL, recess mounted, bottom opening type clean room luminaire with powder coated CRCA housing, stainless steel frame, glass cover, aluminium anodised reflector, 36W CFL lamp, with all mounting accessories as required. (Philips FBS651 3xPL-L 36W EB CR/CR FOP GT or Wipro WIP 43336 SGA / Bajaj BPRF 336C LHD). | Each | 12 | 7153 | 85836
9 | Supplying and fixing 1x10W CFL Bulk head luminaire, complete with die-cast aluminium body heat resistant prismatic glass cover, M.S galvanised wire guard, 10W CFL lamp etc complete with all mounting accessories as required. (Bajaj BJDB 10 CFL / Philips FXC 101) | Each | 6 | 705 | 4230
10 | Supplying and fixing PVC batten / angle holder including connection etc with all required accessories as required. | Each | 14 | 79 | 1106
11 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
a | 4 x 10 Sq mm | m | 70 | 120 | 8400
b | 4 x 16 Sq mm | m | 50 | 135 | 6750
c | 3.5 x 35 Sq mm | m | 40 | 185 | 7400
d | 3.5 x 70 Sq mm | m | 25 | 335 | 8375
e | 3.5 x 185 Sq mm | m | 30 | 740 | 22200
12 | Supply and fixing 32 A Metal clad TPN SFU with HRC Fuses ISI Certified mounted on suitable angle iron frame work, giving connection, testing and commissioning etc including all accessories complete as required. | Each | 4 | 3590 | 14360
13 | Supply and fixing 63 A Metal clad TPN SFU with HRC Fuses ISI Certified mounted on suitable angle iron frame work, giving connection, testing and commissioning etc including all accessories complete as required. | Each | 1 | 4230 | 4230
14 | Supply, Installation, Testing & Commissioning of LT panel, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP42, free standing, floor mounting, dust and vermin proof, powder coated, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system with busbars extendable on both sides, including internal wiring with suitable size wires, rotary handle, spreaders, 3mm thick gland plate, hinged type door with neoprene gasket etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification.
INCOMER
1 No. 200A, FP, 25kA, MCCB with Thermal Magnetic release, Ics=Icu, having adjustable over load & short circuit protection.
BUSBARS
1 Set of 250A TPN busbars of high conductivity electrolytic quality Aluminium alloy.
1 Set of 25 x 3 mm copper busbars of high conductivity electrolytic quality shall be provided throught out the panel for its earthing.
INSTRUMENTS
1 No 3 phase Digital Multi function meter to read V, A, F, Acc class 1.
1 Set of phase indicating lamps, LED type, RYB.
1 Set of 2A 10kA C curve SP control MCB
1 Set of 160/5A, Class 1.0, 10VA, Cast Resin CT
OUTGOING
1 no 100A, TPN, AC23A, 415V, 50Hz switch disconnector fuse unit with suitable size Din type HRC fuse as per load.
3 no. 63A, TPN, AC23A, 415V, 50Hz switch disconnector fuse unit with suitable size Din type HRC fuse as per load.
4 nos. 32A, TPN, AC23A, 415V, 50Hz switch disconnector fuse unit with suitable size Din type HRC fuse as per load..
| Space provision for 2 nos. 63A, TPN, AC23A, 415V, 50Hz switch disconnector fuse unit. | Each | 1 | 58087 | 58087
15 | Preparation of all required drawings and getting approval from Electrical inspectorate, Kerala State Electricity Board and local bodies, including liaison works complete as required ( Statutory fees will be reimbursed by the client on production of actual bill) | Job | 1 | 50000 | 50000
16 | Supply & fixing modular type computer outlet (RJ-45) with modular base and cover plate, GI box complete with all accessories, connection etc. complete as required. | Each | 16 | 528 | 8448
17 | Supply and laying CAT 6 cable in the exisitng surface / recessed steel / PVC conduit as required. | m | 240 | 30 | 7200
18 | Supply, installation, testing & commissioning of 10 kVA, 3 phase, input, 3 phase output, true on-line UPS system with 30 minutes back up (full load), including all accessories, SMF batteries VRLA type with powder coated MS cabinet including all accessories as required complete having following specification.
Fully digital controlled based on DSP
Power factor corrected from end > 0.9
Pure sine wave output.
Full time output voltage & frequency regulation
Auto regulation of battery end voltage
Intelligent interface with LED/LCD display
Static bypass switch & manual by pass switch
| Auto temperature compensation | Set | 1 | 325000 | 325000
19 | Supplying and fixing U-PVC Trunking Type Cable Management System for Power, Data, -(Double Compartment) Cables/wires complete with Cover Plates, End Caps, Internal & External angles, Cable Retainers, cable Dividers,Tees, accessories etc as required. The same shall be suitable for fixing 6A, 16A Sockets, switchs, RJ45, with its modular box & front plate etc. The CMS shall conform to BS:4678/ BS:4662 & corresponding BIS.
| Size 100 x 50 mm | Mtr | 45 | 1560 | 70200
20 | Supply & installation of following modular type switches & sockets in the exisitng DLP trunking with all required accessories like modular box, front plate etc as required.
a | 6A socket with switch | Each | 36 | 650 | 23400
b | 6/16A socket with switch | Each | 24 | 812 | 19488
c | RJ45 data outlet | Each | 12 | 650 | 7800
| Total LMR |  |  |  | 785842
21 | Point wiring in PVC conduit, with Modular type switch: Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FR PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FR PVC insulated copper conductor single core cable etc as required.
a | Group B | Point | 20 | 544 | 10880
b | Group C | Point | 40 | 664 | 26560
22 | Twin control point wiring in PVC conduit, with modular type switch: Wiring for twin control light point with 1.5 sq.mm FR PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FR PVC insulated copper conductor single core cable etc as required. | Point | 2 | 710 | 1420
23 | Power plug wiring in PVC conduit ( 2x4 sq mm ): Wiring for light/ power plug with 2X4 sq. mm FR PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 1 No 4 sq. mm FR PVC insulated copper conductor single core cable for loop earthing as required. | m | 250 | 162 | 40500
24 | Power plug wiring in PVC conduit ( 4x4 sq mm ): Wiring for light/ power plug with 4X4 sq. mm FR PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 2 Nos 4 sq. mm FR PVC insulated copper conductor single core cable for loop earthing as required. | m | 25 | 268 | 6700
25 | Circuit Sub main wiring in PVC Conduit: Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FR PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required
a | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | m | 450 | 107 | 48150
b | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | m | 100 | 131 | 13100
c | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | m | 150 | 162 | 24300
e | 4 X 4 sq. mm + 2 X 4 sq. mm earth wire | m | 25 | 268 | 6700
f | 4 X 6 sq. mm + 2 X 6 sq. mm earth wire | m | 50 | 358 | 17900
26 | Telephone wiring in existing conduit: Supplying and drawing following pair 0.5 sq mm FR PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required.
| 2 Pair | m | 120 | 15.5 | 1860
27 | T. V cable in existing conduit: Supplying and drawing co-axial TV cable RG-6 grade, 0.7 mm solid copper conductor PE insulated, shielded with fine tinned copper braid and protected with PVC sheath in the existing surface/ recessed steel/ PVC conduit as required. | m | 60 | 22 | 1320
28 | S/F PVC conduit: Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
a | 20 mm | m | 450 | 56.5 | 25425
b | 25 mm | m | 50 | 64.5 | 3225
29 | S/F Metal boxes: Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
a | 250 mm X 300 mm X 60 mm deep | Each | 2 | 286 | 572
b | 250 mm X 300 mm X 100 mm deep | Each | 1 | 310 | 310
30 | S/F Modular type switch/ socket: Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
a | Telephone socket outlet | Each | 6 | 89 | 534
b | TV antenna socket outlet | Each | 3 | 93 | 279
c | Bell push | Each | 2 | 98.5 | 197
31 | Supplying and fixing electronic fan regulator: Supplying and fixing stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | Each | 8 | 322 | 2576
32 | S/F Modular type blanking plates: Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | Each | 30 | 22 | 660
33 | S/F Modular boxes, base & cover plate: Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.
a | 1 or 2 Module (75mmX75mm) | Each | 27 | 142 | 3834
b | 12 Module (200mmX150mm) | Each | 2 | 344 | 688
34 | S/F light plug point modular type accessaries: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). | Each | 56 | 288 | 16128
35 | S/F Power plug point with modular type switch: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | Each | 16 | 366 | 5856
36 | S/F Ceiling rose: Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. | Each | 40 | 34 | 1360
37 | S/F call bell/buzzer: Supplying and fixing call bell/ buzzer suitable for single phase, 230 volts, complete as required. | Each | 2 | 54.5 | 109
38 | ITC Fluroscent fitting directly on surface: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | Each | 8 | 69.5 | 556
39 | ITC Fluroscent fitting with down rod: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc., including supplying and fixing ball and socket arrangement, 2 no. down rods of 20 mm dia X 1.6 mm thick steel conduit upto 30 cm length, painting and wiring the down rods and connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | Each | 12 | 195 | 2340
40 | S/F extra down rod: Providing and fixing extra conduit down rod of 20 mm dia, 2 X 10 cm length wiring with 2 X 1.5 sq. mm FR PVC insulated, copper conductor, single core cable including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | Each | 24 | 28.5 | 684
41 | ITC Ceiling fan: Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable etc. as required. | Each | 7 | 73.5 | 514.5
42 | Extra down rod 15 mm dia 10 CM Length: Supplying and fixing extra down rod of 10 cm length G.I. pipe ,15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | Each | 7 | 19.5 | 136.5
43 | Extra down rod 15 mm dia 20 CM Length: Supplying and fixing extra conduit down rod of 20 cm length G.I. pipe 15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | Each | 7 | 23 | 161
44 | ITC Exhaust fan: Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required.
| Upto 450 mm sweep | Each | 6 | 163 | 978
45 | S/F TP& N FSU in cubicle panel board: Providing and fixing following capacity TP&N disconnector fuse switch unit inside the existing panel board with ISI marked HRC fuses including drilling holes in cubicle panel, making connections, etc. as required.
a | 100 Amp, 16 KA | Each | 1 | 2801 | 2801
b | 200 Amp, 25 KA | Each | 1 | 7290 | 7290
46 | S/F TP MCB DB: Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
a | 4 way (4 + 12), Double door | Each | 3 | 1654 | 4962
b | 6 way (4 + 18), Double door | Each | 1 | 2047 | 2047
47 | S/F Vertical Type TP MCB DB with provision for MCCB as Incomer: Supplying and fixing following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, with provision of 100 amps TP 16 KA MCCB as incomer, interconnection between incomer MCCB and bus bars (but without MCB's/ MCCB) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.)
| 8 Way TP | Each | 1 | 6081 | 6081
48 | S/F 'C' series, MCB: Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | Single pole | Each | 26 | 141 | 3666
b | Triple pole | Each | 5 | 562 | 2810
49 | S/F S P MCB blanking plate: Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | Each | 20 | 5.5 | 110
50 | S/F TPN RCCB: Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 25 amps | Each | 1 | 1679 | 1679
b | 40 amps | Each | 2 | 1703 | 3406
c | 63 amps | Each | 2 | 1965 | 3930
51 | S/F 20A SPN MCB industrial socket outlet: Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | Each | 4 | 693 | 2772
52 | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | Each | 2 | 121 | 242
53 | G.I.Earth plate Electrode with Salt & Charcoal: Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | Set | 2 | 3996 | 7992
54 | Supplying and laying 6 SWG G.I. wire in ground: Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including connection/ termination with GI thimble etc. as required. | m | 150 | 23 | 3450
55 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess: Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | m | 20 | 120 | 2400
56 | Providing and fixing 4.00 mm dia copper wire on surface or in recess: Providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing as required. | m | 50 | 87.5 | 4375
57 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation and refilling the trench etc as required, but excluding sand cushioning and protective covering.
a | Upto 35 sq. mm | m | 60 | 65.5 | 3930
b | Above 35 sq. mm and upto 95 sq. mm | m | 25 | 71.5 | 1787.5
c | Above 95 sq. mm and upto 185 sq. mm | m | 30 | 77 | 2310
58 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
a | Upto 35 sq. mm (clamped with 1mm thick saddle) | m | 120 | 19.5 | 2340
b | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | m | 25 | 60 | 1500
c | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | m | 25 | 69 | 1725
59 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required.
a | 4 x 10 Sq mm | Each | 12 | 120 | 1440
b | 4 X 16 sq. mm | Each | 8 | 188 | 1504
c | 3.5 x 35 Sq mm | Each | 6 | 185 | 1110
d | 3.5 x 70 Sq mm | Each | 4 | 335 | 1340
e | 3.5 x 185 Sq mm | Each | 4 | 740 | 2960
| Total SR |  |  |  | 348472.5
Abstract
Electrical,HVAC & Medical Gas Pipe Line Works
Part II A Internal Electrification-
| Estimate Amount at LMR |  |  |  | 785842
| Estimate Amount at SR 2012 |  |  |  | 348472.5
| Total Part II A |  |  |  | 1134314.5
| Assistant Project Engineer (Elec) |  | Deputy Manager (Mech)
| HLL Lifecare LTD (ID) TVM |  | HLL Lifecare LTD (ID) TVM
Deputy Manager (Mech)
HLL Lifecare LTD (ID) TVM
Deputy Manager (Bio Medical)
HLL Lifecare LTD (ID) TVM
Note on E5: Abraham Jacob:

## PART C HVAC
CONVERSION OF WARD # 27 IN TO GERIATRIC HIGH DEPENDENCY UNIT AT MEDICAL COLLEGE KOTTAYAM DISTRICT.
PART C - SITC of HVAC SYSTEM
Sl. No. | Description of item | Qty | Unit | Rate in figures & words (Rs) | Amount in Rs
Section A - MACHINERY
1 | Supply, intallation, testing and commissioning (SITC) of 8.5 TR capacity aircooled Outdoor condensing unit with scroll compressor as per specifications complete with suitable capacity drive motor, air cooled condenser with all accessories, hermetically sealed scroll compressor, electronic microprocessor pendant controller with digital display, first charge R 22 refrigerant gas, vibration isolator pads and saftey devices like thermal protector, pressure relief valve, over load relays single phase preventor, high-low pressure cut out, suitable for three phase 440V supply. | 2 | Each
2 | Supply, installation, testing and commissioning of suitable hard drawn copper refrigerant piping for 8.5TR machine with 13 mm nitrile rubber insulation interconnecting the condensing unit to evaporating unit for packaged units as per site condition. | 44 | Rm
3 | Supply, intallation, testing and commissioning (SITC) of 5.5 TR capacity aircooled Ductable split air conditioner with scroll compressor, Ceiling Suspended Indoor Units (IDU) and all standard fittings, IDU SS drain pan, as per specifications complete with suitable capacity drive motor, air cooled condenser with all accessories, hermetically sealed scroll compressor, electronic microprocessor pendant controller with digital display, first charge R 22 refrigerant gas, vibration isolator pads and saftey devices like thermal protector, pressure relief valve, over load relays single phase preventor, high-low pressure cut out, suitable for three phase 440V supply. | 2 | Each
4 | Supply, installation, testing and commissioning of suitable hard drawn copper refrigerant piping for 5.5TR machine with 13 mm nitrile rubber insulation interconnecting the condensing unit to evaporating unit for packaged units as per site condition | 66 | Rm
5 | SITC of DX type double skinned air handling units, ceiling suspended type 17 TR, 2500 lps capcity complete with suitable DIDW blower (asper approved make), blower section, static pressure of 125mm of water column, built in pre filter(EU4), fine filter(EU7) and HEPA filter(EU13) and controls connected to condensing units, insulated SS drain pan, 6 row cooling coil, electric motor, belt drive package with TEFC motor class 'B' insulation, suitable for 3 phase, 415 V, 50Hz supply, suitable AHU panel, ARI certified, belt guards, thermometers and pressure gauges at the inlet & outlet, suitable supports for suspending from slab, vibration isolator, etc. conforming to specifications. The air handling units shall have 2 inlet refrigerant coils and 2 outlet refrigerant coils suitable for 2 numbers of 8.5 TR capacity ODU and shall conform to specifications. | 1 | Each
6 | Supply, Laying and Fixing of 4C 4Sq.mm size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Aluminium conductor cable conforming to IS 7098 (Part 1) amended upto date with brass compression glands on surface/ cable tray/ wall / build in trench etc as required from the Indoor to outdoor units of all units for control wiring. | 26.4 | Rm
7 | Supply, installation, testing and commissioning PVC drain pipe of 25mm dia ISI marked, connecting the drain lines from the indoor units to floor sump, with 9mm nitrile rubber insulation as per specification | 26.4 | Rm
8 | Supply, installation, testing and commissioning of Air Cooled High Wall mounted Split Air Conditioner of following capacity consisting of high wall mounted type room unit (fan coil) with cordless remote control and one number outdoor condensing unit comprising of enegy efficient suitable rotary compressor for operation on single phase, 230 V, 50Hz supply, fixing the outdoor unit on a raised platform as per manufacturers recommendation and fixing of room (fan coil) unit on wall, upto 10 m distance refrigerant copper piping with 13mm nitrile rubber insulation, providing and making interconnection between room & condenser as per site conditions, comprising of 1" dia drain PVC pipe with insulation 10m, canvas connections, full electrical cabling from power plug near indoor unit and to outdoor unit, vibration isolators, first charge refrigarant gas, min 4star rated as per BEE suitable stabilizer etc complete as required.
8.1 | 1.5 TR | 1 | Each
9 | Supply and fixing Heater package with Humidistat and contactor for humidity control | 1 | Each
Section B - AIR DISTRIBUTION
10 | Supply, installation, testing and commissioning of factory fabricated rectangular GSS sheet metal ducting for Supply/return/fresh air duct/collar connecting to indoor unit as per ducting specifications and with suitable supports using MS angles, channels, rods, anchor bolts, etc to roof /truss as per IS 655 and as per specifications.
10.1 | 20 G | 3 | SQM
10.2 | 22 G | 16 | SQM
10.3 | 24 G | 69 | SQM
11 | SITC of External thermal insulation on supply air ducts using min 12mm thick nitrile rubber class "O" closed cell type with antimicrobial protection as per specifications | 69 | SQM
12 | Supply, installation, testing and commissioning of Acoustic duct lining using 10mm nitrile rubber insulation open cell type inside the ducts, at the outlets of all indoor units upto 4m distance from fan outlet as per spec provided. | 16 | SQM
13 | Supply, fabrication, installation, testing of flexible connections made out of fire resistant flexible double canvas sleeve. | 3 | Set
14 | Supply, installation, testing and comissioning of Powder coated extruded aluminimum Continuous grilles 16mm frame, 15deg deflection for supply / return air 150mm wide as per spec | 4 | SQM
15 | SITC of Powder coated extruded aluminimum supply air diffusers 4 way both side coated with collar damper aluminuim extruded black anodized . (300mmX300mm/600mmx600mm) | 1 | SQM
16 | SITC of Powder coated extruded aluminium return air diffusers 4 way both side coated without VCD. (300mmX300mm/600mmx600mm) | 1 | SQM
17 | SITC of Fire Control Damper made of 16G GSS sheet blade and frame with 165mm casing, heavy duty interlocking blades and fuly enclosed bade linkage mechanism, SS lateral seal blade seals, self lubricating sintered bronze bushes, fire rating as per UL555-1995 tested as per BS-476 part 20 with 18G extended sleeve 450mm and with fusible link, spring mechanism control panel temp sensor, smoke sensor, limit swith with lever for auto shut off in case of fire/smoke as per specifications. | 1 | SQM
18 | SITC of multi blade type volume control dampers made of extruded auminium for ducts/ collars to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distributions system in main ducts & other area as per specification. | 1.44 | SQM
19 | SITC of Fresh air GI louvers of size 300x300 mm with wire mesh and birds screen for IDUs/AHUs as per specifications. | 1 | SQM
20 | Supply, installation, testing and comissioning of Inline Centrifugal duct fan with dynamically balanced impeller of 700cfm capacity, min 10 mm static , complete with GI box, with single phase direct driven motor with class B, IP44 protection with an internal automatic safety thermal overload protection, dynamically balanced impeller of following capacity, with an operating sound level of less than 55dB at 3 m distance. | 4 | Each
TOTAL (PART C-HVAC)
Note on E3: Abraham Jacob: