## Ele edit
CONSTRUCTION OF SURGICAL WARD ABOVE THE TRAUMA CARE UNIT/ OT BLOCK AT THQH KOTTARAKKARA
PART B _ ELECTRICAL WORKS
Sl. No. |  | Description of item | Unit | Qty | Rate Rs(in figures&words) | Amount
1 | 1.1 | Wiring for light point/exhaust fan point/ wall fan point /call bell point with 1.5 sq:mm FRLS PVC insulated copper conductor single core cable cable in surface/ recessed PVC conduit, with modular switch, modular plate, suitable size G.I. box and earthing the point with 1.5 sq:mm FRLS PVC insulated copper conductor single core cable etc as required.
a) | 1.10.3 | Group C | Point | 280
2 | 1.11 | Wiring for twin control light point with 1.5 sq:mm FRLS PVC insulated copper conductor single core cable in surface/recessed medium class PVC conduit, 2 way modular type switch, modular plate, suitable GI box and earthing the point with 1.5 sq mm. FRLS PVC insulated copper conductor single core cable etc as required. | Point | 5
3 | 1.12 | Wiring for light/ power plug with 2x4 sq.mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium PVC coduit along with 1 No 4 sq mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | Rm | 200
4 | 1.14 | Wiring for circuit sub main wiring alongwith earthwire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed PVC conduit as required.
a) | 1.14.1 | 2x1.5 sq mm +1x1.5 sq. mm earth wire | Rm | 1600
b) | 1.14.2 | 2x2.5 sq mm +1x 2. 5 sq.mm earth wire | Rm | 800
c) | 1.14.9 | 4x6 sq mm + 2x6 sq mm earth wire. | Rm | 300
d) | 1.14.10 | 4x10 sq mm + 2x10 sq mm earth wire. | Rm | 100
5 | 1.15 | Rewiring for light point/fan point/exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable and 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable as earth wire in existing surface/ recessed PVC conduit including dismantling as required.
a) | 1.15.3 | Group C | Point | 30
6 | 1.17 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel / PVC conduit as required.
a) | 1.17.1 | 1 x 1.5 sq. mm | Rm | 3500
b) | 1.17.11 | 2 x 2.5 sq. mm | Rm | 900
c) | 1.17.20 | 2 x 4 sq. mm | Rm | 200
7 | 1.18 | Supplying and drawing following pair, 0.5 sq mm FRLS PVC insulated copper conductor, un armoured telephone cable in the existing surface/recessed steel/ PVC conduit.
a) | 1.18.2 | 2 Pair | Rm | 525
8 | 1.19 | Supplying and drawing co - axial TV cable RG-6 grade, 0.7 mm solid copper conductor PE insulated, shielded with fine tinned copper braid and protected with PVC sheath in the existing surface/recessed steel/ PVC conduit as required. | Rm | 175
9 | 1.21 | Supplying and fixing of following sizes of PVC conduit along with accessaries in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
a) | 1.21.1 | 20 mm | Rm | 1200
b) | 1.21.2 | 25 mm | Rm | 50
10 | 1.22 | Supplying and fixing metal box of following sizes ( Nominal size ) on surface or recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
a) | 1.22.13 | 200 mmx 300 mmx 60mm deep | Each | 4
11 | 1.24 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc as required.
a) | 1.24.6 | Telephone socket outlet | Each | 15
b) | 1.24.7 | TV antena socket outlet | Each | 5
12 | 1.25 | Supplying and fixing stepped type electronic fan regulator on the existing modular plate and switch box excluding modular plate but including connections etc as required. | Each | 65
13 | 1.26 | Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | Each | 40
14 | 1.27 | Supplying and fixing following size/ modules,GI box along with modular base, cover plate for modular switches in recess etc as required.
a) | 1.27.1 | 1 or 2 module( 75 mmx75 mm) | Each | 85
15 | 1.31 | Supplying and fixing suitable size G. I box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc as required, | Each | 110
16 | 1.32 | Supplying and fixing suitable size G. I box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 15/16& 5/6 amps modular socket outlet and 15/16 amps modular switch, connection,painting etc as required. | Each | 30
17 | 1.33 | Supplying and fixing 3 pin , 5 amps ceiling rose on the existing junction box / wooden block including connection etc as required. | Each | 60
18 | 1.38 | Supplying and fixing call bell / buzer suitable for D.C / A.C single phase, 230 volts, complete as required. | Each | 10
19 | 1.41 | Installation testing and commissioning of pre- wired, fluroscent fitting / compact fluroscent fitting of all types, complete with all accessories and tube etc. directly on ceiling / wall, including connection with 1.5 sq mm FR PVC insulated,copper conductor, single core cable and earthing etc as required. | Each | 70
20 | 1.42 | Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc., including supplying and fixing ball and socket arrangement, 2 no. down rods of 20 mm dia X 1.6 mm thick steel conduit upto 30 cm length, painting and wiring the down rods and connection with 1.5 sq. mm FRLS PVC insulated,copper conductor, single core cable and earthing etc. as required | Each | 80
21 | 1.43 | Providing and fixing extra conduit downrod of 20mm dia 2x10cm length wiring with 2x1.5 sqmm FRLS PVC insultated copper conductor single core cable including painting etc as required. (Note: More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored). | Each | 120
22 | 1.44 | Installation ,testing and commissioning of ceiling fan, including wiring the down rods of standard length { Up to 30 Cm } with 1.5 sq mm FR PVC insulated, copper conductor, single core cable as reqjired. | Each | 65
23 | 1.47 | Supplying and fixing extra down rod of 10 Cm length G. I pipe, 15 mm dia, heavy guage including painting etc. as required ( Note: More than 5 Cm length shall be rounded to the nearest 10 Cm and 5 Cm or less shall be ignored) | Each | 140
24 | 1.50.1 | Installation of exhaust fan up to 450 mm sweep in the existing opening, including, making the hole to suit the size of the above fan, making good the damage, connection, testing , commissioning etc as required. | Each | 20
25 | 1.53 | Supply and drawing of UTP 4 pair CAT 6 LAN cable in the exisitng surface / recessed steel / PVC conduit as required. | Rm | 100
26 | 2.2 | Providing and fixing following rating and breaking capacity and pole MCCB in the existing cubicle panel board including drilling holes in cubicle panel, making connections etc as required.
a) | 2.2.1 | 100 Amps, 16kA, TP MCCB | Each | 2
27 | 2.6 | Supplying and fixing following way, surface / recess mounting, vertical type, 415 volts, TPN MCB distributon board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, neutral bus bar, earth bar, din bar for mounting MCB's with provision of 100 amps TP 16kA MCCB as incomer, interconnection between incomer MCCB and bus bars (but without MCB's / MCCB) as required. (Note: Verticle type MCB TPDB is normally used where 3 phase outlets are required).
a) | 2.6.1 | 4 way TP | Each | 1
b) | 2.6.2 | 8 way TP | Each | 1
28 | 2.8 | Supplying and fixing following way, prewired TP&N MCB distribution board of sheet steel, for 415 volts on surface/recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FRLS PVC insultated copper conductor upto terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc as required. (But without MCB/RCCB/Isolator).
a) | 2.8.5 | 4 way, Double door | Each | 3
b) | 2.8.6 | 6 way, Double door | Each | 3
29 | 2.9 | Supplying and fixing following way, prewired TP&N MCB distribution board of sheet steel, for 415 volts on surface/recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly pre-wires with adequate size of FRLS PVC insulated copper conductor upto the terminal connector / neutral link, earthing etc as required (But with out MCB/RCCB/Isolator). (Note: Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required).
a) | 2.9.5 | 4 way, Double door | Each | 1
b) | 2.9.6 | 6 way, Double door | Each | 1
30 | 2.1 | Supplying and fixing 5 amps to 32 amps rating, 240 Volts ' C ' series, miniature circuit breaker suitable for inductive load of the following poles in the existing MCB DB complete with connections, testing and commissioning etc as required.
a) | 2.10.1 | Single pole | Each | 60
a) |  | Single pole | each | 60
b) | 2.10.4 | Triple pole | Each | 10
b) | 2.10.5 | Tripple pole and neutral | Each | 6
c |  | Triple pole & neutral | Each | 6
31 | 2.11 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc as required. | Each | 20
32 | 2.15 | Supplying and fixing following rating,four pole,415 volts, residual current circuit breaker { RCCB }, having a sensitivity current up to 300 milli amperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a) | 2.15.1 | 25 amps | Each | 2
b) | 2.15.2 | 40 amps | Each | 4
b) | 2.15.3 | 63 amps | Each | 3
33 | 2.13 | Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a) | 2.13.1 | 40 amps | Each | 2
b) | 2.13.2 | 63 amps | Each | 4
34 | 2.17 | Supply abd fixing TP sheet steel enclosure on surface / recess along with 16/25/32 amps 415V, C curve TP MCB complete with connections, testing and commissioing etc as required. | Each | 8
35 | 4.1 | Supplying and installing following size of perforated GI cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with GI suspenders including bolts & nuts, suspenders, bends, tees etc as required.
a) | 4.1.4 | 300 mm width X 50 mm depth X 1.6 mm thickness | Rm | 50
36 | 2.18 | Supplying and fixing 20 amps, 240 Volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top along with 20 amps 'C' series, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket outlet and complete with connections, testing and commissioning etc. as required. | Each | 10
37 | 5.4 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | Set | 2
38 | 5.9 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | Rm | 30
39 | 5.15 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | Rm | 80
40 | 5.17 | Providing and fixing 4 mm dia copper wire on surface or in recess for loop earthing as required. | Rm | 160
41 | 7.7 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
a) | 7.7.1 | Upto 35 sq. mm (clamped with 1mm thick saddle) | Rm | 300
b) | 7.7.2 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | Rm | 90
42 | 7.8 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
a) | 7.8.1 | Upto 35 sq. mm (clamped with 1mm thick saddle) | Rm | 400
b) | 7.8.2 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | Rm | 100
43 | 9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
a) | 9.1.32 | 4 x 10 Sq mm | Each | 10
b) | 9.1.33 | 4 x 16 Sq mm | Each | 12
c) | 9.1.9 | 3.5 x 25 Sq mm | Each | 8
d) | 9.1.21 | 3.5 x 35 Sq mm | Each | 6
e) | 9.1.22 | 3.5 x 50 Sq mm | Each | 4
f) | 9.1.23 | 3.5 x 70 Sq mm | Each | 4
44 | 14.13.3 | Providing, laying & fixing 100mm dia GI pipe (medium class) in ground complete with GI fittngs including trenching (75cm) deep and refilling etc as required. | m | 30
45 | LMR | Supply of 1x28 watts surface mounted luminaire, CRCA powder coated housing, aluminium reflector, pre-wired complete with all accessories like electronic ballast, 28W T5 lamp etc complete as required. (Philips TMS 122 M IxTL5-28W EBE / GE GET CI 1x28 C/S HF / Crompton T5RSF28EB). | Each | 110
46 | LMR | Supply of 1x28 watts fluroscent tube fitting sleek with decorative end cap, powder coated CRCA steel channel complete with all electrical accessories like electronic ballast, lamp holder, 28W T5 lamp etc complete as required. (Philips TMS 540 HF / GE LMS 28 N N / Crompton T5GP28EBS9). | Each | 15
47 | LMR | Supply of 1x28 watts surface mounted mirror optic luminaire, powder coated CRCA housing, complete with all accessories like electronic ballast, 28W T5 lamp etc complete as required.(Philips TCS150 IxTL5 -28W MI EBT / GE GETC 1x28 MOS HF / Crompton T5CS128EB). | Each | 25
48 | LMR | Supply and fixing of 2x36W, indoor clean room, recess mounted light fixture with CRCA housing, pre-anodised aluminium reflector and control gear tray duly powder coated, clear acrylic cover, non-hygroscopic gasket to ensure dust proofing, 36 W CFL lamps, prewired complete with all necessary accessories suitable for operation on 230V, 50Hz AC supply as required including chain, mounting hook, anchor fastner etc as required. (Philips FCS650 2xPL-L36W EBP FOP GT / GE CRP 236CFL BO / Crompton CRFW 12236EB). | Each | 12
49 | LMR | Supply of ceiling fan 1200 mm sweep, double ball bearing, approved colour and quality with original down rod, suspension shackle, canopy etc with out regulator complete with all accessories as required. (Usha Sonata Max or equivalent) | Each | 65
50 | LMR | Supply of medium duty exhaust fan 300 mm sweep, metal blades of approved colour, for single phase 230 volt, 50Hz AC supply complete with motor, capacitor, metal grill cover and all accessories as required complete. (Usha Turbo Hi speed or equivalent) | Each | 20
51 | LMR | Supply and installation of 400 mm sweep, wall fan, swinging type with speed control, necessary adapter, of approved colour, for single phase 230 volt, 50Hz AC supply complete with motor, capacitor all accessories as required complete. (Usha Max Air or equivalent) | Each | 5
52 | LMR | Supply & fixing PVC straight / Angle batten holder with ISI marking including connection etc complete with all accessories as required. | Each | 25
53 | LMR | Supply and fixing ISI marked Compact Fluroscent Lamp (CFL), 15 watts of approved quality. | Each | 25
54 | LMR | Supply and fixing Polished aluminium reflector on the PVC straight / angle batten holder etc complete as required. | Each | 25
55 | LMR | Supply of the following size 1.1kV grade XLPE insulated PVC sheathed, armoured Aluminium conductor power cable confirming to IS 7098 (part 1) ammended upto date.
a) |  | 4 x 10 Sq mm | Rm | 120
b) |  | 4 x 16 Sq mm | Rm | 220
c) |  | 3.5 x 25 Sq mm | Rm | 180
c) |  | 3.5 x 35 Sq mm | Rm | 150
d) |  | 3.5 x 50 Sq mm | Rm | 90
e) |  | 3.5 x 70 Sq mm | Rm | 100
56 | LMR | Supplying and fixing following rating, 415 Volts, "C" curve, miniature circuit breaker suitable for power loads of following poles in the existing MCB DB complete with connections, testing and commissioning etc as required.
a |  | 40A TP MCB | Each | 2
b |  | 63A TP MCB | Each | 4
|  | 63A TP MCB | Each | 4
57 | LMR | Supply & fixing modular type computer outlet (RJ-45) with modular base and cover plate, GI box complete with all accessories, connection etc. complete as required. | Each | 5
58 | LMR | Supply and Installation of 10 pair MDF box, back mount frame and original 10 pair krone connectors including connection with all accessories. | Each | 2
59 | LMR | Supplying and laying 10 SWG copper wire on surface / recess / groundloop earthing, including soldering connection / termination with Cu thimble etc as required | Rm | 100
60 | LMR | Supplying and fixing FP sheet steel/PVC enclosure with IP 54 protection on surface/ recess for 63A TPN MCB with connections, testing and commissioning etc. as required. | Each | 6
61 | LMR | Dismantling the existing light fixing, ceiling fan, exhaust fan, wall fan etc. and stacking the same to the place as per the direction of engineer in charge. | Each | 75
62 | LMR | Dismantling the existing MCB DB / SFU DB including the incoming & outgoing cables / wires etc. and stacking the same to the place as per the direction of engineer in charge. | Each | 5
63 | LMR | Dismantling the existing switch board including socket/switch including wiring, conduits etc and stacking the same to the place as per the direction of engineer in charge. | Each | 45
64 | LMR | Rewiring for light point/fan point/exhaust fan point/ call bell point with 1.0 sq.mm FRLS PVC insulated copper conductor single core cable and 1.0 sq.mm. FRLS PVC insulated copper conductor single core cable as earth wire in existing surface/ recessed PVC conduit including dismantling as required. | Point | 15
65 | LMR | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel / PVC conduit as required.
a) |  | 1 x 1.0 sq. mm | m | 800
66 | LMR | Preparation of electrical drawing for the building, submission of drawings to Electrical inspectorate and obtaining approval, arranging inspection for entire installation and other utilities, obtaining road cutting permission obtaining sanction orders for the elctrical installation. Necessary power allocation, service connection, energising the installation from KSEB complete. Including all incidental expenses except the fees payable to the electrical inspectorete with valid receipts from the authorities. | Job | 1
67 | LMR | Supply and providing 6 mm thick & 1 m wide electrical grade chequered type rubber mat to withstand 3.3 KV dielectric strength conforming to IS 5429/ 1969. | Rm | 5
68 | LMR | Supply and providing First Aid Chart duly framed and placed in a conspicuous location for clear vision. | Each | 2
TOTAL - PART B ELECTRICAL WORKS