## Final BOQ
BILL OF QUANTITIES
S no | Unit | Rate (INR) | Description of Items | Qty | Amount (INR) | Make/Items used
1 | LS |  | Dismantling existing ceiling, electrical fixtures, floorand cladded tiles, paver block, aluminium partition etc. and disposal of waste material and handing over the servisiable materials to AIIMS. | 1
2 | Sqm |  | P/L 15mm Cement Plaster of mix 1:4:2 (1Cement:4 Fine sand:2 Coarse sand) in line, level and plumb including smooth cement finish as directed including providing necessary bands, drip would groove and wire-mesh at all junction of walls and ceiling, necessary curing scaffolding etc. complete as directed and specified. | 20
3 | Sqm |  | P/F ISI marked Flush door shutter conforming to IS :2202 (Part I) non-decorative type, core of block board construction with frame of 1st class hard wood and well matched commercial 3 ply veneering with vertical grains or cross bands and face veneers on both faces of shutters, 35 mm thick including both side laminate and ISI marked Stainless Steel butt hinges, door closer, mortise lock, handle etc complete with necessary screws as per direction. The work also includes 150x65mm size teak wood door frame duly melamine polished. | 2.1
4 | Sqm |  | P/F 12mm thick Toughened Glass in Partition, fixed with SS 'U' channel in floor and ceiling, Finish with silicon as per design intend. | 30
5 | Sqm |  | P/F Grid ceiling -25mm tabular to fix Dune Prime tile 600x600mm installation. To comprise main runner spaced at 1200mm centers securely fixed to the structural soffit using 150mm from spliced joints. The First/Last suspension system at the end of each main runner should not be greater than 600mm from the adjacent wall. 1200mm long cross tees to be interlocked between main runners at 600mm center to form 1200 x 600 mm module. All Perimeter trim to be wall angles, secured to walls at 450mm maximum centers. Suspention System accessories manufactured and supplied consisting of M6 anchor fasteners with vertical hangers made of galvanized steel of size 26x26 x25x1.2mm. Straightened Hanger wire of dia-2.68 mm of 1.83 m length., thickness with adjustable hook clips of 0.8mm thick. The adjustable clip also consists of a 3.5mm aquiline wire to be used with the main runner. | 40
6 | Nos |  | P/F Single Leaf Glass door made of 12mm thick tempered glass. The rate should be inclusive of all hardware Ozone upper patch bottom patch Ozone make door handle OGH 55(25 x600)/ PSS/ SSS-H shape, Ozone make floor spring FS 8400, floor lock, strike plate & EP cylinder etc complete as per design and drawing. | 1
7 | Nos |  | P/F of prelaminated Over head Storage unit of of AFC Make 25mm. thick prelam board top PVC edge-binding as/design 18mm thick prelam board hinged shutter with laminate and handle with individual locks.6mm thick laminated ply as backing of the unit along. with 18mm thick prelam board as adjustable shelves. | 1
8 | Nos |  | P/F of 2100x450x300mm size Medicine Storage with vertical suports with prelaminated 25mm Post formed over MDF board as/design 25mm thick prelam board top with to be provided at 450mm ht, 18mm thick prelam board drawer with laminate and handle with individual locks. 6mm thick laminated ply to be used as backing of the unity along with 12mm thick toughened glass (7nos) as adjustable shelves. The edges will have 150x300mm toughtned glass open selfs complete in all respect as per drawing. | 27
9 | Nos |  | P/F Modular Workstation 1400x600mmx1200mm high of main screen with powder coated trims fabric panel and writing board above table top and laminated panel below work top. Side screen of fabric above table top and laminate below table top. Relevant raceways one at skirting level and one able table top to be provided. Table top-25mm thick prelaminated Worktop with one padestal unit of size 450x550x740mm complete with one lock system complete in all respect as per direction. | 1
10 | Nos |  | P/F 3mm thick 250mm wide 450mm length SS Printer ledges suspended and screwed by SS steel string as per architects approval and design. | 1
11 | Nos |  | P/P fabric seat/back, 5 pronged chrome plated finish base Stool of on twin wheel casters, with 3600 swivel Gas lift height adjustment, | 2
12 | Nos |  | P/P medium back fabric Chairs, 5 pronged chrome plated finish base on twin wheel casters with 3600 swivel Gas lift height adjustment, synchrotilt mechanism with locking facility having chrome arms fixed on cast aluminum frame. Color of upholstery as/app. | 1
13 | Nos |  | P/F Signage Board of size 9.0x0.6m with Acrylic LED Letter of 1" thickness of 60 font with led neon lighting fixed with studs. Having timer and 12volt power supply and transformer for continuous supply. | 1
14 | Sqm |  | Apply three coats of Plastic Paint. Paint shall emit 90% less VOC, soft sheen, high scrub resistant, free from lead, mercury chromium. | 70
15 | Nos |  | P/F 100Amp 10KA, TPMCCB in existing cubical panel making connection etc as required as per direction of Engineer - in- charge. | 1
16 | Nos |  | Vertical Distribution Board with 100Amp 10 KA, TPN MCCB as incomer and 100Amp 10 KA, TPN MCCB-1no., 63Amp 10KA TPN MCCB - 1no. with 200amp al busbar making connection etc as required. | 1
17 | Mts |  | Wiring for Sub-Mains-Wiring with 4x16sqmm +2x16sqmm earth wire of FR PVC insulated, multi-stranded copper conductor single core cables in surface/recessed PVC conduit as required. | 25
18 | Nos |  | 12 way SPN-DB, 9No. 6amps SP MCBs, 6No. 16amps SP MCBs & 5Nos. 20amps SP MCBs as outgoing & 1No.40amps FP RCBO of 100mA leakage current and 1No.40 amps 4Pole MCB as incomer with separate neutral link for each phase. | 2
19 | Mts |  | S/L/T of under 3.5C 50sqmm of Aluminum Conductor XLPE insulated PVC sheathed & sleeved armored and overall PVC sleeved 1.1KV grade power distribution cables conforming to relevant IS code and as per specification in ground through pipe or on wall/ racks cable trays including dressing and clamping the cable with MS zinc passivity clamps etc. as required. | 40
20 | Mts |  | S/L/T of under 4C 25sqmm of Aluminum Conductor XLPE insulated PVC sheathed & sleeved armored and overall PVC sleeved 1.1KV grade power distribution cables conforming to relevant IS code and as per specification in ground through pipe or on wall/ racks cable trays including dressing and clamping the cable with MS zinc passivity clamps etc. as required. | 30
21 | Mts |  | S/L/F 8core 2.5sqmm un-armored Control cable from D.G. set to AMF panel as per direction of Engineer - in- charge. | 35
22 |  |  | Wiring for the following Light Points with 2x1.5sqmm PVC insulated copper conductor 1100volts grade stranded flexible FRLS wires of approved make in concealed or surface mounted 19mm dia with medium duty PVC conduit including P/F of 6amps single pole rocker operated flush mounted switch of approved quality color make & design in 2mm well thick GI box and earthling of fixtures and the outlet box with 1sqmm PVC insulated copper conductor stranded flexible FRLS wire.
23 | Nos |  | Two light controlled by one 6A modular one way Switch. | 8
24 | Nos |  | P/F UPS POINT A 3No. Modular Socket 1no, Modular Switch with 18SWG G.I Box & Modular Face Plate complete as directed. | 8
25 | Nos |  | Wiring for Fan Point with 2x1.5sqmm insulated copper conductor 1100volts grade stranded flexible FRLS wires of approved make in 19mm dia medium duty PVC conduit including P/F of 6amps flush mounted switch at the normal switch level in 1.6mm thick GI box and 6amps 3pin flush mounted socket near exhaust fan and earthling of exhaust fan through the third pin of the socket outlet and GI box with 1.5sqmm PVC insulated copper conductor flexible FRLS wire. | 5
26 | Nos |  | Wiring for 250volts single phase and neutral 16amps Switched Socket outlet with 4sqmm PVC insulated copper conductor 1100volts grade stranded flexible FRLS wires in concealed or surface mounted 25mm dia with heavy duty FRLS PVC conduit including P/F of 16amps 3pin switched sockets of approved make and design in 1.6mm thick GI box with grid plates and earthling the third pin of each socket outlet with 2X2.5+1x2.5 sqmm PVC insulated copper conductor stranded flexible FRLS wire (Power points). | 2
27 | Nos |  | P/F/T/C of under noted rating flush type Industrial Socket Outlet with plug top controlled by MCB all mounted in M.S. sheet steel box duly painted In recess/surface complete as required (excluding, wiring and conduit) 20Amps 3pin socket outlet controlled by 16amp MCB with 2x4.0sqmm + 1x2.5sqmm FR PVC insulated multi stranded copper conductor single core cable in surface /recessed PVC conduit | 1
28 | Nos |  | S/F/T/C of minimum 40watt LED Recessed type Light fixture (600x600 mm) Wipro cat no. LM17-411-XXX-57-XX extruded aluminum Luminaries with heat sink installed back side, high quality diffuser fix in front frame max depth of 10mm total system wattage less than 45W with LED make of Cree/ Nichea (36x1W LED) operating at 350mA. lamp color 4000k, complete with electronic driver, CRI80, lockable holders and including connection etc. as required. | 15
29 | Nos |  | S/I/T/C of 400mm sweep 1250RPM, 240 V, 50Hz single phase Wall Bracket Fan of approved make & color confirming to IS complete with three blade oscillatory/ fixed and pulling chord arrangement for operation of speed regulator and oscillating mechanism, clamps screw etc. | 3
30 | Nos |  | S/I/T/C of 400mm sweep 1400RPM, 240 V, 50Hz High Speed Wall Bracket Fan of approved make & color confirming to IS complete with three blade oscillatory/ fixed and pulling chord arrangement for operation of speed regulator and oscillating mechanism, clamps screw etc. | 2
31 | Mtr |  | S/I/T/C of 0.5mm dia annealed Copper conductor PVC insulated sheathed Telephone wire in existing conduit/wire way duct etc as required of following sizes:2 pair (4 core) | 100
32 | Nos |  | S/F M.S. box with modular type Telephone (RJ-11) outlet complete as required. | 3
33 | Mtr |  | P/L/T/C of data/computer Cat-6 cable along wall or ceiling or through conduit | 160
34 | Nos |  | S/F M.S. box with modular type Data/computer RJ-45 outlet complete as required. | 8
35 | Nos |  | S/I/T/C of 8-Port Switch as per specifications complete as required. | 1
36 | Nos |  | SI/T/C of fully closed 4U Rack Cabinet with dual source power supply all accessories as per specifications complete as required. | 1
37 | Nos |  | S/L/T/C of cat-6 Patch Cord 3.0m long complete as per specification as required. | 8
38 | Nos |  | S/I/T/C of cat-6 Patch Cord 1.0m long complete as per specification as required. | 8
39 | Nos |  | S/I/T/C of 4 Channel color Digital Video Mgmt system with 4 cameras inputs Built in multiplexer, Digital Video recorder & 500GB HOD | 1
40 | Nos |  | S/I/T/C of CCD Colored Cameras, 1/3inch 480 lines, HIGH RESOLUTION, with IR Leds for Day and night vision or equivalent complete as required in mini dome shape fixed type, including all wiring from the control module in existing PVC conduits complete as required. | 4
41 | Nos |  | S/I/T/C of Power-Supply unit complete as required. (One no for set of 5 cameras). | 1
42 | Nos |  | S/I/T/C of 1/8 EPBAX (Telephone Exchange) advance Hybrid PBX system with power supply and battery back-up for 45minuts complete in all respect as per direction of Project-In-Charge. | 1
43 | Nos |  | S/I/T/C of Telephone Instruments BEETAL make complete as per direction. | 3
44 | Nos |  | Wiring for FIRE-ALARM-SYSTEM S/L 2core, 1.5sqmm armored cable complete in all respect including all accessories. | 70
45 | Mtr |  | S/I/T/C of ionization type Smoke Detector, twin blinking LED as required. | 4
46 | Nos |  | S/I/T/C of duel tone Electronic Hooter suitable for wall mounted electronic hooter for complete with 75 decibel sound as required. | 1
47 | Nos |  | S/I/T/C of Manual Call Box in suitable enclosure with hammer. | 1
48 | Nos |  | CO2 Type Fire Extenguisher | 2
49 | Nos |  | S/I/T/C of micro process base main Fire Alarm Control Panel of 2(two) Zone capacity as complete with Exide batteries & charger illuminated numeric display complete as required. | 1
50 | Nos |  | S/I/T/C of 3 KVA UPS system configuration with three phase Input and Single Phase Output True On Line Double Conversion UPS including Battery Circuit Breaker for each Module CRCA housing with all required fixing accessories and hardware, Inbuilt Galvanic Isolation Transformer at the output, Inbuilt Static switch bypass and inverter in each UPS module, In-Built Manual Maintenance by-pass, inbuilt batteries for 15min back up. etc complete as required. | 1
51 | Nos |  | D/I/T/C of 3-phase, 15 KVA, 12 KW, 22 BHP (CPCB-I) 1500 RPM Silent DG Set at 0.8mm P/F lagging diesel engine alternator set mounted on common base frame in outdoor type acoustic enclosure, with battery charger, return fuel cooler, anti vibration mounting pads including residential silencer, engine alternator, DG Exhaust, insulation, supports as per site conditions, safeties with accessories as per specification complete as required. Diesel engine shall conform to IS:10000 and alternator shall be self excited. | 1
52 | Nos |  | 15 KVA AMF Panel contactor based with Contactor 40A, 4 pole,Indication Lamp, metering, changeover 63A 4pole, cubical panel box made out from 18 SWG CRCA sheet steel duly powder coated with Siemens Grey and size of panel shall be 600mm (w)X1000 mm (H)X200mm (D) or suitable complete. | 1
53 | Nos |  | Earthing with 2.5 mtr Earthing Electrode of 38 mm G.I. Pipe including accessories and providing masonry enclosure with cover plate having locking arrangement with watering pipe complete with coke and salt etc. as required. | 1
54 | Mts |  | P/F/L of 25x3 mm G.I Strip | 30
55 | Mts |  | P/F/L of 8 No. mm G.I Wire | 40
56 | Nos |  | S/I/T/C 2.0 Ton Spit Wall mounted type AC of Hitachi make including out door and indoor units wiring | 1
57 | Mtr |  | Refrigerant pipe insulation and accessories for the split type units. | 5
58 | Mtr |  | S/I/T/C of CPVC drain piping 25mm complete with fitting, supports, valves, and 6 mm thick nitrile rubber foam insulation as per specifications and drawings. | 10

## Approved Materials
LIST OF APPROVED MATERIALS
Laminated sheet (1.0 mm thick) | Formica/Greenlam/Sunmica/Merino/ Century/national
Comm. Board | Greenply/Kitply/Century/ Merino
Commercial Ply wood | Greenply /kitply/Century/ Merino
MR grade ply Conforming to IS 303 | Greenply /kitply/Century/ Merino
Ply wood Conforming IS 710 | Greenply /Kitply/Century/ Merino | A
Block Board | Greenply /kitply/Century/ Merino
Melamine Finish | Asian Paints/Nerolac/ICI
Modular Furniture | Intex Lifestyle/AFC/Spark International/ Godrej
Ceramic Tiles/vitrified homogeneous glazed tiles. | HR Johnson/ Kajaria/ Nitco/Marbo-Granit
Glazing (Clear) | St. Gobain/ Indo Asahi/ Modi float
Hardware | Dorma./Hetich/Godrej/Ozone/hafele
Sanitary Ware | Parryware/Hindware/Cera/Jagaur
Stainless Steel sink | A.M.C. /Diamond / Nirali
C.I. Pipe | RIF/NEC
PVC Pipe | Prince,
Nahani Trap | NECO
G.I. Pipe | TATA/ Jindal/Surya
Bends | Unik
Gate Valve | Leader
Sanitary Convenience Fittings | Kimberly Clarke
Sanitary ware | Perryware/Hindware/Cera/Jagaur
False Ceilings: Gypsum | India gypsum/ST. Gobain
Acoustical False Ceilings: Mineral fiber board | Armstrong/Gypsum India/ ST. Gobain
Glue | Fevicol/Pidlite
Paint | Asian/ ICI / Nerolac
Locks | Godrej/ Harrison
Cyndiral lock | Godrej/ Harrison
Electrical Wires/Cables (PVC Insulated Copper Fire resistant Cable) | Grandlay/Finolex/Polycab/Skytone/RR Kabel. (ISI MARKED ONLY)
Electrical Switches/Dimmers/Modular Plate Switch Socket/TV Socket/Telephone Socket/Computer Socket. | Northwest/ MK/ Clipcell MDS/Legrand
Electrical Distribution Boards | MDS/Sleek /Siemens/ Legrand/L&T
Electrical Conduits | 2 MM PVC CONDUITS AKG/SETIA
Electrical Fixtures | PHILIPS/ CROMPTON GRAVES/WIPRO
Electrical Tube lights/ PL Lights | PHILIPS/OSRAM/WIPRO
Ceiling/Exhaust Fans | CROMPTON/BAJAJ
MCB/MCBDB | MDS/SCHNEIDER/ABB/GE
MCCB | MDS/SCHNEIDER/ABB/GE
Indication Lamp | BCH/L & T
Ammeter, Voltmeter | AE/ENERCON
CT’S | AE/KAPPA
Selector Switch | SALZER/KAYCEE
Data and Voice Networking Cable | AMP/MOLEX/SIMON/DLINK
Patch Panel | HCL/DIGITAL/COMRAC/DLINK
Information Outlets | AMP/MOLEX/SIMON/DLINK
Patch Cords | AMP/MOLEX/SIMON/DLINK
Keyboard trays | EBCO/Supreme/Dortel
Telephone | Beetel
Air conditioner | Samsung, Hitachi, Voltas, Lloyd
Fire Alarm systems | Appollo, GST, Ozone
DG Sets | Mahindra,Greaves, Kirloskar
Fire Extingusher | Ceasefire/Safex
UPS Systems | Eaton/Microtek/Poweron