## civil-+ELEab -final (hidden)
ESTIMATE FOR CIVIL&ELECTRICAL WORKS IN CONFERENCE HALL IN KAKKANADU FACTORY,COCHIN
Item no. | DSR | Item Description | Qty | Unit | Rate | Rate+CI | Amount
CIVIL WORKS(PART-A)
1 | 15.2.2 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material as per direction of Engineer-in-charge. | 10 | Cum | 550.5 | 796.9038 | 7969.038
2 | 15.3 | Demolishing R.C.C. work manually/ by mechanical means includingstacking of steel bars and disposal of unserviceable material as per direction of Engineer - in- charge. | 1 | Cum | 1302.3 | 1885.2095 | 1885.2095
3 | 15.5 | Extra for cutting reinforcement bars manually/ by mechanical means inR.C.C. or R.B. work (Payment shall be made on the cross sectional areaof R.C.C. or R.B. work) as per direction of Engineer -in -charge. | 30 | Sqm | 450.45 | 652.0714 | 19562.1426 | 30
4 | 15.23.1 | Dismantling tile work in floors, dadoing and roofs laid in cement mortar including stacking material within 50 metres lead.For thickness of tiles up to 25 mm | 25 | Sqm | 28.2 | 40.8223 | 1020.558
5 | 15.5 | Dismantling of Water closets/wash basin/flushing cistern etc. of all types (C.I./PVC/Vitrious China) including stacking of useful materials near the site and disposal of unserviceable materials | 2 | Each | 519.87 | 752.5638 | 1505.1276 | 2 | Nos
6 | 15.6 | Disposal of building rubbish / malba / similar unserviceable, dismantled or waste materials by mechanical means including loading, transporting, unloading to approved municipal dumping ground or as approved by Engineer-in-charge, beyond 50 m initial lead, for all loads including all lifts involved. | 40 | Cum | 123.7 | 179.0681 | 7162.7248
7 | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30cm in depth. 1.5m in width as well as 10 sqm on plan) including disposal of excavated earth and lift upto 1.5m, disposed earth to be levelled and neatly dressed.:All kinds of soil | 3.375 | Cum | 155.6 | 225.2466 | 760.2071
8 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All works up to plinth level-.1:4:8 (1 Cement : 4 coarse sand : 8 graded stone aggregate 40mm nominal size) | #REF! | Cum | 4301.2 | 6226.4171 | #REF!
9 | 5.37 | Providing and laying in position ready mixed M-25 grade concrete for reinforced cement concrete work, using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , excluding the cost of centering, shuttering finishing and reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, improve workability without impairing strength and durability as per direction of the Engineer - in - charge. |  |  |  | 0 | 0 | 0
|  | (Note :- Cement content considered in this item is @ 330 kg/cum. Excess/less cement used as per design mix is payable/recoverable separately). |  |  |  | 0 | 0 | 0
| 5.37.2 | All work above plinth level up to floor V level -RCC work (M25 concrete) | 22.3373 | Cum | 7363 | 10658.6788 | 238085.605 | #VALUE!
10 | 5.9 | Centering and shuttering including strutting, propping etc., and removal of form for, |  |  |  | 0 | 0 | 0
10.a | 5.9.1 | Foundations, Footings, bases of columns,etc for mass concrete. | 2.25 | Sqm | 196.45 | 284.381 | 639.8573
10.a | 5.9.6 | Columns and Pillars, Piers, Abutments, Posts and Struts. | 64 | Sqm | 453.35 | 656.2695 | 42001.2454
10.b | 5.9.3 | Suspended floors, roofs, landings, Balconies and access platform | 103 | Sqm | 453.35 | 656.2695 | 67595.7544
10.c | 5.9.5 | Lintel,beams,plinth beams,girders,bressumers and cantilevers | 74 | Sqm | 332.15 | 480.8203 | 35580.7052
10.d | 5.9.19 | Weather shade, Chajjas, corbels etc., including edges | 15 | Sqm | 492.35 | 712.7259 | 10690.8879
11 | 5.22.A.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending,placing in position and binding all complete above plinth level. :Thermo-Mechanically Treated bars | 2203.5283 | Kg | 68.1 | 98.5816 | 217227.2593
12 | 6.4.2 | Brick work with F.P.S bricks of class designation 5.0 in superstructure above plinth level up to floor v level in all shapes an sizes in: Cement mortar 1: 6 (1 cement :6 coarse sand) | 24.1605 | Cum | 5426.15 | 7854.8947 | 189778.4679
13 | 6.13.1 | Half brick masonry with F.P.S brick of class designation 7.5 in superstructure above plinth level up to floor V level : CM 1:3 (1 cement : 3 coarse sand) | 28.88 | Sqm | 692.8 | 1002.8973 | 28963.6734
14 | 6.15 | Extra for providing and placing in position 2 Nos. 6mm dia M.S bars at every third course of half brick masonry (with FPS brick) | 28.88 | Sqm | 69.5 | 100.6082 | 2905.5648
15 | 13.2.1 | 15mm cement plaster on the rough side of single or half brick wall of mix : 1 : 4 (1 cement : 4 fine sand) up to 10m height for external walls | 74 | Sqm | 189.4 | 274.1754 | 20288.9826
16 | 13.1.1 | 12mm cement plaster on the rough side of single or half brick wall of mix : 1 : 4 (1 cement : 4 fine sand) for internal walls, column and beams etc | 305.1168 | Sqm | 163.35 | 236.4655 | 72149.5845
17 | 13.16.1 | 6 mm cement plaster of mix : 1:3 (1 cement: 3 fine sand) for ceiling plastering | 93.1392 | Sqm | 134.7 | 194.9917 | 18161.3728
18 | 13.8 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. | 398.256 | Sqm | 89.65 | 129.7773 | 51684.6043
19 | 13.60.1 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade –Two or more coats on new work.-internal walls | 398.256 | Sqm | 80.5 | 116.5318 | 46409.4885
20 | 13.48.1 | Finishing walls with Acrylic Smooth exterior paint of required shade : New work (Two or more coat applied @ 1.67 ltr/10 sqmover and including priming coat of exterior primer applied @ 2.20 kg/ 10 sqm) | 74 | Sqm | 100 | 144.76 | 10712.24
21 | 13.48.3 | Painting Steel work with Delux Multi surface paint to give an even shade.Two or more coat applied @ 0.90 ltr/10sqm over an over an under coat of primer applied @ 0.80ltr/10aqm of approved brand or manufacture. | 3.315 | Sqm | 90 | 130.284 | 431.8915
22 | 8.2.2.2 | Providing and fixing 18mm thick gang saw cut mirror polished premoulded and prepolished) machine cut for kitchen platforms, vanity counters, window sills , facias and similar locations of required size of approved shade, colour and texture laid over 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels. Granite of any colour and shade: Area of slab over 0.50 sqm.: Lowest retail price not less than Rs. 2500.00/m2( Granite to be selected by the Engineer in charge) | 0.9 | Sqm | 2463.55 | 3566.235 | 3209.6115
23 | 9.117.1 | Providing and fixing factory made UPVC door frame made of UPVC extruded section having an overall dimensions as below ( tolerance ± 1mm ), with wall thickness 2.0mm (± 0.2mm), corners of the door frame to be joined with galvanized brackets and stainless steel screws, joints mitered and plastic welded. The hinged side vertical of the frames reinforced by galvanized M.S. tube of size 19x19 mm and 1mm (± 0.1mm) wall thickness and 3 nos. Stainless steel hinged fixed to the frame complete as per manufacturers Specification and direction of engineering -in-change : Extruded section profile size 48x40 mm | 6.72 | M | 213.75 | 309.4245 | 2079.3326
24 | 9.118.1 | Providing and fixing existing door frames: 24 mm thick factory made PVC door shutters made of styles and rails of a UPVC hollow section of size 59x24 mm and wall thickness 2 mm (± 0.2mm) with in built edging on both sides. The styles and rails mitered and joint at the corners by means of M.S. galvanized / plastic brackets of size 75x220 mm having wall thickness 1.0 mm and stainless steel screws. The styles of the shutter reinforced by inserting galvanized M.S. tube of size 20x20 mm and 1mm (± 0.1mm) wall thickness. The lock rail made up of " H" section, a UPVC hollow section of size 100x24 mm and 2mm (± 0.2mm) wall thickness, fixed to the shutters styles by means of plastic/ galvanized M.S.'U' cleats. The shutter frame filled with a UPVC multi chambered single panel of size not less than 620mm, having over all thickness of 20mm and 1mm (± 0.1mm) wall thickness. The panes filled vertically and tie bar at two places by inserting horizontally 6mm galvanized M.S. rod and fastened with nuts and washers, complete as per manufacturer's specification and direction of Engineer- in - charge. (for W,C and bath room door shutter). | 6.72 | Sqm | 2718.6 | 3935.4454 | 26446.1928
25 | 11.41.2 | Providing and laying polished vitrified floor tile in different sizes (thickness to be specified by the manufacturer) with Acid and / or Alkali resistant tiles with water absorptions less than 0.08% and confirming to IS:15622 of approved make in all colours and shades, laid on 20mm thick cement mortor 1:4 (1 cement:4 Coard sand) including grouting the joints with white cement and matching pigments etc. complete. (Lowest retail price not less than Rs. 880/m2) : Size of Tiles 60 x 60 cm (Tiles to be selected by the Engineer in charge) | 68.9249 | sqm | 1405.95 | 2035.2532 | 140279.6247
26 | 11.39 | Providing and laying rectified Glazed Ceramic floor tiles 300x300 mm or more (thickness to be specified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make in colours White, Ivory, Grey, Fume Red Brown, laid on 20mm thick cement mortar 1:4 (1 Cement : 4 Coarse sand) including grouting the joints with white cement and matching pigments etc., complete. | 6.4904 | sqm | 950.05 | 1375.2924 | 8926.1977
27 | 11.4 | Providing and fixing Ist quality ceramic glazed wall tiles of size 300x450mm conforming to IS : 15622 (thickness to be specified by the manufacturer ) of approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados over 12 mm thick bed of cement Mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm including pointing in white cement mixed with pigment of matching shade complete. | 25 | sqm | 1009.6 | 1461.497 | 36537.424
28 | 12.45 | Providing and fixing false ceiling at all height including providing and fixingof frame work made of special sections, power pressed from M.S. sheets and galvanized with zinc coating of 120 gms/sqm (both side inclusive) asper IS : 277 and consisting of angle cleats of size 25 mm wide x 1.6 mmthick with flanges of 27 mm and 37mm, at 1200 mm centre to centre, oneflange fixed to the ceiling with dash fastener 12.5 mm dia x 50mm long with6mm dia bolts, other flange of cleat fixed to the angle hangers of 25x10x0.50mm of required length with nuts & bolts of required size and other end ofangle hanger fixed with intermediate G.I. channels 45x15x0.9 mm runningat the spacing of 1200 mm centre to centre, to which the ceiling section0.5 mm thick bottom wedge of 80 mm with tapered flanges of 26 mm eachhaving lips of 10.5 mm, at 450 mm centre to centre, shall be fixed in adirection perpendicular to G.I. intermediate channel with connecting clipsmade out of 2.64 mm dia x 230 mm long G.I. wire at every junction, includingfixing perimeter channels 0.5 mm thick 27 mm high having flanges of 20mm and 30 mm long, the perimeter of ceiling fixed to wall/partition with the |  |  |  | 0 | 0
help of rawl plugs at 450 mm centre, with 25mm long dry wall screws @230 mm interval, including fixing of gypsum board to ceiling section andperimeter channel with the help of dry wall screws of size 3.5 x 25 mm at230 mm c/c, including jointing and finishing to a flush finish of tapered andsquare edges of the board with recomme-nded jointing compound ,
| 12.45.1 | 12.5 mm thick tapered edge gypsum plain board conformingto IS: 2095- Part I | 48.1626 | sqm | 907.1 | 1313.118 | 63243.1751 | #VALUE! | sqm
29 | 21.1.1.2 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) : For fixed portion: Powder coated aluminium (minimum thickness of powder coating 50 micron) | 115.83 | kg | 377.75 | 546.8309 | 63339.4231
30 | 21.1.2.2 | For shutters of doors, windows & ventilators including providing and fixing hinges/ pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately). Powder coated aluminium (minimum thickness of powder coating 50 micron) | 75.6 | Kg | 435.75 | 630.7917 | 47687.8525
31 | 21.3.2 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.5 mm thickness | 15.12 | sqm | 1054.2 | 1526.0599 | 23074.026
32 | 21.8 | Filling the gap in between aluminium frame & adjacent RCC/Brick/Stone work by providing weather silicon sealant over backer rod of approved quality as per architectural drawings and direction of Enginner-in-charge complete. |  |  |  | 0 | 0
| 21.8.1 | Upto 5mm depth and 5mm width | 10 | Rm | 88.75 | 128.4745 | 1284.745
33 | 21.18 | Providing and fixing 12 mm thick frameless toughened glass door shutter of approved brand and manufacture, including providing and fixing top & bottom pivot & spring type fixing arrangement and making necessary holes etc. for fixing required door fitings, all complete as per direction of Engineer-in-charge ( Door handle, lock and stopper etc. to be paid separately) | 2.7 | Sqm | 4746.3 | 6870.7439 | 18551.0085
34 | MR | Providing and fixing arrangement and making necessary holes etc. for fixing required door fitings, all complete as per direction of Engineer-in-charge Door handle, lock and stopper etc. | 6 | Each | 126 |  | 756
35 | 9.83 | Providing and fixing aluminium die cast body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 35 kg and door width upto 700 mm) with necessary accessories and screws etc. complete. | 2 | Each | 753.75 | 1091.1285 | 2182.257
36 | 9.97 | Providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade with necessary screws etc., complete. |  |  |  | 0 | 0
| 9.97.2 | 250 x 10mm | 8 | Each | 95.25 | 137.8839 | 1103.0712
| 9.97.4 | 150 x 10mm | 8 | Each | 65.35 | 94.6007 | 756.8053
37 | 21.13 | Providing and fixing 100mm brass locks (best make of approved quality) for aluminum doors including necessary cutting and making good etc. complete | 8 | Each | 418.65 | 606.0377 | 4848.3019
38 | 21.12.2 | Providing and fixing aluminium tubular handle bar 32 mm outer dia, 3.0 mm thick & 2100 mm long with SS screws etc .complete as per direction of Engineer-in-Charge. Powder coated minimum thickness 50 micron aluminium tubular handle bar. | 8 | Each | 508.55 | 736.177 | 5889.4158
39 | 9.101 | Providing and fixing aluminium hanging floor door stopper ISI marked anodised (anodic coating note less than grade AC 10 as per IS : 1868) transparent or dyed to required colour and shade with necessary screws etc., complete. |  |  |  | 0 | 0
| 9.101.1 | Single rubber stopper | 3 | Each | 37.5 | 54.285 | 162.855
40 | 21.4 | Providing and fixing double action hydraulic floor spring of approved brand and manufacture IS : 6315 marked, for doors including cost of cutting floors as required, embedding in floors and cover plates with brass pivot and single piect M.S. sheet outer box with side plate etc., complete as per the direction of Engineer-in-charge. |  |  |  | 0 | 0
| 21.4.2 | With brass cover plate | 1 | Each | 2213.2 | 3203.8283 | 3203.8283
41 | 9.149 | Providing and fixing casement handle made of zinc alloyed (white powder coated) for uPVC casement window with necessary screws etc. complete. | 4 | Each | 216.65 | 313.6225 | 1254.4902
42 | 9.68.1 | Providing and fixing oxidised M.S. casement stays (straight peg type) with necessary screws etc. Complete-300 mm weighing not less than 200 gms | 8 | Each | 36.2 | 52.4031 | 419.225
43 | 17.3.1 | Providing and fixing white vitreous china pedestal type water closet (European type) with seat and lid, 10 litre low level white vitreous china flushing cistern & C.P. flush bend with fittings & C.I.brackets, 40mm flush bend, overflow arrangement with specials of standard make and mosquito proof coupling of approved municipal design complete including painting of fittings and brackets, cutting and making good the walls and floors wherever required : W.C. pan with ISI marked white solid plastic seat and lid.(Make: Hindware, Jaquar, Parryware) | 2 | Each | 4784.6 | 6926.187 | 13852.3739
44 | 17.7.1 | Providing and fixing wash basin/counter wash basin with C.I. brackets, 15 mm C.P. brass pillar taps,32 mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever require White Vitreous China Wash basin size 630x450 mm with a pair of 15 mm C.P. brass pillar taps. (Make: Hindware, Jaquar, Parryware) | 2 | Each | 2331.15 | 3374.5727 | 6749.1455
45 | LMR | Providing and fixing C.P. brass long body bib cock of (2 in 1 type)approved quality conforming to IS standards and weighing not less than 690 gms.: 15 mm nominal bore: Make:Jauqar, Hindware, Parryware, crome | 2 | Each | 1540 |  | 3080 | 2 | nos
46 | 17.28.1.1 | Providing and fixing PVC Waste pipe for sink or wash basin including PVC waste fittings complete.:Semi rigid pipe 32mm dia | 2 | Each | 76.75 | 111.1033 | 222.2066 | 2 | nos
47 | 17.34.1 | Providing and fixing Toilet paper holder . Make:Hindware,Cera,Jaquar etc..,:C.P Brass | 1 | Each | 415.9 | 602.0568 | 602.0568 | 2 | nos
48 | 18.65 | Providing and fixing SS soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements. Weighing not less than 106 gms. | 1 | Each | 164.95 | 238.7816 | 238.7816 | 3 | nos
49 | 17.31 | Providing and fixing 600 x 450mm bevelled edge mirror of superior glass (of approved quality) complete with 6mm thick hard board ground fixed to wooden cleats with C.P. brass screws and washers complete. | 1 | Each | 793.95 | 1149.322 | 1149.322 | 1 | nos
50 | 17.73.2 | Providing and fixing SS towel rail complete with brackets fixed to wooden cleats with CP brass screws with concealed fitting arrangement of approved quality and colour. 600mm long towel rail with total length of 645mm, width 78mm and effective height of 88mm, weighing not less than 190gms. | 1 | Each | 541.5 | 783.8754 | 783.8754 | 3 | nos
51 | LMR | Providing & fixing of CP Health faucet. Hand operated spray unit( Instand type)).Make:Jauqar, Hindware, Parryware, crome., (Lowest retail price not less than 1200/each. Materials to be selected by the Engineer in charge) | 2 | Each | 2043 |  | 4086 | 2
52 | LMR | Providing and fixing PVC pipes for water supply arrangements including cost pipes, fittings, solvent cement,testing of pipes, labour charges etc complete : Concealed work including cutting chases and making good the wall etc |  |  |  | 0 | 0
|  | 20mm nominal outer dia .Pipes. (10kg/cm2) | 20 | RM | 220 |  | 4400
|  | 32mm nominal outer dia .Pipes. (10kg/cm2) | 20 | RM | 236 |  | 4720
53 | LMR | Providing and fixing PVC soil, waste and vent pipe to IS : 13592 of SWR quality, including all fittings, like EG : Bends, Tees, Elbows, Collars, junction, inspection doors, cowls, offsets, access pipes, jointing with rubber ring / solvent cement by application of leak proof adhesive like FRP paste including cutting holes in walls and floors and making good. Make: Supreme, Finolex, Astral |  |  |  | 0 | 0
|  | 50mm dia (6kg / sq.cm) | 20 | RM | 260.45 |  | 5209
|  | 63mm dia (6kg / sq.cm) | 25 | RM | 306 |  | 7650
|  | 75mm dia (6kg / sq.cm) | 20 | RM | 407 |  | 8140
|  | 110mm dia (6 kg / sq.cm) | 20 | RM | 557 |  | 11140
54 | 18.77 | Cutting holes upto 15 x 15 cm in R.C.C. floors and roofs for passing drain pipe etc. and repairing the hole after insertion of drain pipe etc. with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) including finishing complete. | 1 | Each | 193 | 279.3868 | 279.3868
55 | 12.41.2 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A including jointing with seal ring conforming to IS : 5382 leaving 10 mm gap for thermal expansion.(i) Single socketed pipes. 110 mm diameter | 8 | RM | 231.65 | 335.3365 | 2682.6923
56 | MR | Providing and fixing PVC floor trap self cleansing design with or without vent arm complete including cutting and making good the walls and floors. Make:Supreme,Finolex,Prince etc.., | 2 | Each | 519 |  | 1038
|  | 110mm dia inlet 110mm dia outlet |  |  |  | 0 | 0 | 2
57 | 18.58.2.1 | Providing and fixing PTMT grating of approved quality and colour.:Rectangular type with openable circular lid.150 mm nominal size square 100 mm diameter of the inner hinged round grating | 3 | Each | 220.45 | 319.1234 | 957.3703
58 | LMR | Providing and fixing C.P. brass pillar cock (push type)approved quality conforming to IS standards and weighing not less than 690 gms.: 15 mm nominal bore for wash basins: Make:Jauqar, Hindware, Parryware, crome | 2 | Each | 2706 |  | 5412 | 3 | nos
59 | 26.1 | Providing and supplying aluminium extruded tubular and other aluminium sections as per the architectural drawings and approved shop drawings , the aluminium quality as per grade 6063 T5 or T6 as per BS 1474,including super durable powder coating of 60-80 microns conforming to AAMA 2604 of required colour and shade as approved by the Engineer-in-Charge. ( The item includes cost of material such as cleats, sleeves, screws etc. necessary for fabrication of extruded aluminium frame work. Nothing extra shall be paid on this account). | 65 | Kg | 338.25 | 489.6507 | 31827.2955
60 | LMR | Supplying and fixing semi- unitised structural glazing, framework using black electro- coloured anodized Hindalco sections, coating thickkness of minimum 15 microns, for Transom and mullion Hindalco 8796, cleat joining with 1890 and 2081, securely fixing the basic frame to the masonry using properly designed anchor bolt of Fisher or equivalent make or properly designed wood screw along with required galvanised nuts and bolts. The sub- frame should be Hindalco section 8936 electro- colour anodized black colour.Fixing of 6mm thick saint gobain make "cool-lite" series glass to the sub parabond or equivalent after a minium curing period of 7 days. After necessary curing period, fixing the glass panes using backer rod and non- stain/non- bleeding weather sealent of GE make Silpruf black or equivalent, and all other accessories. Total cost should be inclusive of all materials, transportation to the site,scaffolding, lead/lift to the desired levels and labour charges for erection. | 9.38 | Sqm | 2556.2 | 3700.3551 | 34709.331
|  | Fixed |  |  |  | 0 | 0
62 | LMR | Providing and fixing poly carbonate (multi wall 6mm or nearest size) sheet roofing of approved make and quality fixed with polymer coated J or L hooks, bolts and nuts of required diameter with necessary washers complete including the cost of M.S square tube 50x25mm 16 gauge fixed with MS flat 25x6mm including necessary nuts and bolts to support the roofing,painting witn two or more coatswaithsyntheticenamel paint over a priming coat of Zinchromate primer etc complete. | 6.22 | Sqm | 2785.59 |  | 17326.3698
63 | 10.2 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete: | 70 | Kg | 73.95 | 107.05 | 7493.5014
|  | TOTAL(PART-A) |  |  |  | 0 | #REF!
ELECTRICAL WORKS(PART-B)
LMR ITEMS
1 |  | Surface mounted Indoor,decorative box type fitting, Retro LED cat ref. LTT8-20 with 20W LED Lamp having high efficiency PMMA diffuser giving soft glare free light of Crompton or Equi | 9 | Each | 3278 |  | 29502
2 |  | Recess down lighter DN194B LED15S of Philips/Equi with lamp | 8 | Each | 2904 |  | 23232
3 |  | Supply of Green square down lighter recessed BBS175 1xDLED of Philips or Equi with Lamp | 4 | Each | 1992 |  | 7968
4 |  | Supply of Recess mounted full glow RC170B LED 29S of Philips or Equi with lamp | 8 | Each | 4646 |  | 37168
5 |  | Supply & installation of LED Lamp Non Dimmable 7/9W B22 on existing angle batten | 2 | Each | 545 |  | 1090
6 |  | Supply of Linnet - LCL-10-CDL,Sleek LED mirror light,with high out put diffuser, 2 feet size of Crompton or Equi | 1 | Each | 2091 |  | 2091
7 |  | Supply of Indoor down lighter,recessed mounted LED down lights with the option for fixed/ adjustable and spot options. BBS312 1xDLED of Philips or Equi | 6 | Each | 2788 |  | 16728
8 |  | Supply & Installation of LED strip light for indoor with driver, Beetle cat ref. LST20RGB of crompton or equi of 5 meter length | 6 | set | 3336 |  | 20016
9 |  | Supply of ceiling fan 1050/1200 mm sweep,230V,1Ph, complete with double ball bearing, motor blades, down rods, canopy, capacitor etc complete as required 5 star rating (Crompton Riviera / Usha Maxx Air / Khaitan Newtec) | 8 | Each | 2180 |  | 17440
10 |  | Supply and installation of Decorative Wall fan 400 mm sweep, 230V.1Ph, complete with Openable mesh Cover ,string Operated etc as required. (Crompton WM Wind Flo / Usha Helix high speed / Khaitan Merlin Hi speed) | 6 | Each | 2698 |  | 16188
11 |  | Supply and fitting 250 mm sweep automatic shutter Sleek and stylish design type exhaust fan complete with louvers and cable from ceiling rose / connector to fan. (Usha Crisp Air / Crompton Crossair / Khaitan Vento). | 2 | Each | 1393 |  | 2786
12 |  | S/F PVC holder: Supplying and fixing PVC batten/ angle holder including connection etc. as required. | 2 | Each | 71 |  | 142
13 |  | Supply & fixing INFORMATION OUTLET WITH FACE PLATE (concealed in modular work station raceways /gypboard partitions/ walls-with modular back box), TERMINATION AND TESTING CAT6 A (AMP/PANDUIT/Systimax) | 10 | Each | 760 |  | 7600
14 |  | Supply of Alluminium cable. Supply of the following sizes of Alluminium armoured PVC insulated, XLPE Power cable of 1.1kV grade to site including transporting and stacking charges at work site.. |  |  |  |  | 0
a |  | 4 X 16 sq. mm | 30 | Metre | 315 |  | 9450
b |  | 4 X 10 sq. mm | 15 | Metre | 278 |  | 4170
15 |  | Supplying and drawing of UTP 4 pair CAT -6A LAN cable in existing surface/ recessed PVC conduit as required, AMP/Molex make | 300 | Metre | 77 |  | 23100
16 |  | S&F MCCB in cubicle Pannel: Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required. |  |  |  |  | 0
|  | 63 Amp, 16 KA TP MCCB | 1 | 1 | 6188 | 6188 | 6188
DSR ITEMS
17 |  | Point wiring in PVC conduit, with Modular type switch: Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
a |  | Group B | 5 | Point | 585 | 846.846 | 4234.23
b |  | Group C | 32 | Point | 718 | 1039.3768 | 33260.0576
18 |  | Twin control point wiring in PVC conduit, with modular type switch: Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. | 2 | Point | 770 | 1114.652 | 2229.304 |  |  | 224859
19 |  | Power plug wiring in PVC conduit ( 2x4 sq mm ): Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 1 No 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 50 | Metre | 162 | 234.5112 | 11725.56
20 |  | Circuit Sub main wiring in PVC Conduit: Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required |  |  |  | 0 | 0
| a | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | 60 | Metre | 106 | 153.4456 | 9206.736
| b | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 80 | Metre | 131 | 189.6356 | 15170.848
| c | 4 X 4 sq. mm + 2 X 4 sq. mm earth wire | 25 | Metre | 275 | 398.09 | 9952.25
| d | 4 X 6 sq. mm + 2 X 6 sq. mm earth wire | 25 | Metre | 389 | 563.1164 | 14077.91
|  | RE- WIRING IN PVC CONDUIT |  |  |  | 0 | 0
21 |  | Telephone wiring in existing conduit: Supplying and drawing following pair 0.5 sq mm FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. |  |  |  | 0 | 0
|  | 2 Pair | 50 | Metre | 18 | 26.0568 | 1302.84
|  | PVC CONDUIT, METAL BOXES |  | Metre |  | 0 | 0
22 |  | S/F PVC conduit: Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. |  |  |  | 0 | 0
| a | 20 mm | 100 | Metre | 146 | 211.3496 | 21134.96
| b | 25 mm | 250 | Metre | 152 | 220.0352 | 55008.8
| c | 40 mm | 20 | Metre | 110 | 159.236 | 3184.72
23 |  | S/F Modular type switch/ socket: Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. |  |  |  | 0 | 0
| a | Telephone socket outlet | 2 | Each | 95 | 137.522 | 275.044
24 |  | Supplying and fixing electronic fan regulator: Supplying and fixing stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | 8 | Each | 284 | 411.1184 | 3288.9472
25 |  | S/F Modular type blanking plates: Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | 12 | Each | 23 | 33.2948 | 399.5376
26 |  | S/F Modular boxes, base & cover plate: Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required. |  |  |  | 0 | 0
| a | 1 or 2 Module (75mmX75mm) | 20 | Each | 166 | 240.3016 | 4806.032
27 |  | S/F light plug point modular type accessaries: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). | 16 | Each | 303 | 438.6228 | 7017.9648
28 |  | S/F Power plug point with modular type switch: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 2 | Each | 395 | 571.802 | 1143.604
29 |  | S/F Ceiling rose: Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. | 15 | Each | 43 | 62.2468 | 933.702
30 |  | S/F call bell/buzzer: Supplying and fixing call bell/ buzzer suitable for single phase, 230 volts, complete as required. | 2 | Each | 61 | 88.3036 | 176.6072
31 |  | ITC Fluroscent/LED fitting directly on surface/celing: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | 35 | Each | 91 | 131.7316 | 4610.606
32 |  | ITC Fluroscent fitting with down rod: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc., including supplying and fixing ball and socket arrangement, 2 no. down rods of 20 mm dia X 1.6 mm thick steel conduit upto 30 cm length, painting and wiring the down rods and connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | 8 | Each | 233 | 337.2908 | 2698.3264
33 |  | S/F extra down rod: Providing and fixing extra conduit down rod of 20 mm dia, 2 X 10 cm length wiring with 2 X 1.5 sq. mm FR PVC insulated, copper conductor, single core cable including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | 16 | Each | 31 | 44.8756 | 718.0096
34 |  | ITC Ceiling fan: Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable etc. as required. | 8 | Each | 95 | 137.522 | 1100.176
35 |  | Extra down rod 15 mm dia 20 CM Length: Supplying and fixing extra conduit down rod of 20 cm length G.I. pipe 15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | 24 | Each | 27 | 39.0852 | 938.0448
36 |  | ITC Exhaust fan: Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. |  |  |  | 0 | 0
|  | Upto 450 mm sweep | 2 | Each | 204 | 295.3104 | 590.6208
37 |  | S/F SP MCB DB: Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) |  |  |  | 0 | 0
|  | 2 + 6/8 way, Double door | 2 | Each | 1041 | 1506.9516 | 3013.9032
38 |  | S/F Vertical Type Pre Wired TP MCB DB: Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required ,suitable for MCCB incomer.(But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.) |  |  |  | 0 | 0
| 2.9.5 | 4 way Double door | 1 | Each | 7901 | 11437.4876 | 11437.4876
39 |  | S/F 'C' series, MCB: Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | 0 | 0
a |  | Single pole | 8 | Each | 169 | 244.6444 | 1957.1552
40 |  | S/F S P MCB blanking plate: Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | 10 | Each | 7 | 10.1332 | 101.332
41 |  | S/F DP MCB isolator: Supplying and fixing following rating, double pole, 240 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | 0 | 0
|  | 40 amps | 2 | Each | 218 | 315.5768 | 631.1536
42 |  | S/F SPN RCCB: Supplying and fixing following rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  | Each |  | 0 | 0
|  | 25 amps | 2 | Each | 1645 | 2381.302 | 4762.604
43 |  | S/F 20A SPN MCB industrial socket outlet: Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 2 | Each | 954 | 1381.0104 | 2762.0208
44 |  | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 1 | Each | 141 | 204.1116 | 204.1116
45 |  | G.I Earth Pipe Electrode With Salt & Charcoal: Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 2 | Each | 3926 | 5683.2776 | 11366.5552
46 |  | Providing and fixing 4.00mm dia copper wire on surface or in recess: Providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 60 | metre | 86 | 124.4936 | 7469.616
47 |  | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. |  |  |  | 0 | 0
|  | Upto 35 sq. mm | 35 | metre | 606 | 877.2456 | 30703.596
48 |  | Supplying and making end termination with brass compression gland and aluminium lugs: Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. |  |  |  | 0 | 0
| 9.1.32 | 4 X 10 sq. mm (25mm) | 2 | Each | 193 | 279.3868 | 558.7736
| 9.1.33 | 4 X 16 sq. mm (28mm) | 2 | Each | 245 | 354.662 | 709.324
|  | TOTAL FOR PART-B |  |  |  |  | 509722.0708
|  | GRAND TOTAL(PARTA+PART-B) |  |  |  |  | #REF!

## civil-+ELEab (4) (hidden)
ESTIMATE FOR CIVIL&ELECTRICAL WORKS IN CONFERENCE HALL IN KAKKANADU FACTORY,COCHIN
Item no. | DSR | Item Description | Qty | Unit | Rate | Rate+CI | Amount
CIVIL WORKS(PART-A)
1 | 15.2.2 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge.In cement mortar-Nominal concrete 1:4:8 or leaner mix (i/c equivalent designmix) | 10 | Cum | 550.5 | 796.9038 | 7969.038
2 | 15.3 | Demolishing R.C.C. work manually/ by mechanical means includingstacking of steel bars and disposal of unserviceable material within 50metres lead as per direction of Engineer - in- charge. | 1 | Cum | 1302.3 | 1885.2095 | 1885.2095
3 | 15.5 | Extra for cutting reinforcement bars manually/ by mechanical means inR.C.C. or R.B. work (Payment shall be made on the cross sectional areaof R.C.C. or R.B. work) as per direction of Engineer -in -charge. | 30 | Sqm | 450.45 | 652.0714 | 19562.1426 | 30
4 | 15.23.1 | Dismantling tile work in floors, dadoing and roofs laid in cement mortar including stacking material within 50 metres lead.For thickness of tiles up to 25 mm | 25 | Sqm | 28.2 | 40.8223 | 1020.558
5 | 15.5 | Dismantling of Water closets/wash basin/flushing cistern etc. of all types (C.I./PVC/Vitrious China) including stacking of useful materials near the site and disposal of unserviceable materials | 2 | Each | 519.87 | 752.5638 | 1505.1276 | 2 | Nos
6 | 15.6 | Disposal of building rubbish / malba / similar unserviceable, dismantled or waste materials by mechanical means including loading, transporting, unloading to approved municipal dumping ground or as approved by Engineer-in-charge, beyond 50 m initial lead, for all loads including all lifts involved. | 40 | Cum | 123.7 | 179.0681 | 7162.7248
7 | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30cm in depth. 1.5m in width as well as 10 sqm on plan) including disposal of excavated earth and lift upto 1.5m, disposed earth to be levelled and neatly dressed.:All kinds of soil | 3.375 | Cum | 155.6 | 225.2466 | 760.2071
8 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All works up to plinth level-.1:4:8 (1 Cement : 4 coarse sand : 8 graded stone aggregate 40 mm nominal size) | #REF! | Cum | 4301.2 | 6226.4171 | #REF!
9 | 5.37 | Providing and laying in position ready mixed M-25 grade concrete for reinforced cement concrete work, using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , excluding the cost of centering, shuttering finishing and reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, improve workability without impairing strength and durability as per direction of the Engineer - in - charge. |  |  |  | 0 | 0 | 0
|  | (Note :- Cement content considered in this item is @ 330 kg/cum. Excess/less cement used as per design mix is payable/recoverable separately). |  |  |  | 0 | 0 | 0
| 5.37.2 | All work above plinth level up to floor V level -RCC work (M25 concrete) | 22.3373 | Cum | 7363 | 10658.6788 | 238085.605 | #VALUE!
10 | 5.9 | Centering and shuttering including strutting, propping etc., and removal of form for, |  |  |  | 0 | 0 | 0
10.a | 5.9.1 | Foundations, Footings, bases of columns,etc for mass concrete. | 2.25 | Sqm | 196.45 | 284.381 | 639.8573
10.a | 5.9.6 | Columns and Pillars, Piers, Abutments, Posts and Struts. | 64 | Sqm | 453.35 | 656.2695 | 42001.2454
10.b | 5.9.3 | Suspended floors, roofs, landings, Balconies and access platform | 103 | Sqm | 453.35 | 656.2695 | 67595.7544
10.c | 5.9.5 | Lintel,beams,plinth beams,girders,bressumers and cantilevers | 74 | Sqm | 332.15 | 480.8203 | 35580.7052
10.d | 5.9.19 | Weather shade, Chajjas, corbels etc., including edges | 15 | Sqm | 492.35 | 712.7259 | 10690.8879
11 | 5.22.A.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending,placing in position and binding all complete above plinth level. :Thermo-Mechanically Treated bars | 2203.5283 | Kg | 68.1 | 98.5816 | 217227.2593
12 | 6.4.2 | Brick work with F.P.S bricks of class designation 5.0 in superstructure above plinth level up to floor v level in all shapes an sizes in: Cement mortar 1: 6 (1 cement :6 coarse sand) | 24.1605 | Cum | 5426.15 | 7854.8947 | 189778.4679
13 | 6.13.1 | Half brick masonry with F.P.S brick of class designation 7.5 in superstructure above plinth level up to floor V level : CM 1:3 (1 cement : 3 coarse sand) | 28.88 | Sqm | 692.8 | 1002.8973 | 28963.6734
14 | 6.15 | Extra for providing and placing in position 2 Nos. 6mm dia M.S bars at every third course of half brick masonry (with FPS brick) | 28.88 | Sqm | 69.5 | 100.6082 | 2905.5648
15 | 13.2.1 | 15mm cement plaster on the rough side of single or half brick wall of mix : 1 : 4 (1 cement : 4 fine sand) up to 10m height for external walls | 74 | Sqm | 189.4 | 274.1754 | 20288.9826
16 | 13.1.1 | 12mm cement plaster on the rough side of single or half brick wall of mix : 1 : 4 (1 cement : 4 fine sand) for internal walls, column and beams etc | 305.1168 | Sqm | 163.35 | 236.4655 | 72149.5845
17 | 13.16.1 | 6 mm cement plaster of mix : 1:3 (1 cement: 3 fine sand) for ceiling plastering | 93.1392 | Sqm | 134.7 | 194.9917 | 18161.3728
18 | 13.8 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. | 398.256 | Sqm | 89.65 | 129.7773 | 51684.6043
19 | 13.60.1 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade –Two or more coats on new work.-internal walls | 398.256 | Sqm | 80.5 | 116.5318 | 46409.4885
20 | 13.48.1 | Finishing walls with Acrylic Smooth exterior paint of required shade : New work (Two or more coat applied @ 1.67 ltr/10 sqmover and including priming coat of exterior primer applied @ 2.20 kg/ 10 sqm) | 74 | Sqm | 100 | 144.76 | 10712.24
21 | 13.48.3 | Painting Steel work with Delux Multi surface paint to give an even shade.Two or more coat applied @ 0.90 ltr/10sqm over an over an under coat of primer applied @ 0.80ltr/10aqm of approved brand or manufacture. | 3.315 | Sqm | 90 | 130.284 | 431.8915
22 | 8.2.2.2 | Providing and fixing 18mm thick gang saw cut mirror polished premoulded and prepolished) machine cut for kitchen platforms, vanity counters, window sills , facias and similar locations of required size of approved shade, colour and texture laid over 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels. Granite of any colour and shade: Area of slab over 0.50 sqm.: Lowest retail price not less than Rs. 2500.00/m2( Granite to be selected by the Engineer in charge) | 0.9 | Sqm | 2463.55 | 3566.235 | 3209.6115
23 | 9.117.1 | Providing and fixing factory made UPVC door frame made of UPVC extruded section having an overall dimensions as below ( tolerance ± 1mm ), with wall thickness 2.0mm (± 0.2mm), corners of the door frame to be joined with galvanized brackets and stainless steel screws, joints mitered and plastic welded. The hinged side vertical of the frames reinforced by galvanized M.S. tube of size 19x19 mm and 1mm (± 0.1mm) wall thickness and 3 nos. Stainless steel hinged fixed to the frame complete as per manufacturers Specification and direction of engineering -in-change : Extruded section profile size 48x40 mm | 6.72 | M | 213.75 | 309.4245 | 2079.3326
24 | 9.118.1 | Providing and fixing existing door frames: 24 mm thick factory made PVC door shutters made of styles and rails of a UPVC hollow section of size 59x24 mm and wall thickness 2 mm (± 0.2mm) with in built edging on both sides. The styles and rails mitered and joint at the corners by means of M.S. galvanized / plastic brackets of size 75x220 mm having wall thickness 1.0 mm and stainless steel screws. The styles of the shutter reinforced by inserting galvanized M.S. tube of size 20x20 mm and 1mm (± 0.1mm) wall thickness. The lock rail made up of " H" section, a UPVC hollow section of size 100x24 mm and 2mm (± 0.2mm) wall thickness, fixed to the shutters styles by means of plastic/ galvanized M.S.'U' cleats. The shutter frame filled with a UPVC multi chambered single panel of size not less than 620mm, having over all thickness of 20mm and 1mm (± 0.1mm) wall thickness. The panes filled vertically and tie bar at two places by inserting horizontally 6mm galvanized M.S. rod and fastened with nuts and washers, complete as per manufacturer's specification and direction of Engineer- in - charge. (for W,C and bath room door shutter). | 6.72 | Sqm | 2718.6 | 3935.4454 | 26446.1928
25 | 11.41.2 | Providing and laying polished vitrified floor tile in different sizes (thickness to be specified by the manufacturer) with Acid and / or Alkali resistant tiles with water absorptions less than 0.08% and confirming to IS:15622 of approved make in all colours and shades, laid on 20mm thick cement mortor 1:4 (1 cement:4 Coard sand) including grouting the joints with white cement and matching pigments etc. complete. (Lowest retail price not less than Rs. 880/m2) : Size of Tiles 60 x 60 cm (Tiles to be selected by the Engineer in charge) | 68.9249 | sqm | 1405.95 | 2035.2532 | 140279.6247
26 | 11.39 | Providing and laying rectified Glazed Ceramic floor tiles 300x300 mm or more (thickness to be specified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make in colours White, Ivory, Grey, Fume Red Brown, laid on 20mm thick cement mortar 1:4 (1 Cement : 4 Coarse sand) including grouting the joints with white cement and matching pigments etc., complete. | 6.4904 | sqm | 950.05 | 1375.2924 | 8926.1977
27 | 11.4 | Providing and fixing Ist quality ceramic glazed wall tiles of size 300x450mm conforming to IS : 15622 (thickness to be specified by the manufacturer ) of approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados over 12 mm thick bed of cement Mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm including pointing in white cement mixed with pigment of matching shade complete. | 25 | sqm | 1009.6 | 1461.497 | 36537.424
28 | 12.45 | Providing and fixing false ceiling at all height including providing and fixingof frame work made of special sections, power pressed from M.S. sheets and galvanized with zinc coating of 120 gms/sqm (both side inclusive) asper IS : 277 and consisting of angle cleats of size 25 mm wide x 1.6 mmthick with flanges of 27 mm and 37mm, at 1200 mm centre to centre, oneflange fixed to the ceiling with dash fastener 12.5 mm dia x 50mm long with6mm dia bolts, other flange of cleat fixed to the angle hangers of 25x10x0.50mm of required length with nuts & bolts of required size and other end ofangle hanger fixed with intermediate G.I. channels 45x15x0.9 mm runningat the spacing of 1200 mm centre to centre, to which the ceiling section0.5 mm thick bottom wedge of 80 mm with tapered flanges of 26 mm eachhaving lips of 10.5 mm, at 450 mm centre to centre, shall be fixed in adirection perpendicular to G.I. intermediate channel with connecting clipsmade out of 2.64 mm dia x 230 mm long G.I. wire at every junction, includingfixing perimeter channels 0.5 mm thick 27 mm high having flanges of 20 mm and 30 mm long, the perimeter of ceiling fixed to wall/partition with the help of rawl plugs at 450 mm centre, with 25mm long dry wall screws @230 mm interval, including fixing of gypsum board to ceiling section andperimeter channel with the help of dry wall screws of size 3.5 x 25 mm at230 mm c/c, including jointing and finishing to a flush finish of tapered andsquare edges of the board with recomme-nded jointing compound , jointingtapes , finishing with jointing compound in 3 layers covering upto 150 mmon both sides of joint and two coats of primer suitable for board, all as permanufacturer’s specification and also including the cost of making openingsfor light fittings, grills, diffusers, cutouts made with frame of perimeterchannels suitably fixed, all complete as per drawings, specification anddirection of the Engineer in Charge but excluding the cost of painting with |  |  |  | 0 | 0
| 12.45.1 | 12.5 mm thick tapered edge gypsum plain board conformingto IS: 2095- Part I | 48.1626 | sqm | 907.1 | 1313.118 | 63243.1751 | #VALUE! | sqm
29 | 21.1.1.2 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) : For fixed portion: Powder coated aluminium (minimum thickness of powder coating 50 micron) | 115.83 | kg | 377.75 | 546.8309 | 63339.4231
30 | 21.1.2.2 | For shutters of doors, windows & ventilators including providing and fixing hinges/ pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately). Powder coated aluminium (minimum thickness of powder coating 50 micron) | 75.6 | Kg | 435.75 | 630.7917 | 47687.8525
31 | 21.3.2 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.5 mm thickness | 15.12 | sqm | 1054.2 | 1526.0599 | 23074.026
32 | 21.8 | Filling the gap in between aluminium frame & adjacent RCC/Brick/Stone work by providing weather silicon sealant over backer rod of approved quality as per architectural drawings and direction of Enginner-in-charge complete. |  |  |  | 0 | 0
| 21.8.1 | Upto 5mm depth and 5mm width | 10 | Rm | 88.75 | 128.4745 | 1284.745
33 | 21.18 | Providing and fixing 12 mm thick frameless toughened glass door shutter of approved brand and manufacture, including providing and fixing top & bottom pivot & spring type fixing arrangement and making necessary holes etc. for fixing required door fitings, all complete as per direction of Engineer-in-charge ( Door handle, lock and stopper etc. to be paid separately) | 2.7 | Sqm | 4746.3 | 6870.7439 | 18551.0085
35 | 9.83 | Providing and fixing aluminium die cast body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 35 kg and door width upto 700 mm) with necessary accessories and screws etc. complete. | 2 | Each | 753.75 | 1091.1285 | 2182.257
36 | 9.97 | Providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade with necessary screws etc., complete. |  |  |  | 0 | 0
| 9.97.2 | 250 x 10mm | 8 | Each | 95.25 | 137.8839 | 1103.0712
| 9.97.4 | 150 x 10mm | 8 | Each | 65.35 | 94.6007 | 756.8053
37 | 21.13 | Providing and fixing 100mm brass locks (best make of approved quality) for aluminum doors including necessary cutting and making good etc. complete | 8 | Each | 418.65 | 606.0377 | 4848.3019
38 | 21.12.2 | Providing and fixing aluminium tubular handle bar 32 mm outer dia, 3.0 mm thick & 2100 mm long with SS screws etc .complete as per direction of Engineer-in-Charge. Powder coated minimum thickness 50 micron aluminium tubular handle bar. | 8 | Each | 508.55 | 736.177 | 5889.4158
39 | 9.101 | Providing and fixing aluminium hanging floor door stopper ISI marked anodised (anodic coating note less than grade AC 10 as per IS : 1868) transparent or dyed to required colour and shade with necessary screws etc., complete. |  |  |  | 0 | 0
| 9.101.1 | Single rubber stopper | 3 | Each | 37.5 | 54.285 | 162.855
40 | 21.4 | Providing and fixing double action hydraulic floor spring of approved brand and manufacture IS : 6315 marked, for doors including cost of cutting floors as required, embedding in floors and cover plates with brass pivot and single piect M.S. sheet outer box with side plate etc., complete as per the direction of Engineer-in-charge. |  |  |  | 0 | 0
| 21.4.2 | With brass cover plate | 1 | Each | 2213.2 | 3203.8283 | 3203.8283
41 | 9.149 | Providing and fixing casement handle made of zinc alloyed (white powder coated) for uPVC casement window with necessary screws etc. complete. | 4 | Each | 216.65 | 313.6225 | 1254.4902
42 | 9.68.1 | Providing and fixing oxidised M.S. casement stays (straight peg type) with necessary screws etc. Complete-300 mm weighing not less than 200 gms | 8 | Each | 36.2 | 52.4031 | 419.225
43 | 17.3.1 | Providing and fixing white vitreous china pedestal type water closet (European type) with seat and lid, 10 litre low level white vitreous china flushing cistern & C.P. flush bend with fittings & C.I.brackets, 40mm flush bend, overflow arrangement with specials of standard make and mosquito proof coupling of approved municipal design complete including painting of fittings and brackets, cutting and making good the walls and floors wherever required : W.C. pan with ISI marked white solid plastic seat and lid.(Make: Hindware, Jaquar, Parryware) | 2 | Each | 4784.6 | 6926.187 | 13852.3739
44 | 17.7.1 | Providing and fixing wash basin/counter wash basin with C.I. brackets, 15 mm C.P. brass pillar taps,32 mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever require White Vitreous China Wash basin size 630x450 mm with a pair of 15 mm C.P. brass pillar taps. (Make: Hindware, Jaquar, Parryware) | 2 | Each | 2331.15 | 3374.5727 | 6749.1455
46 | 17.28.1.1 | Providing and fixing PVC Waste pipe for sink or wash basin including PVC waste fittings complete.:Semi rigid pipe 32mm dia | 2 | Each | 76.75 | 111.1033 | 222.2066 | 2 | nos
47 | 17.34.1 | Providing and fixing Toilet paper holder . Make:Hindware,Cera,Jaquar etc..,:C.P Brass | 1 | Each | 415.9 | 602.0568 | 602.0568 | 2 | nos
48 | 18.65 | Providing and fixing SS soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements. Weighing not less than 106 gms. | 1 | Each | 164.95 | 238.7816 | 238.7816 | 3 | nos
49 | 17.31 | Providing and fixing 600 x 450mm bevelled edge mirror of superior glass (of approved quality) complete with 6mm thick hard board ground fixed to wooden cleats with C.P. brass screws and washers complete. | 1 | Each | 793.95 | 1149.322 | 1149.322 | 1 | nos
50 | 17.73.2 | Providing and fixing SS towel rail complete with brackets fixed to wooden cleats with CP brass screws with concealed fitting arrangement of approved quality and colour. 600mm long towel rail with total length of 645mm, width 78mm and effective height of 88mm, weighing not less than 190gms. | 1 | Each | 541.5 | 783.8754 | 783.8754 | 3 | nos
54 | 18.77 | Cutting holes upto 15 x 15 cm in R.C.C. floors and roofs for passing drain pipe etc. and repairing the hole after insertion of drain pipe etc. with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) including finishing complete. | 1 | Each | 193 | 279.3868 | 279.3868
55 | 12.41.2 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A including jointing with seal ring conforming to IS : 5382 leaving 10 mm gap for thermal expansion.(i) Single socketed pipes. 110 mm diameter | 8 | RM | 231.65 | 335.3365 | 1853.2
|  | 110mm dia inlet 110mm dia outlet |  |  |  | 0 | 0 | 2
57 | 18.58.2.1 | Providing and fixing PTMT grating of approved quality and colour.:Rectangular type with openable circular lid.150 mm nominal size square 100 mm diameter of the inner hinged round grating | 3 | Each | 220.45 | 319.1234 | 661.35
58 | LMR | Providing and fixing C.P. brass pillar cock (push type)approved quality conforming to IS standards and weighing not less than 690 gms.: 15 mm nominal bore for wash basins: Make:Jauqar, Hindware, Parryware, crome | 2 | Each | 2706 |  | 5412 | 3 | nos
59 | 26.1 | Providing and supplying aluminium extruded tubular and other aluminium sections as per the architectural drawings and approved shop drawings , the aluminium quality as per grade 6063 T5 or T6 as per BS 1474,including super durable powder coating of 60-80 microns conforming to AAMA 2604 of required colour and shade as approved by the Engineer-in-Charge. ( The item includes cost of material such as cleats, sleeves, screws etc. necessary for fabrication of extruded aluminium frame work. Nothing extra shall be paid on this account). | 65 | Kg | 338.25 | 489.6507 | 21986.25
60 | 26.2 | Designing, fabricating, testing, protection, installing and fixing in positionsemi (grid) unitized system of structural glazing (with open joints) for linearas well as curvilinear portions of the building for all heights and all levels,including:a) Structural analysis & design and preparation of shop drawings for thespecified design loads conforming to IS 875 part III (the system mustpassed the proof test at 1.5 times design wind pressure without anyfailure), including functional design of the aluminum sections for fixing glazing panels of various thicknesses, aluminium cleats, sleeves and c) Providing and filling, two part pump filled, structural silicone sealant and one part weather silicone sealant compatible with the structuralsilicone sealant of required bite size in a clean and controlled factory /work shop environment , including double sided spacer tape, setting blocks and backer rod, all of approved grade, brand and manufacture,as per the approved sealant design, within and all around the perimeterd) Providing and fixing in position flashings of solid aluminium sheet mm thick and of sizes, shapes and profiles, as required as per the site conditions, to seal the gap between the building structure and all its interfaces with curtain glazing to make it watertighte) Making provision for drainage of moisture/ water that enters the curtainglazing system to make it watertight, by incorporating principles of required), making necessary holes of required sizes and of requirednumbers etc. complete. This item includes cost of all inputs ofsplice plates etc. gaskets, screws, toggles, nuts, bolts, clamps etc., structural and weather silicone sealants, flashings, fire stop (barrier)-cum-smoke seals, microwave cured EPDM gaskets for water tightness, pressure equalisation & drainage and protection against fire hazardincluding:b) Fabricating and supplying serrated M.S. hot dip galvanised / Aluminiumalloy of 6005 T5 brackets of required sizes, sections and profiles etc.to accommodate 3 Dimentional movement for achieving perfectverticality and fixing structural glazing system rigidly to theRCC/masonry/structural steel framework of building structure using stainless steel anchor fasteners/ bolts, nylon seperator to prevent bimetallic contacts with nuts and washers etc. of stainless steel grade 316, of the required capacity and in required numbers | #REF! | Sqm | 2556.2 | 3700.3551 | #REF!
|  | installation of glazed units, T&P, scaffolding and other incidental charges including wastages etc., enabling temporary structures and services, cranes or cradles etc. as described above and as specified. The item includes the cost of getting all the structural and functional design including shop drawings checked by a structural designer, dully approved by Engineer-in-charge. The item also includes the cost of all mock ups at site, cost of all samples of the individual components for testing in an approved laboratory, field tests on the assembled working structural glazing as specified, cleaning and protection till the handing over of the building for occupation. In the end, the Contractor shall provide a water tight structural glazing having all the performance characteristics etc. all complete as required, as per the Architectural drawings, as per item description, as specified, as per the approved shop drawings and as directed by the Engineerin-Charge. |  |  |  | 0 | 0
|  | Note:- 1. The cost of providing extruded aluminium frames, shadow boxes, extruded aluminium section capping for fixing in the grooves of the curtain glazing and vermin proof stainless steel wire mesh shall be paid for separately under relevant items under this subhead. However, for the purpose of payment, only the actual area of structural glazing (including width of grooves ) on the external face shall be measured in sqm. up to two decimal places. Note:-2. The following performance test are to be conducted on structural glazing system if area of structural glazing exceeds 2500 Sqm from the certified laboratories accreditated by NABL(National Accreditation Board for Testing and Calibration Laboratories), Department of Science & Technologies, India. Cost of testing is payable separately. The NIT approving authority will decide the necessity of testing on the basis of cost of the work, cost of the test and importance of the work. Performance Testing of Structural glazing system Tests to be conducted in the NBL Certified laboratories |  |  |  | 0 | 0
61 | 26.3 | Providing, assembling and supplying vision glass panels (IGUs) comprising of hermetically-sealed 6-12- 6 mm insulated glass (double glazed) vision panel units of size and shape as required and specified, comprising of an outer heat strengthened float glass 6mm thick, of approved colour and shade with reflective soft coating on surface # 2 of approved colour and shade, an inner Heat strengthned clear float glass 6mm thick, spacer tube | #REF! | Sqm | 4091 | 5922.1316 | #REF!
62 | LMR | Providing and fixing poly carbonate (multi wall 6mm or nearest size) sheet roofing of approved make and quality fixed with polymer coated J or L hooks, bolts and nuts of required diameter with necessary washers complete including the cost of M.S square tube 50x25mm 16 gauge fixed with MS flat 25x6mm including necessary nuts and bolts to support the roofing,painting witn two or more coatswaithsyntheticenamel paint over a priming coat of Zinchromate primer etc complete. | 6.22 | Sqm | 2785.59 |  | 17326.3698
63 | 10.2 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete: | 70 | Kg | 73.95 | 107.05 | 5176.5
|  | TOTAL(PART-A) |  |  |  | 0 | #REF!
ELECTRICAL WORKS(PART-B)
LMR ITEMS
1 |  | Surface mounted Indoor,decorative box type fitting, Retro LED cat ref. LTT8-20 with 20W LED Lamp having high efficiency PMMA diffuser giving soft glare free light of Crompton or Equi | 9 | Each | 3278 |  | 29502
2 |  | Recess down lighter DN194B LED15S of Philips/Equi with lamp | 8 | Each | 2904 |  | 23232
3 |  | Supply of Green square down lighter recessed BBS175 1xDLED of Philips or Equi with Lamp | 4 | Each | 1992 |  | 7968
4 |  | Supply of Recess mounted full glow RC170B LED 29S of Philips or Equi with lamp | 8 | Each | 4646 |  | 37168
5 |  | Supply & installation of LED Lamp Non Dimmable 7/9W B22 on existing angle batten | 2 | Each | 545 |  | 1090
6 |  | Supply of Linnet - LCL-10-CDL,Sleek LED mirror light,with high out put diffuser, 2 feet size of Crompton or Equi | 1 | Each | 2091 |  | 2091
7 |  | Supply of Indoor down lighter,recessed mounted LED down lights with the option for fixed/ adjustable and spot options. BBS312 1xDLED of Philips or Equi | 6 | Each | 2788 |  | 16728
8 |  | Supply & Installation of LED strip light for indoor with driver, Beetle cat ref. LST20RGB of crompton or equi of 5 meter length | 6 | set | 3336 |  | 20016
9 |  | Supply of ceiling fan 1050/1200 mm sweep,230V,1Ph, complete with double ball bearing, motor blades, down rods, canopy, capacitor etc complete as required 5 star rating (Crompton Riviera / Usha Maxx Air / Khaitan Newtec) | 8 | Each | 2180 |  | 17440
10 |  | Supply and installation of Decorative Wall fan 400 mm sweep, 230V.1Ph, complete with Openable mesh Cover ,string Operated etc as required. (Crompton WM Wind Flo / Usha Helix high speed / Khaitan Merlin Hi speed) | 6 | Each | 2698 |  | 16188
11 |  | Supply and fitting 250 mm sweep automatic shutter Sleek and stylish design type exhaust fan complete with louvers and cable from ceiling rose / connector to fan. (Usha Crisp Air / Crompton Crossair / Khaitan Vento). | 2 | Each | 1393 |  | 2786
12 |  | S/F PVC holder: Supplying and fixing PVC batten/ angle holder including connection etc. as required. | 2 | Each | 71 |  | 142
13 |  | Supply & fixing INFORMATION OUTLET WITH FACE PLATE (concealed in modular work station raceways /gypboard partitions/ walls-with modular back box), TERMINATION AND TESTING CAT6 A (AMP/PANDUIT/Systimax) | 10 | Each | 760 |  | 7600
14 |  | Supply of Alluminium cable. Supply of the following sizes of Alluminium armoured PVC insulated, XLPE Power cable of 1.1kV grade to site including transporting and stacking charges at work site.. |  |  |  |  | 0
a |  | 4 X 16 sq. mm | 30 | Metre | 315 |  | 9450
b |  | 4 X 10 sq. mm | 15 | Metre | 278 |  | 4170
15 |  | Supplying and drawing of UTP 4 pair CAT -6A LAN cable in existing surface/ recessed PVC conduit as required, AMP/Molex make | 300 | Metre | 77 |  | 23100
16 |  | S&F MCCB in cubicle Pannel: Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required. |  |  |  |  | 0
|  | 63 Amp, 16 KA TP MCCB | 1 | 1 | 6188 | 6188 | 6188
DSR ITEMS
17 |  | Point wiring in PVC conduit, with Modular type switch: Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
a |  | Group B | 5 | Point | 585 | 846.846 | 4234.23
b |  | Group C | 32 | Point | 718 | 1039.3768 | 33260.0576
18 |  | Twin control point wiring in PVC conduit, with modular type switch: Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. | 2 | Point | 770 | 1114.652 | 2229.304 |  |  | 224859
19 |  | Power plug wiring in PVC conduit ( 2x4 sq mm ): Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 1 No 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 50 | Metre | 162 | 234.5112 | 11725.56
20 |  | Circuit Sub main wiring in PVC Conduit: Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required |  |  |  | 0 | 0
| a | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | 60 | Metre | 106 | 153.4456 | 9206.736
| b | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 80 | Metre | 131 | 189.6356 | 15170.848
| c | 4 X 4 sq. mm + 2 X 4 sq. mm earth wire | 25 | Metre | 275 | 398.09 | 9952.25
| d | 4 X 6 sq. mm + 2 X 6 sq. mm earth wire | 25 | Metre | 389 | 563.1164 | 14077.91
|  | RE- WIRING IN PVC CONDUIT |  |  |  | 0 | 0
21 |  | Telephone wiring in existing conduit: Supplying and drawing following pair 0.5 sq mm FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. |  |  |  | 0 | 0
|  | 2 Pair | 50 | Metre | 18 | 26.0568 | 1302.84
|  | PVC CONDUIT, METAL BOXES |  | Metre |  | 0 | 0
22 |  | S/F PVC conduit: Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. |  |  |  | 0 | 0
| a | 20 mm | 100 | Metre | 146 | 211.3496 | 21134.96
| b | 25 mm | 250 | Metre | 152 | 220.0352 | 55008.8
| c | 40 mm | 20 | Metre | 110 | 159.236 | 3184.72
23 |  | S/F Modular type switch/ socket: Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. |  |  |  | 0 | 0
| a | Telephone socket outlet | 2 | Each | 95 | 137.522 | 275.044
24 |  | Supplying and fixing electronic fan regulator: Supplying and fixing stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | 8 | Each | 284 | 411.1184 | 3288.9472
25 |  | S/F Modular type blanking plates: Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | 12 | Each | 23 | 33.2948 | 399.5376
26 |  | S/F Modular boxes, base & cover plate: Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required. |  |  |  | 0 | 0
| a | 1 or 2 Module (75mmX75mm) | 20 | Each | 166 | 240.3016 | 4806.032
27 |  | S/F light plug point modular type accessaries: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). | 16 | Each | 303 | 438.6228 | 7017.9648
28 |  | S/F Power plug point with modular type switch: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 2 | Each | 395 | 571.802 | 1143.604
29 |  | S/F Ceiling rose: Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. | 15 | Each | 43 | 62.2468 | 933.702
30 |  | S/F call bell/buzzer: Supplying and fixing call bell/ buzzer suitable for single phase, 230 volts, complete as required. | 2 | Each | 61 | 88.3036 | 176.6072
31 |  | ITC Fluroscent/LED fitting directly on surface/celing: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | 35 | Each | 91 | 131.7316 | 4610.606
32 |  | ITC Fluroscent fitting with down rod: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc., including supplying and fixing ball and socket arrangement, 2 no. down rods of 20 mm dia X 1.6 mm thick steel conduit upto 30 cm length, painting and wiring the down rods and connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | 8 | Each | 233 | 337.2908 | 2698.3264
33 |  | S/F extra down rod: Providing and fixing extra conduit down rod of 20 mm dia, 2 X 10 cm length wiring with 2 X 1.5 sq. mm FR PVC insulated, copper conductor, single core cable including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | 16 | Each | 31 | 44.8756 | 718.0096
34 |  | ITC Ceiling fan: Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable etc. as required. | 8 | Each | 95 | 137.522 | 1100.176
35 |  | Extra down rod 15 mm dia 20 CM Length: Supplying and fixing extra conduit down rod of 20 cm length G.I. pipe 15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | 24 | Each | 27 | 39.0852 | 938.0448
36 |  | ITC Exhaust fan: Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. |  |  |  | 0 | 0
|  | Upto 450 mm sweep | 2 | Each | 204 | 295.3104 | 590.6208
37 |  | S/F SP MCB DB: Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) |  |  |  | 0 | 0
|  | 2 + 6/8 way, Double door | 2 | Each | 1041 | 1506.9516 | 3013.9032
38 |  | S/F Vertical Type Pre Wired TP MCB DB: Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required ,suitable for MCCB incomer.(But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.) |  |  |  | 0 | 0
| 2.9.5 | 4 way Double door | 1 | Each | 7901 | 11437.4876 | 11437.4876
39 |  | S/F 'C' series, MCB: Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | 0 | 0
a |  | Single pole | 8 | Each | 169 | 244.6444 | 1957.1552
40 |  | S/F S P MCB blanking plate: Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | 10 | Each | 7 | 10.1332 | 101.332
41 |  | S/F DP MCB isolator: Supplying and fixing following rating, double pole, 240 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | 0 | 0
|  | 40 amps | 2 | Each | 218 | 315.5768 | 631.1536
42 |  | S/F SPN RCCB: Supplying and fixing following rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  | Each |  | 0 | 0
|  | 25 amps | 2 | Each | 1645 | 2381.302 | 4762.604
43 |  | S/F 20A SPN MCB industrial socket outlet: Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 2 | Each | 954 | 1381.0104 | 2762.0208
44 |  | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 1 | Each | 141 | 204.1116 | 204.1116
45 |  | G.I Earth Pipe Electrode With Salt & Charcoal: Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 2 | Each | 3926 | 5683.2776 | 11366.5552
46 |  | Providing and fixing 4.00mm dia copper wire on surface or in recess: Providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 60 | metre | 86 | 124.4936 | 7469.616
47 |  | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. |  |  |  | 0 | 0
|  | Upto 35 sq. mm | 35 | metre | 606 | 877.2456 | 30703.596
48 |  | Supplying and making end termination with brass compression gland and aluminium lugs: Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. |  |  |  | 0 | 0
| 9.1.32 | 4 X 10 sq. mm (25mm) | 2 | Each | 193 | 279.3868 | 558.7736
| 9.1.33 | 4 X 16 sq. mm (28mm) | 2 | Each | 245 | 354.662 | 709.324
|  | TOTAL FOR PART-B |  |  |  |  | 509722.0708
|  | GRAND TOTAL(PARTA+PART-B) |  |  |  |  | #REF!

## civil-+ELEab (3) (hidden)
ESTIMATE FOR CIVIL&ELECTRICAL WORKS IN CONFERENCE HALL IN KAKKANADU FACTORY,COCHIN
Item no. | DSR | Item Description | Qty | Unit | Rate | Rate+CI | Amount
CIVIL WORKS(PART-A)
1 | 15.2.2 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge.In cement mortar-Nominal concrete 1:4:8 or leaner mix (i/c equivalent designmix) | 10 | Cum | 550.5 | 796.9038 | 5505
2 | 15.3 | Demolishing R.C.C. work manually/ by mechanical means includingstacking of steel bars and disposal of unserviceable material within 50metres lead as per direction of Engineer - in- charge. | 1 | Cum | 1302.3 | 1885.2095 | 1302.3
3 | 15.5 | Extra for cutting reinforcement bars manually/ by mechanical means inR.C.C. or R.B. work (Payment shall be made on the cross sectional areaof R.C.C. or R.B. work) as per direction of Engineer -in -charge. | 30 | Sqm | 450.45 | 652.0714 | 13513.5 | 30
4 | 15.23.1 | Dismantling tile work in floors, dadoing and roofs laid in cement mortar including stacking material within 50 metres lead.For thickness of tiles up to 25 mm | 25 | Sqm | 28.2 | 40.8223 | 705
5 | 15.5 | Dismantling of Water closets/wash basin/flushing cistern etc. of all types (C.I./PVC/Vitrious China) including stacking of useful materials near the site and disposal of unserviceable materials | 2 | Each | 519.87 | 752.5638 | 1039.74 | 2 | Nos
6 | 15.6 | Disposal of building rubbish / malba / similar unserviceable, dismantled or waste materials by mechanical means including loading, transporting, unloading to approved municipal dumping ground or as approved by Engineer-in-charge, beyond 50 m initial lead, for all loads including all lifts involved. | 40 | Cum | 123.7 | 179.0681 | 4948
7 | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30cm in depth. 1.5m in width as well as 10 sqm on plan) including disposal of excavated earth and lift upto 1.5m, disposed earth to be levelled and neatly dressed.:All kinds of soil | 3.375 | Cum | 155.6 | 225.2466 | 525.15
8 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All works up to plinth level-.1:4:8 (1 Cement : 4 coarse sand : 8 graded stone aggregate 40 mm nominal size) | #REF! | Cum | 4301.2 | 6226.4171 | #REF!
9 | 5.37 | Providing and laying in position ready mixed M-25 grade concrete for reinforced cement concrete work, using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , excluding the cost of centering, shuttering finishing and reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, improve workability without impairing strength and durability as per direction of the Engineer - in - charge. |  |  |  | 0 | 0 | 0
|  | (Note :- Cement content considered in this item is @ 330 kg/cum. Excess/less cement used as per design mix is payable/recoverable separately). |  |  |  | 0 | 0 | 0
| 5.37.2 | All work above plinth level up to floor V level -RCC work (M25 concrete) | 22.3373 | Cum | 7363 | 10658.6788 | 164469.1938 | #VALUE!
10 | 5.9 | Centering and shuttering including strutting, propping etc., and removal of form for, |  |  |  | 0 | 0 | 0
10.a | 5.9.1 | Foundations, Footings, bases of columns,etc for mass concrete. | 2.25 | Sqm | 196.45 | 284.381 | 442.0125
10.a | 5.9.6 | Columns and Pillars, Piers, Abutments, Posts and Struts. | 64 | Sqm | 453.35 | 656.2695 | 29014.4
10.b | 5.9.3 | Suspended floors, roofs, landings, Balconies and access platform | 103 | Sqm | 453.35 | 656.2695 | 46695.05
10.c | 5.9.5 | Lintel,beams,plinth beams,girders,bressumers and cantilevers | 74 | Sqm | 332.15 | 480.8203 | 24579.1
10.d | 5.9.19 | Weather shade, Chajjas, corbels etc., including edges | 15 | Sqm | 492.35 | 712.7259 | 7385.25
11 | 5.22.A.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending,placing in position and binding all complete above plinth level. :Thermo-Mechanically Treated bars | 2203.5283 | Kg | 68.1 | 98.5816 | 150060.2786
12 | 6.4.2 | Brick work with F.P.S bricks of class designation 5.0 in superstructure above plinth level up to floor v level in all shapes an sizes in: Cement mortar 1: 6 (1 cement :6 coarse sand) | 24.1605 | Cum | 5426.15 | 7854.8947 | 131098.693
13 | 6.13.1 | Half brick masonry with F.P.S brick of class designation 7.5 in superstructure above plinth level up to floor V level : CM 1:3 (1 cement : 3 coarse sand) | 28.88 | Sqm | 692.8 | 1002.8973 | 20008.064
14 | 6.15 | Extra for providing and placing in position 2 Nos. 6mm dia M.S bars at every third course of half brick masonry (with FPS brick) | 28.88 | Sqm | 69.5 | 100.6082 | 2007.16
15 | 13.2.1 | 15mm cement plaster on the rough side of single or half brick wall of mix : 1 : 4 (1 cement : 4 fine sand) up to 10m height for external walls | 74 | Sqm | 189.4 | 274.1754 | 14015.6
16 | 13.1.1 | 12mm cement plaster on the rough side of single or half brick wall of mix : 1 : 4 (1 cement : 4 fine sand) for internal walls, column and beams etc | 305.1168 | Sqm | 163.35 | 236.4655 | 49840.8293
17 | 13.16.1 | 6 mm cement plaster of mix : 1:3 (1 cement: 3 fine sand) for ceiling plastering | 93.1392 | Sqm | 134.7 | 194.9917 | 12545.8502
18 | 13.8 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. | 398.256 | Sqm | 89.65 | 129.7773 | 35703.6504
19 | 13.60.1 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade –Two or more coats on new work.-internal walls | 398.256 | Sqm | 80.5 | 116.5318 | 32059.608
20 | 13.48.1 | Finishing walls with Acrylic Smooth exterior paint of required shade : New work (Two or more coat applied @ 1.67 ltr/10 sqmover and including priming coat of exterior primer applied @ 2.20 kg/ 10 sqm) | 74 | Sqm | 100 | 144.76 | 7400
21 | 13.48.3 | Painting Steel work with Delux Multi surface paint to give an even shade.Two or more coat applied @ 0.90 ltr/10sqm over an over an under coat of primer applied @ 0.80ltr/10aqm of approved brand or manufacture. | 3.315 | Sqm | 90 | 130.284 | 298.35
22 | 8.2.2.2 | Providing and fixing 18mm thick gang saw cut mirror polished premoulded and prepolished) machine cut for kitchen platforms, vanity counters, window sills , facias and similar locations of required size of approved shade, colour and texture laid over 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels. Granite of any colour and shade: Area of slab over 0.50 sqm.: Lowest retail price not less than Rs. 2500.00/m2( Granite to be selected by the Engineer in charge) | 0.9 | Sqm | 2463.55 | 3566.235 | 2217.195
23 | 9.117.1 | Providing and fixing factory made UPVC door frame made of UPVC extruded section having an overall dimensions as below ( tolerance ± 1mm ), with wall thickness 2.0mm (± 0.2mm), corners of the door frame to be joined with galvanized brackets and stainless steel screws, joints mitered and plastic welded. The hinged side vertical of the frames reinforced by galvanized M.S. tube of size 19x19 mm and 1mm (± 0.1mm) wall thickness and 3 nos. Stainless steel hinged fixed to the frame complete as per manufacturers Specification and direction of engineering -in-change : Extruded section profile size 48x40 mm | 6.72 | M | 213.75 | 309.4245 | 1436.4
24 | 9.118.1 | Providing and fixing existing door frames: 24 mm thick factory made PVC door shutters made of styles and rails of a UPVC hollow section of size 59x24 mm and wall thickness 2 mm (± 0.2mm) with in built edging on both sides. The styles and rails mitered and joint at the corners by means of M.S. galvanized / plastic brackets of size 75x220 mm having wall thickness 1.0 mm and stainless steel screws. The styles of the shutter reinforced by inserting galvanized M.S. tube of size 20x20 mm and 1mm (± 0.1mm) wall thickness. The lock rail made up of " H" section, a UPVC hollow section of size 100x24 mm and 2mm (± 0.2mm) wall thickness, fixed to the shutters styles by means of plastic/ galvanized M.S.'U' cleats. The shutter frame filled with a UPVC multi chambered single panel of size not less than 620mm, having over all thickness of 20mm and 1mm (± 0.1mm) wall thickness. The panes filled vertically and tie bar at two places by inserting horizontally 6mm galvanized M.S. rod and fastened with nuts and washers, complete as per manufacturer's specification and direction of Engineer- in - charge. (for W,C and bath room door shutter). | 6.72 | Sqm | 2718.6 | 3935.4454 | 18268.992
25 | 11.41.2 | Providing and laying polished vitrified floor tile in different sizes (thickness to be specified by the manufacturer) with Acid and / or Alkali resistant tiles with water absorptions less than 0.08% and confirming to IS:15622 of approved make in all colours and shades, laid on 20mm thick cement mortor 1:4 (1 cement:4 Coard sand) including grouting the joints with white cement and matching pigments etc. complete. (Lowest retail price not less than Rs. 880/m2) : Size of Tiles 60 x 60 cm (Tiles to be selected by the Engineer in charge) | 68.9249 | sqm | 1405.95 | 2035.2532 | 96904.9632
26 | 11.39 | Providing and laying rectified Glazed Ceramic floor tiles 300x300 mm or more (thickness to be specified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make in colours White, Ivory, Grey, Fume Red Brown, laid on 20mm thick cement mortar 1:4 (1 Cement : 4 Coarse sand) including grouting the joints with white cement and matching pigments etc., complete. | 6.4904 | sqm | 950.05 | 1375.2924 | 6166.2045
27 | 11.4 | Providing and fixing Ist quality ceramic glazed wall tiles of size 300x450mm conforming to IS : 15622 (thickness to be specified by the manufacturer ) of approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados over 12 mm thick bed of cement Mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm including pointing in white cement mixed with pigment of matching shade complete. | 25 | sqm | 1009.6 | 1461.497 | 25240
28 | 12.45 | Providing and fixing false ceiling at all height including providing and fixingof frame work made of special sections, power pressed from M.S. sheets and galvanized with zinc coating of 120 gms/sqm (both side inclusive) asper IS : 277 and consisting of angle cleats of size 25 mm wide x 1.6 mmthick with flanges of 27 mm and 37mm, at 1200 mm centre to centre, oneflange fixed to the ceiling with dash fastener 12.5 mm dia x 50mm long with6mm dia bolts, other flange of cleat fixed to the angle hangers of 25x10x0.50mm of required length with nuts & bolts of required size and other end ofangle hanger fixed with intermediate G.I. channels 45x15x0.9 mm runningat the spacing of 1200 mm centre to centre, to which the ceiling section0.5 mm thick bottom wedge of 80 mm with tapered flanges of 26 mm eachhaving lips of 10.5 mm, at 450 mm centre to centre, shall be fixed in adirection perpendicular to G.I. intermediate channel with connecting clipsmade out of 2.64 mm dia x 230 mm long G.I. wire at every junction, includingfixing perimeter channels 0.5 mm thick 27 mm high having flanges of 20 mm and 30 mm long, the perimeter of ceiling fixed to wall/partition with the help of rawl plugs at 450 mm centre, with 25mm long dry wall screws @230 mm interval, including fixing of gypsum board to ceiling section andperimeter channel with the help of dry wall screws of size 3.5 x 25 mm at230 mm c/c, including jointing and finishing to a flush finish of tapered andsquare edges of the board with recomme-nded jointing compound , jointingtapes , finishing with jointing compound in 3 layers covering upto 150 mmon both sides of joint and two coats of primer suitable for board, all as permanufacturer’s specification and also including the cost of making openingsfor light fittings, grills, diffusers, cutouts made with frame of perimeterchannels suitably fixed, all complete as per drawings, specification anddirection of the Engineer in Charge but excluding the cost of painting with |  |  |  | 0 | 0
| 12.45.1 | 12.5 mm thick tapered edge gypsum plain board conformingto IS: 2095- Part I | 48.1626 | sqm | 907.1 | 1313.118 | 43688.2945 | #VALUE! | sqm
29 | 21.1.1.2 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) : For fixed portion: Powder coated aluminium (minimum thickness of powder coating 50 micron) | 115.83 | kg | 377.75 | 546.8309 | 43754.7825
30 | 21.1.2.2 | For shutters of doors, windows & ventilators including providing and fixing hinges/ pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately). Powder coated aluminium (minimum thickness of powder coating 50 micron) | 75.6 | Kg | 435.75 | 630.7917 | 32942.7
31 | 21.3.2 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.5 mm thickness | 15.12 | sqm | 1054.2 | 1526.0599 | 15939.504
32 | 21.8 | Filling the gap in between aluminium frame & adjacent RCC/Brick/Stone work by providing weather silicon sealant over backer rod of approved quality as per architectural drawings and direction of Enginner-in-charge complete. |  |  |  | 0 | 0
| 21.8.1 | Upto 5mm depth and 5mm width | 10 | Rm | 88.75 | 128.4745 | 887.5
33 | 21.18 | Providing and fixing 12 mm thick frameless toughened glass door shutter of approved brand and manufacture, including providing and fixing top & bottom pivot & spring type fixing arrangement and making necessary holes etc. for fixing required door fitings, all complete as per direction of Engineer-in-charge ( Door handle, lock and stopper etc. to be paid separately) | 2.7 | Sqm | 4746.3 | 6870.7439 | 12815.01
35 | 9.83 | Providing and fixing aluminium die cast body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 35 kg and door width upto 700 mm) with necessary accessories and screws etc. complete. | 2 | Each | 753.75 | 1091.1285 | 1507.5
36 | 9.97 | Providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade with necessary screws etc., complete. |  |  |  | 0 | 0
| 9.97.2 | 250 x 10mm | 8 | Each | 95.25 | 137.8839 | 762
| 9.97.4 | 150 x 10mm | 8 | Each | 65.35 | 94.6007 | 522.8
37 | 21.13 | Providing and fixing 100mm brass locks (best make of approved quality) for aluminum doors including necessary cutting and making good etc. complete | 8 | Each | 418.65 | 606.0377 | 3349.2
38 | 21.12.2 | Providing and fixing aluminium tubular handle bar 32 mm outer dia, 3.0 mm thick & 2100 mm long with SS screws etc .complete as per direction of Engineer-in-Charge. Powder coated minimum thickness 50 micron aluminium tubular handle bar. | 8 | Each | 508.55 | 736.177 | 4068.4
39 | 9.101 | Providing and fixing aluminium hanging floor door stopper ISI marked anodised (anodic coating note less than grade AC 10 as per IS : 1868) transparent or dyed to required colour and shade with necessary screws etc., complete. |  |  |  | 0 | 0
| 9.101.1 | Single rubber stopper | 3 | Each | 37.5 | 54.285 | 112.5
40 | 21.4 | Providing and fixing double action hydraulic floor spring of approved brand and manufacture IS : 6315 marked, for doors including cost of cutting floors as required, embedding in floors and cover plates with brass pivot and single piect M.S. sheet outer box with side plate etc., complete as per the direction of Engineer-in-charge. |  |  |  | 0 | 0
| 21.4.2 | With brass cover plate | 1 | Each | 2213.2 | 3203.8283 | 2213.2
41 | 9.149 | Providing and fixing casement handle made of zinc alloyed (white powder coated) for uPVC casement window with necessary screws etc. complete. | 4 | Each | 216.65 | 313.6225 | 866.6
42 | 9.68.1 | Providing and fixing oxidised M.S. casement stays (straight peg type) with necessary screws etc. Complete-300 mm weighing not less than 200 gms | 8 | Each | 36.2 | 52.4031 | 289.6
43 | 17.3.1 | Providing and fixing white vitreous china pedestal type water closet (European type) with seat and lid, 10 litre low level white vitreous china flushing cistern & C.P. flush bend with fittings & C.I.brackets, 40mm flush bend, overflow arrangement with specials of standard make and mosquito proof coupling of approved municipal design complete including painting of fittings and brackets, cutting and making good the walls and floors wherever required : W.C. pan with ISI marked white solid plastic seat and lid.(Make: Hindware, Jaquar, Parryware) | 2 | Each | 4784.6 | 6926.187 | 9569.2
44 | 17.7.1 | Providing and fixing wash basin/counter wash basin with C.I. brackets, 15 mm C.P. brass pillar taps,32 mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever require White Vitreous China Wash basin size 630x450 mm with a pair of 15 mm C.P. brass pillar taps. (Make: Hindware, Jaquar, Parryware) | 2 | Each | 2331.15 | 3374.5727 | 4662.3
46 | 17.28.1.1 | Providing and fixing PVC Waste pipe for sink or wash basin including PVC waste fittings complete.:Semi rigid pipe 32mm dia | 2 | Each | 76.75 | 111.1033 | 153.5 | 2 | nos
47 | 17.34.1 | Providing and fixing Toilet paper holder . Make:Hindware,Cera,Jaquar etc..,:C.P Brass | 1 | Each | 415.9 | 602.0568 | 415.9 | 2 | nos
48 | 18.65 | Providing and fixing SS soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements. Weighing not less than 106 gms. | 1 | Each | 164.95 | 238.7816 | 164.95 | 3 | nos
49 | 17.31 | Providing and fixing 600 x 450mm bevelled edge mirror of superior glass (of approved quality) complete with 6mm thick hard board ground fixed to wooden cleats with C.P. brass screws and washers complete. | 1 | Each | 793.95 | 1149.322 | 793.95 | 1 | nos
50 | 17.73.2 | Providing and fixing SS towel rail complete with brackets fixed to wooden cleats with CP brass screws with concealed fitting arrangement of approved quality and colour. 600mm long towel rail with total length of 645mm, width 78mm and effective height of 88mm, weighing not less than 190gms. | 1 | Each | 541.5 | 783.8754 | 541.5 | 3 | nos
54 | 18.77 | Cutting holes upto 15 x 15 cm in R.C.C. floors and roofs for passing drain pipe etc. and repairing the hole after insertion of drain pipe etc. with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) including finishing complete. | 1 | Each | 193 | 279.3868 | 193
55 | 12.41.2 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A including jointing with seal ring conforming to IS : 5382 leaving 10 mm gap for thermal expansion.(i) Single socketed pipes. 110 mm diameter | 8 | RM | 231.65 | 335.3365 | 1853.2
|  | 110mm dia inlet 110mm dia outlet |  |  |  | 0 | 0 | 2
57 | 18.58.2.1 | Providing and fixing PTMT grating of approved quality and colour.:Rectangular type with openable circular lid.150 mm nominal size square 100 mm diameter of the inner hinged round grating | 3 | Each | 220.45 | 319.1234 | 661.35
59 | 26.1 | Providing and supplying aluminium extruded tubular and other aluminium sections as per the architectural drawings and approved shop drawings , the aluminium quality as per grade 6063 T5 or T6 as per BS 1474,including super durable powder coating of 60-80 microns conforming to AAMA 2604 of required colour and shade as approved by the Engineer-in-Charge. ( The item includes cost of material such as cleats, sleeves, screws etc. necessary for fabrication of extruded aluminium frame work. Nothing extra shall be paid on this account). | 65 | Kg | 338.25 | 489.6507 | 21986.25
60 | 26.2 | Designing, fabricating, testing, protection, installing and fixing in positionsemi (grid) unitized system of structural glazing (with open joints) for linearas well as curvilinear portions of the building for all heights and all levels,including:a) Structural analysis & design and preparation of shop drawings for thespecified design loads conforming to IS 875 part III (the system mustpassed the proof test at 1.5 times design wind pressure without anyfailure), including functional design of the aluminum sections for fixing glazing panels of various thicknesses, aluminium cleats, sleeves and c) Providing and filling, two part pump filled, structural silicone sealant and one part weather silicone sealant compatible with the structuralsilicone sealant of required bite size in a clean and controlled factory /work shop environment , including double sided spacer tape, setting blocks and backer rod, all of approved grade, brand and manufacture,as per the approved sealant design, within and all around the perimeterd) Providing and fixing in position flashings of solid aluminium sheet mm thick and of sizes, shapes and profiles, as required as per the site conditions, to seal the gap between the building structure and all its interfaces with curtain glazing to make it watertighte) Making provision for drainage of moisture/ water that enters the curtainglazing system to make it watertight, by incorporating principles of required), making necessary holes of required sizes and of requirednumbers etc. complete. This item includes cost of all inputs ofsplice plates etc. gaskets, screws, toggles, nuts, bolts, clamps etc., structural and weather silicone sealants, flashings, fire stop (barrier)-cum-smoke seals, microwave cured EPDM gaskets for water tightness, pressure equalisation & drainage and protection against fire hazardincluding:b) Fabricating and supplying serrated M.S. hot dip galvanised / Aluminiumalloy of 6005 T5 brackets of required sizes, sections and profiles etc.to accommodate 3 Dimentional movement for achieving perfectverticality and fixing structural glazing system rigidly to theRCC/masonry/structural steel framework of building structure using stainless steel anchor fasteners/ bolts, nylon seperator to prevent bimetallic contacts with nuts and washers etc. of stainless steel grade 316, of the required capacity and in required numbers | #REF! | Sqm | 2556.2 | 3700.3551 | #REF!
|  | installation of glazed units, T&P, scaffolding and other incidental charges including wastages etc., enabling temporary structures and services, cranes or cradles etc. as described above and as specified. The item includes the cost of getting all the structural and functional design including shop drawings checked by a structural designer, dully approved by Engineer-in-charge. The item also includes the cost of all mock ups at site, cost of all samples of the individual components for testing in an approved laboratory, field tests on the assembled working structural glazing as specified, cleaning and protection till the handing over of the building for occupation. In the end, the Contractor shall provide a water tight structural glazing having all the performance characteristics etc. all complete as required, as per the Architectural drawings, as per item description, as specified, as per the approved shop drawings and as directed by the Engineerin-Charge. |  |  |  | 0 | 0
|  | Note:- 1. The cost of providing extruded aluminium frames, shadow boxes, extruded aluminium section capping for fixing in the grooves of the curtain glazing and vermin proof stainless steel wire mesh shall be paid for separately under relevant items under this subhead. However, for the purpose of payment, only the actual area of structural glazing (including width of grooves ) on the external face shall be measured in sqm. up to two decimal places. Note:-2. The following performance test are to be conducted on structural glazing system if area of structural glazing exceeds 2500 Sqm from the certified laboratories accreditated by NABL(National Accreditation Board for Testing and Calibration Laboratories), Department of Science & Technologies, India. Cost of testing is payable separately. The NIT approving authority will decide the necessity of testing on the basis of cost of the work, cost of the test and importance of the work. Performance Testing of Structural glazing system Tests to be conducted in the NBL Certified laboratories |  |  |  | 0 | 0
61 | 26.3 | Providing, assembling and supplying vision glass panels (IGUs) comprising of hermetically-sealed 6-12- 6 mm insulated glass (double glazed) vision panel units of size and shape as required and specified, comprising of an outer heat strengthened float glass 6mm thick, of approved colour and shade with reflective soft coating on surface # 2 of approved colour and shade, an inner Heat strengthned clear float glass 6mm thick, spacer tube | #REF! | Sqm | 4091 | 5922.1316 | #REF!
63 | 10.2 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete: | 70 | Kg | 73.95 | 107.05 | 5176.5
|  | TOTAL(PART-A) |  |  |  | 0 | #REF! |  | #REF!
|  | ELECTRICAL WORKS(PART-B) | [7 empty] | #REF!
LMR ITEMS
1 |  | Surface mounted Indoor,decorative box type fitting, Retro LED cat ref. LTT8-20 with 20W LED Lamp having high efficiency PMMA diffuser giving soft glare free light of Crompton or Equi | 9 | Each | 3278 |  | 29502
2 |  | Recess down lighter DN194B LED15S of Philips/Equi with lamp | 8 | Each | 2904 |  | 23232
3 |  | Supply of Green square down lighter recessed BBS175 1xDLED of Philips or Equi with Lamp | 4 | Each | 1992 |  | 7968
4 |  | Supply of Recess mounted full glow RC170B LED 29S of Philips or Equi with lamp | 8 | Each | 4646 |  | 37168
5 |  | Supply & installation of LED Lamp Non Dimmable 7/9W B22 on existing angle batten | 2 | Each | 545 |  | 1090
6 |  | Supply of Linnet - LCL-10-CDL,Sleek LED mirror light,with high out put diffuser, 2 feet size of Crompton or Equi | 1 | Each | 2091 |  | 2091
7 |  | Supply of Indoor down lighter,recessed mounted LED down lights with the option for fixed/ adjustable and spot options. BBS312 1xDLED of Philips or Equi | 6 | Each | 2788 |  | 16728
8 |  | Supply & Installation of LED strip light for indoor with driver, Beetle cat ref. LST20RGB of crompton or equi of 5 meter length | 6 | set | 3336 |  | 20016
9 |  | Supply of ceiling fan 1050/1200 mm sweep,230V,1Ph, complete with double ball bearing, motor blades, down rods, canopy, capacitor etc complete as required 5 star rating (Crompton Riviera / Usha Maxx Air / Khaitan Newtec) | 8 | Each | 2180 |  | 17440
10 |  | Supply and installation of Decorative Wall fan 400 mm sweep, 230V.1Ph, complete with Openable mesh Cover ,string Operated etc as required. (Crompton WM Wind Flo / Usha Helix high speed / Khaitan Merlin Hi speed) | 6 | Each | 2698 |  | 16188
11 |  | Supply and fitting 250 mm sweep automatic shutter Sleek and stylish design type exhaust fan complete with louvers and cable from ceiling rose / connector to fan. (Usha Crisp Air / Crompton Crossair / Khaitan Vento). | 2 | Each | 1393 |  | 2786
12 |  | S/F PVC holder: Supplying and fixing PVC batten/ angle holder including connection etc. as required. | 2 | Each | 71 |  | 142
13 |  | Supply & fixing INFORMATION OUTLET WITH FACE PLATE (concealed in modular work station raceways /gypboard partitions/ walls-with modular back box), TERMINATION AND TESTING CAT6 A (AMP/PANDUIT/Systimax) | 10 | Each | 760 |  | 7600
14 |  | Supply of Alluminium cable. Supply of the following sizes of Alluminium armoured PVC insulated, XLPE Power cable of 1.1kV grade to site including transporting and stacking charges at work site.. |  |  |  |  | 0
a |  | 4 X 16 sq. mm | 30 | Metre | 315 |  | 9450
b |  | 4 X 10 sq. mm | 15 | Metre | 278 |  | 4170
15 |  | Supplying and drawing of UTP 4 pair CAT -6A LAN cable in existing surface/ recessed PVC conduit as required, AMP/Molex make | 300 | Metre | 77 |  | 23100
16 |  | S&F MCCB in cubicle Pannel: Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required. |  |  |  |  | 0
|  | 63 Amp, 16 KA TP MCCB | 1 | 1 | 6188 | 6188 | 6188
DSR ITEMS
17 |  | Point wiring in PVC conduit, with Modular type switch: Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
a |  | Group B | 5 | Point | 585 | 846.846 | 4234.23
b |  | Group C | 32 | Point | 718 | 1039.3768 | 33260.0576
18 |  | Twin control point wiring in PVC conduit, with modular type switch: Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. | 2 | Point | 770 | 1114.652 | 2229.304 |  |  | 224859
19 |  | Power plug wiring in PVC conduit ( 2x4 sq mm ): Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 1 No 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 50 | Metre | 162 | 234.5112 | 11725.56
20 |  | Circuit Sub main wiring in PVC Conduit: Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required |  |  |  | 0 | 0
| a | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | 60 | Metre | 106 | 153.4456 | 9206.736
| b | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 80 | Metre | 131 | 189.6356 | 15170.848
| c | 4 X 4 sq. mm + 2 X 4 sq. mm earth wire | 25 | Metre | 275 | 398.09 | 9952.25
| d | 4 X 6 sq. mm + 2 X 6 sq. mm earth wire | 25 | Metre | 389 | 563.1164 | 14077.91
|  | RE- WIRING IN PVC CONDUIT |  |  |  | 0 | 0
21 |  | Telephone wiring in existing conduit: Supplying and drawing following pair 0.5 sq mm FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. |  |  |  | 0 | 0
|  | 2 Pair | 50 | Metre | 18 | 26.0568 | 1302.84
|  | PVC CONDUIT, METAL BOXES |  | Metre |  | 0 | 0
22 |  | S/F PVC conduit: Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. |  |  |  | 0 | 0
| a | 20 mm | 100 | Metre | 146 | 211.3496 | 21134.96
| b | 25 mm | 250 | Metre | 152 | 220.0352 | 55008.8
| c | 40 mm | 20 | Metre | 110 | 159.236 | 3184.72
23 |  | S/F Modular type switch/ socket: Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. |  |  |  | 0 | 0
| a | Telephone socket outlet | 2 | Each | 95 | 137.522 | 275.044
24 |  | Supplying and fixing electronic fan regulator: Supplying and fixing stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | 8 | Each | 284 | 411.1184 | 3288.9472
25 |  | S/F Modular type blanking plates: Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | 12 | Each | 23 | 33.2948 | 399.5376
26 |  | S/F Modular boxes, base & cover plate: Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required. |  |  |  | 0 | 0
| a | 1 or 2 Module (75mmX75mm) | 20 | Each | 166 | 240.3016 | 4806.032
27 |  | S/F light plug point modular type accessaries: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). | 16 | Each | 303 | 438.6228 | 7017.9648
28 |  | S/F Power plug point with modular type switch: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 2 | Each | 395 | 571.802 | 1143.604
29 |  | S/F Ceiling rose: Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. | 15 | Each | 43 | 62.2468 | 933.702
30 |  | S/F call bell/buzzer: Supplying and fixing call bell/ buzzer suitable for single phase, 230 volts, complete as required. | 2 | Each | 61 | 88.3036 | 176.6072
31 |  | ITC Fluroscent/LED fitting directly on surface/celing: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | 35 | Each | 91 | 131.7316 | 4610.606
32 |  | ITC Fluroscent fitting with down rod: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc., including supplying and fixing ball and socket arrangement, 2 no. down rods of 20 mm dia X 1.6 mm thick steel conduit upto 30 cm length, painting and wiring the down rods and connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | 8 | Each | 233 | 337.2908 | 2698.3264
33 |  | S/F extra down rod: Providing and fixing extra conduit down rod of 20 mm dia, 2 X 10 cm length wiring with 2 X 1.5 sq. mm FR PVC insulated, copper conductor, single core cable including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | 16 | Each | 31 | 44.8756 | 718.0096
34 |  | ITC Ceiling fan: Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable etc. as required. | 8 | Each | 95 | 137.522 | 1100.176
35 |  | Extra down rod 15 mm dia 20 CM Length: Supplying and fixing extra conduit down rod of 20 cm length G.I. pipe 15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | 24 | Each | 27 | 39.0852 | 938.0448
36 |  | ITC Exhaust fan: Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. |  |  |  | 0 | 0
|  | Upto 450 mm sweep | 2 | Each | 204 | 295.3104 | 590.6208
37 |  | S/F SP MCB DB: Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) |  |  |  | 0 | 0
|  | 2 + 6/8 way, Double door | 2 | Each | 1041 | 1506.9516 | 3013.9032
38 |  | S/F Vertical Type Pre Wired TP MCB DB: Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required ,suitable for MCCB incomer.(But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.) |  |  |  | 0 | 0
| 2.9.5 | 4 way Double door | 1 | Each | 7901 | 11437.4876 | 11437.4876
39 |  | S/F 'C' series, MCB: Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | 0 | 0
a |  | Single pole | 8 | Each | 169 | 244.6444 | 1957.1552
40 |  | S/F S P MCB blanking plate: Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | 10 | Each | 7 | 10.1332 | 101.332
41 |  | S/F DP MCB isolator: Supplying and fixing following rating, double pole, 240 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | 0 | 0
|  | 40 amps | 2 | Each | 218 | 315.5768 | 631.1536
42 |  | S/F SPN RCCB: Supplying and fixing following rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  | Each |  | 0 | 0
|  | 25 amps | 2 | Each | 1645 | 2381.302 | 4762.604
43 |  | S/F 20A SPN MCB industrial socket outlet: Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 2 | Each | 954 | 1381.0104 | 2762.0208
44 |  | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 1 | Each | 141 | 204.1116 | 204.1116
45 |  | G.I Earth Pipe Electrode With Salt & Charcoal: Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 2 | Each | 3926 | 5683.2776 | 11366.5552
46 |  | Providing and fixing 4.00mm dia copper wire on surface or in recess: Providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 60 | metre | 86 | 124.4936 | 7469.616
47 |  | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. |  |  |  | 0 | 0
|  | Upto 35 sq. mm | 35 | metre | 606 | 877.2456 | 30703.596
48 |  | Supplying and making end termination with brass compression gland and aluminium lugs: Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. |  |  |  | 0 | 0
| 9.1.32 | 4 X 10 sq. mm (25mm) | 2 | Each | 193 | 279.3868 | 558.7736
| 9.1.33 | 4 X 16 sq. mm (28mm) | 2 | Each | 245 | 354.662 | 709.324
|  | TOTAL FOR PART-B |  |  |  |  | 509722.0708
|  | GRAND TOTAL(PARTA+PART-B) |  |  |  |  | #REF!

## civil-+ELEab (2) (hidden)
ESTIMATE FOR CIVIL&ELECTRICAL WORKS IN CONFERENCE HALL IN KAKKANADU FACTORY,COCHIN
Item no. | DSR | Item Description | Qty | Unit | Rate | Rate+CI | Amount
CIVIL WORKS(PART-A)
34 | MR | Providing and fixing arrangement and making necessary holes etc. for fixing required door fitings, all complete as per direction of Engineer-in-charge Door handle, lock and stopper etc. | 6 | Each | 126 |  | 756
45 | LMR | Providing and fixing C.P. brass long body bib cock of (2 in 1 type)approved quality conforming to IS standards and weighing not less than 690 gms.: 15 mm nominal bore: Make:Jauqar, Hindware, Parryware, crome | 2 | Each | 1540 |  | 3080 | 2 | nos
51 | LMR | Providing & fixing of CP Health faucet. Hand operated spray unit( Instand type)).Make:Jauqar, Hindware, Parryware, crome., (Lowest retail price not less than 1200/each. Materials to be selected by the Engineer in charge) | 2 | Each | 2043 |  | 4086 | 2
52 | LMR | Providing and fixing PVC pipes for water supply arrangements including cost pipes, fittings, solvent cement,testing of pipes, labour charges etc complete : Concealed work including cutting chases and making good the wall etc |  |  |  | 0 | 0
|  | 20mm nominal outer dia .Pipes. (10kg/cm2) | 20 | RM | 220 |  | 4400
|  | 32mm nominal outer dia .Pipes. (10kg/cm2) | 20 | RM | 236 |  | 4720
53 | LMR | Providing and fixing PVC soil, waste and vent pipe to IS : 13592 of SWR quality, including all fittings, like EG : Bends, Tees, Elbows, Collars, junction, inspection doors, cowls, offsets, access pipes, jointing with rubber ring / solvent cement by application of leak proof adhesive like FRP paste including cutting holes in walls and floors and making good. Make: Supreme, Finolex, Astral |  |  |  | 0 | 0
|  | 50mm dia (6kg / sq.cm) | 20 | RM | 260.45 |  | 5209
|  | 63mm dia (6kg / sq.cm) | 25 | RM | 306 |  | 7650
|  | 75mm dia (6kg / sq.cm) | 20 | RM | 407 |  | 8140
|  | 110mm dia (6 kg / sq.cm) | 20 | RM | 557 |  | 11140
56 | MR | Providing and fixing PVC floor trap self cleansing design with or without vent arm complete including cutting and making good the walls and floors. Make:Supreme,Finolex,Prince etc.., | 2 | Each | 519 |  | 1038
|  | 110mm dia inlet 110mm dia outlet |  |  |  | 0 | 0 | 2
58 | LMR | Providing and fixing C.P. brass pillar cock (push type)approved quality conforming to IS standards and weighing not less than 690 gms.: 15 mm nominal bore for wash basins: Make:Jauqar, Hindware, Parryware, crome | 2 | Each | 2706 |  | 5412 | 3 | nos
62 | LMR | Providing and fixing poly carbonate (multi wall 6mm or nearest size) sheet roofing of approved make and quality fixed with polymer coated J or L hooks, bolts and nuts of required diameter with necessary washers complete including the cost of M.S square tube 50x25mm 16 gauge fixed with MS flat 25x6mm including necessary nuts and bolts to support the roofing,painting witn two or more coatswaithsyntheticenamel paint over a priming coat of Zinchromate primer etc complete. | 6.22 | Sqm | 2785.59 |  | 17326.3698
|  | TOTAL(PART-A) |  |  |  | 0 | 0
|  | ELECTRICAL WORKS(PART-B) |  |  |  |  | 72957.3698
LMR ITEMS
1 |  | Surface mounted Indoor,decorative box type fitting, Retro LED cat ref. LTT8-20 with 20W LED Lamp having high efficiency PMMA diffuser giving soft glare free light of Crompton or Equi | 9 | Each | 3278 |  | 29502
2 |  | Recess down lighter DN194B LED15S of Philips/Equi with lamp | 8 | Each | 2904 |  | 23232
3 |  | Supply of Green square down lighter recessed BBS175 1xDLED of Philips or Equi with Lamp | 4 | Each | 1992 |  | 7968
4 |  | Supply of Recess mounted full glow RC170B LED 29S of Philips or Equi with lamp | 8 | Each | 4646 |  | 37168
5 |  | Supply & installation of LED Lamp Non Dimmable 7/9W B22 on existing angle batten | 2 | Each | 545 |  | 1090
6 |  | Supply of Linnet - LCL-10-CDL,Sleek LED mirror light,with high out put diffuser, 2 feet size of Crompton or Equi | 1 | Each | 2091 |  | 2091
7 |  | Supply of Indoor down lighter,recessed mounted LED down lights with the option for fixed/ adjustable and spot options. BBS312 1xDLED of Philips or Equi | 6 | Each | 2788 |  | 16728
8 |  | Supply & Installation of LED strip light for indoor with driver, Beetle cat ref. LST20RGB of crompton or equi of 5 meter length | 6 | set | 3336 |  | 20016
9 |  | Supply of ceiling fan 1050/1200 mm sweep,230V,1Ph, complete with double ball bearing, motor blades, down rods, canopy, capacitor etc complete as required 5 star rating (Crompton Riviera / Usha Maxx Air / Khaitan Newtec) | 8 | Each | 2180 |  | 17440
10 |  | Supply and installation of Decorative Wall fan 400 mm sweep, 230V.1Ph, complete with Openable mesh Cover ,string Operated etc as required. (Crompton WM Wind Flo / Usha Helix high speed / Khaitan Merlin Hi speed) | 6 | Each | 2698 |  | 16188
11 |  | Supply and fitting 250 mm sweep automatic shutter Sleek and stylish design type exhaust fan complete with louvers and cable from ceiling rose / connector to fan. (Usha Crisp Air / Crompton Crossair / Khaitan Vento). | 2 | Each | 1393 |  | 2786
12 |  | S/F PVC holder: Supplying and fixing PVC batten/ angle holder including connection etc. as required. | 2 | Each | 71 |  | 142
13 |  | Supply & fixing INFORMATION OUTLET WITH FACE PLATE (concealed in modular work station raceways /gypboard partitions/ walls-with modular back box), TERMINATION AND TESTING CAT6 A (AMP/PANDUIT/Systimax) | 10 | Each | 760 |  | 7600
14 |  | Supply of Alluminium cable. Supply of the following sizes of Alluminium armoured PVC insulated, XLPE Power cable of 1.1kV grade to site including transporting and stacking charges at work site.. |  |  |  |  | 0
a |  | 4 X 16 sq. mm | 30 | Metre | 315 |  | 9450
b |  | 4 X 10 sq. mm | 15 | Metre | 278 |  | 4170
15 |  | Supplying and drawing of UTP 4 pair CAT -6A LAN cable in existing surface/ recessed PVC conduit as required, AMP/Molex make | 300 | Metre | 77 |  | 23100
16 |  | S&F MCCB in cubicle Pannel: Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required. |  |  |  |  | 0
|  | 63 Amp, 16 KA TP MCCB | 1 | 1 | 6188 | 6188 | 6188
DSR ITEMS
17 |  | Point wiring in PVC conduit, with Modular type switch: Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. | [7 empty] | 224859
a |  | Group B | 5 | Point | 585 | 846.846 | 4234.23
b |  | Group C | 32 | Point | 718 | 1039.3768 | 33260.0576
18 |  | Twin control point wiring in PVC conduit, with modular type switch: Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. | 2 | Point | 770 | 1114.652 | 2229.304 |  |  | 224859
19 |  | Power plug wiring in PVC conduit ( 2x4 sq mm ): Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 1 No 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 50 | Metre | 162 | 234.5112 | 11725.56
20 |  | Circuit Sub main wiring in PVC Conduit: Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required |  |  |  | 0 | 0
| a | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | 60 | Metre | 106 | 153.4456 | 9206.736
| b | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 80 | Metre | 131 | 189.6356 | 15170.848
| c | 4 X 4 sq. mm + 2 X 4 sq. mm earth wire | 25 | Metre | 275 | 398.09 | 9952.25
| d | 4 X 6 sq. mm + 2 X 6 sq. mm earth wire | 25 | Metre | 389 | 563.1164 | 14077.91
|  | RE- WIRING IN PVC CONDUIT |  |  |  | 0 | 0
21 |  | Telephone wiring in existing conduit: Supplying and drawing following pair 0.5 sq mm FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. |  |  |  | 0 | 0
|  | 2 Pair | 50 | Metre | 18 | 26.0568 | 1302.84
|  | PVC CONDUIT, METAL BOXES |  | Metre |  | 0 | 0
22 |  | S/F PVC conduit: Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. |  |  |  | 0 | 0
| a | 20 mm | 100 | Metre | 146 | 211.3496 | 21134.96
| b | 25 mm | 250 | Metre | 152 | 220.0352 | 55008.8
| c | 40 mm | 20 | Metre | 110 | 159.236 | 3184.72
23 |  | S/F Modular type switch/ socket: Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. |  |  |  | 0 | 0
| a | Telephone socket outlet | 2 | Each | 95 | 137.522 | 275.044
24 |  | Supplying and fixing electronic fan regulator: Supplying and fixing stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | 8 | Each | 284 | 411.1184 | 3288.9472
25 |  | S/F Modular type blanking plates: Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | 12 | Each | 23 | 33.2948 | 399.5376
26 |  | S/F Modular boxes, base & cover plate: Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required. |  |  |  | 0 | 0
| a | 1 or 2 Module (75mmX75mm) | 20 | Each | 166 | 240.3016 | 4806.032
27 |  | S/F light plug point modular type accessaries: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). | 16 | Each | 303 | 438.6228 | 7017.9648
28 |  | S/F Power plug point with modular type switch: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 2 | Each | 395 | 571.802 | 1143.604
29 |  | S/F Ceiling rose: Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. | 15 | Each | 43 | 62.2468 | 933.702
30 |  | S/F call bell/buzzer: Supplying and fixing call bell/ buzzer suitable for single phase, 230 volts, complete as required. | 2 | Each | 61 | 88.3036 | 176.6072
31 |  | ITC Fluroscent/LED fitting directly on surface/celing: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | 35 | Each | 91 | 131.7316 | 4610.606
32 |  | ITC Fluroscent fitting with down rod: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc., including supplying and fixing ball and socket arrangement, 2 no. down rods of 20 mm dia X 1.6 mm thick steel conduit upto 30 cm length, painting and wiring the down rods and connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | 8 | Each | 233 | 337.2908 | 2698.3264
33 |  | S/F extra down rod: Providing and fixing extra conduit down rod of 20 mm dia, 2 X 10 cm length wiring with 2 X 1.5 sq. mm FR PVC insulated, copper conductor, single core cable including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | 16 | Each | 31 | 44.8756 | 718.0096
34 |  | ITC Ceiling fan: Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable etc. as required. | 8 | Each | 95 | 137.522 | 1100.176
35 |  | Extra down rod 15 mm dia 20 CM Length: Supplying and fixing extra conduit down rod of 20 cm length G.I. pipe 15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | 24 | Each | 27 | 39.0852 | 938.0448
36 |  | ITC Exhaust fan: Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. |  |  |  | 0 | 0
|  | Upto 450 mm sweep | 2 | Each | 204 | 295.3104 | 590.6208
37 |  | S/F SP MCB DB: Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) |  |  |  | 0 | 0
|  | 2 + 6/8 way, Double door | 2 | Each | 1041 | 1506.9516 | 3013.9032
38 |  | S/F Vertical Type Pre Wired TP MCB DB: Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required ,suitable for MCCB incomer.(But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.) |  |  |  | 0 | 0
| 2.9.5 | 4 way Double door | 1 | Each | 7901 | 11437.4876 | 11437.4876
39 |  | S/F 'C' series, MCB: Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | 0 | 0
a |  | Single pole | 8 | Each | 169 | 244.6444 | 1957.1552
40 |  | S/F S P MCB blanking plate: Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | 10 | Each | 7 | 10.1332 | 101.332
41 |  | S/F DP MCB isolator: Supplying and fixing following rating, double pole, 240 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | 0 | 0
|  | 40 amps | 2 | Each | 218 | 315.5768 | 631.1536
42 |  | S/F SPN RCCB: Supplying and fixing following rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  | Each |  | 0 | 0
|  | 25 amps | 2 | Each | 1645 | 2381.302 | 4762.604
43 |  | S/F 20A SPN MCB industrial socket outlet: Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 2 | Each | 954 | 1381.0104 | 2762.0208
44 |  | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 1 | Each | 141 | 204.1116 | 204.1116
45 |  | G.I Earth Pipe Electrode With Salt & Charcoal: Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 2 | Each | 3926 | 5683.2776 | 11366.5552
46 |  | Providing and fixing 4.00mm dia copper wire on surface or in recess: Providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 60 | metre | 86 | 124.4936 | 7469.616
47 |  | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. |  |  |  | 0 | 0
|  | Upto 35 sq. mm | 35 | metre | 606 | 877.2456 | 30703.596
48 |  | Supplying and making end termination with brass compression gland and aluminium lugs: Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. |  |  |  | 0 | 0
| 9.1.32 | 4 X 10 sq. mm (25mm) | 2 | Each | 193 | 279.3868 | 558.7736
| 9.1.33 | 4 X 16 sq. mm (28mm) | 2 | Each | 245 | 354.662 | 709.324
|  | TOTAL FOR PART-B |  |  |  |  | 509722.0708
|  | GRAND TOTAL(PARTA+PART-B) |  |  |  |  | 509722.0708

## DSR) (hidden)
ESTIMATE FOR CIVILWORKS IN CONFERENCE HALL IN KAKKANADU FACTORY,COCHIN-PART-A
Item no. | DSR | Item Description | Qty | Unit | Rate | Rate+CI | Amount
CIVIL WORKS(PART-A)
1 | 15.2.2 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material as per direction of Engineer-in-charge. | 10 | Cum | 550.5 | 796.9038 | 5505
2 | 15.3 | Demolishing R.C.C. work manually/ by mechanical means includingstacking of steel bars and disposal of unserviceable material as per direction of Engineer - in- charge. | 1 | Cum | 1302.3 | 1885.2095 | 1302.3
3 | 15.5 | Extra for cutting reinforcement bars manually/ by mechanical means inR.C.C. or R.B. work (Payment shall be made on the cross sectional areaof R.C.C. or R.B. work) as per direction of Engineer -in -charge. | 30 | Sqm | 450.45 | 652.0714 | 13513.5 | 30
4 | 15.23.1 | Dismantling tile work in floors, dadoing and roofs laid in cement mortar including stacking material within 50 metres lead.For thickness of tiles up to 25 mm | 25 | Sqm | 28.2 | 40.8223 | 705
5 | 15.5 | Dismantling of Water closets/wash basin/flushing cistern etc. of all types (C.I./PVC/Vitrious China) including stacking of useful materials near the site and disposal of unserviceable materials | 2 | Each | 519.87 | 752.5638 | 1039.74 | 2 | Nos
6 | 15.6 | Disposal of building rubbish / malba / similar unserviceable, dismantled or waste materials by mechanical means including loading, transporting, unloading to approved municipal dumping ground or as approved by Engineer-in-charge, beyond 50 m initial lead, for all loads including all lifts involved. | 40 | Cum | 123.7 | 179.0681 | 4948
7 | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30cm in depth. 1.5m in width as well as 10 sqm on plan) including disposal of excavated earth and lift upto 1.5m, disposed earth to be levelled and neatly dressed.:All kinds of soil | 3.375 | Cum | 155.6 | 225.2466 | 525.15
8 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All works up to plinth level-.1:4:8 (1 Cement : 4 coarse sand : 8 graded stone aggregate 40mm nominal size) | #REF! | Cum | 4301.2 | 6226.4171 | #REF!
9 | 5.37 | Providing and laying in position ready mixed M-25 grade concrete for reinforced cement concrete work, using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , excluding the cost of centering, shuttering finishing and reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, improve workability without impairing strength and durability as per direction of the Engineer - in - charge. |  |  |  | 0 | 0 | 0
|  | (Note :- Cement content considered in this item is @ 330 kg/cum. Excess/less cement used as per design mix is payable/recoverable separately). |  |  |  | 0 | 0 | 0
| 5.37.2 | All work above plinth level up to floor V level -RCC work (M25 concrete) | 22.3373 | Cum | 7363 | 10658.6788 | 164469.1938 | #VALUE!
10 | 5.9 | Centering and shuttering including strutting, propping etc., and removal of form for, |  |  |  | 0 | 0 | 0
10.a | 5.9.1 | Foundations, Footings, bases of columns,etc for mass concrete. | 2.25 | Sqm | 196.45 | 284.381 | 442.0125
10.a | 5.9.6 | Columns and Pillars, Piers, Abutments, Posts and Struts. | 64 | Sqm | 453.35 | 656.2695 | 29014.4
10.b | 5.9.3 | Suspended floors, roofs, landings, Balconies and access platform | 103 | Sqm | 453.35 | 656.2695 | 46695.05
10.c | 5.9.5 | Lintel,beams,plinth beams,girders,bressumers and cantilevers | 74 | Sqm | 332.15 | 480.8203 | 24579.1
10.d | 5.9.19 | Weather shade, Chajjas, corbels etc., including edges | 15 | Sqm | 492.35 | 712.7259 | 7385.25
11 | 5.22.A.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending,placing in position and binding all complete above plinth level. :Thermo-Mechanically Treated bars | 2203.5283 | Kg | 68.1 | 98.5816 | 150060.2786
12 | 6.4.2 | Brick work with F.P.S bricks of class designation 5.0 in superstructure above plinth level up to floor v level in all shapes an sizes in: Cement mortar 1: 6 (1 cement :6 coarse sand) | 24.1605 | Cum | 5426.15 | 7854.8947 | 131098.693
13 | 6.13.1 | Half brick masonry with F.P.S brick of class designation 7.5 in superstructure above plinth level up to floor V level : CM 1:3 (1 cement : 3 coarse sand) | 28.88 | Sqm | 692.8 | 1002.8973 | 20008.064
14 | 6.15 | Extra for providing and placing in position 2 Nos. 6mm dia M.S bars at every third course of half brick masonry (with FPS brick) | 28.88 | Sqm | 69.5 | 100.6082 | 2007.16
15 | 13.2.1 | 15mm cement plaster on the rough side of single or half brick wall of mix : 1 : 4 (1 cement : 4 fine sand) up to 10m height for external walls | 74 | Sqm | 189.4 | 274.1754 | 14015.6
16 | 13.1.1 | 12mm cement plaster on the rough side of single or half brick wall of mix : 1 : 4 (1 cement : 4 fine sand) for internal walls, column and beams etc | 305.1168 | Sqm | 163.35 | 236.4655 | 49840.8293
17 | 13.16.1 | 6 mm cement plaster of mix : 1:3 (1 cement: 3 fine sand) for ceiling plastering | 93.1392 | Sqm | 134.7 | 194.9917 | 12545.8502
18 | 13.8 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. | 398.256 | Sqm | 89.65 | 129.7773 | 35703.6504
19 | 13.60.1 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade –Two or more coats on new work.-internal walls | 398.256 | Sqm | 80.5 | 116.5318 | 32059.608
20 | 13.48.1 | Finishing walls with Acrylic Smooth exterior paint of required shade : New work (Two or more coat applied @ 1.67 ltr/10 sqmover and including priming coat of exterior primer applied @ 2.20 kg/ 10 sqm) | 74 | Sqm | 100 | 144.76 | 7400
21 | 13.48.3 | Painting Steel work with Delux Multi surface paint to give an even shade.Two or more coat applied @ 0.90 ltr/10sqm over an over an under coat of primer applied @ 0.80ltr/10aqm of approved brand or manufacture. | 3.315 | Sqm | 90 | 130.284 | 298.35
22 | 8.2.2.2 | Providing and fixing 18mm thick gang saw cut mirror polished premoulded and prepolished) machine cut for kitchen platforms, vanity counters, window sills , facias and similar locations of required size of approved shade, colour and texture laid over 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels. Granite of any colour and shade: Area of slab over 0.50 sqm.: Lowest retail price not less than Rs. 2500.00/m2( Granite to be selected by the Engineer in charge) | 0.9 | Sqm | 2463.55 | 3566.235 | 2217.195
23 | 9.117.1 | Providing and fixing factory made UPVC door frame made of UPVC extruded section having an overall dimensions as below ( tolerance ± 1mm ), with wall thickness 2.0mm (± 0.2mm), corners of the door frame to be joined with galvanized brackets and stainless steel screws, joints mitered and plastic welded. The hinged side vertical of the frames reinforced by galvanized M.S. tube of size 19x19 mm and 1mm (± 0.1mm) wall thickness and 3 nos. Stainless steel hinged fixed to the frame complete as per manufacturers Specification and direction of engineering -in-change : Extruded section profile size 48x40 mm | 6.72 | M | 213.75 | 309.4245 | 1436.4
24 | 9.118.1 | Providing and fixing existing door frames: 24 mm thick factory made PVC door shutters made of styles and rails of a UPVC hollow section of size 59x24 mm and wall thickness 2 mm (± 0.2mm) with in built edging on both sides. The styles and rails mitered and joint at the corners by means of M.S. galvanized / plastic brackets of size 75x220 mm having wall thickness 1.0 mm and stainless steel screws. The styles of the shutter reinforced by inserting galvanized M.S. tube of size 20x20 mm and 1mm (± 0.1mm) wall thickness. The lock rail made up of " H" section, a UPVC hollow section of size 100x24 mm and 2mm (± 0.2mm) wall thickness, fixed to the shutters styles by means of plastic/ galvanized M.S.'U' cleats. The shutter frame filled with a UPVC multi chambered single panel of size not less than 620mm, having over all thickness of 20mm and 1mm (± 0.1mm) wall thickness. The panes filled vertically and tie bar at two places by inserting horizontally 6mm galvanized M.S. rod and fastened with nuts and washers, complete as per manufacturer's specification and direction of Engineer- in - charge. (for W,C and bath room door shutter). | 6.72 | Sqm | 2718.6 | 3935.4454 | 18268.992
25 | 11.41.2 | Providing and laying polished vitrified floor tile in different sizes (thickness to be specified by the manufacturer) with Acid and / or Alkali resistant tiles with water absorptions less than 0.08% and confirming to IS:15622 of approved make in all colours and shades, laid on 20mm thick cement mortor 1:4 (1 cement:4 Coard sand) including grouting the joints with white cement and matching pigments etc. complete. (Lowest retail price not less than Rs. 880/m2) : Size of Tiles 60 x 60 cm (Tiles to be selected by the Engineer in charge) | 68.9249 | sqm | 1405.95 | 2035.2532 | 96904.9632
26 | 11.39 | Providing and laying rectified Glazed Ceramic floor tiles 300x300 mm or more (thickness to be specified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make in colours White, Ivory, Grey, Fume Red Brown, laid on 20mm thick cement mortar 1:4 (1 Cement : 4 Coarse sand) including grouting the joints with white cement and matching pigments etc., complete.(lowest price of tile not less than 650/m2) | 6.4904 | sqm | 950.05 | 1375.2924 | 6166.2045
27 | 11.4 | Providing and fixing Ist quality ceramic glazed wall tiles of size 300x450mm conforming to IS : 15622 (thickness to be specified by the manufacturer ) of approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados over 12 mm thick bed of cement Mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm including pointing in white cement mixed with pigment of matching shade complete.(.(lowest price of tile not less than 725/m2) | 25 | sqm | 1009.6 | 1461.497 | 25240
28 | 12.45 | Providing and fixing false ceiling at all height including providing and fixingof frame work made of special sections, power pressed from M.S. sheets and galvanized with zinc coating of 120 gms/sqm (both side inclusive) asper IS : 277 and consisting of angle cleats of size 25 mm wide x 1.6 mmthick with flanges of 27 mm and 37mm, at 1200 mm centre to centre, oneflange fixed to the ceiling with dash fastener 12.5 mm dia x 50mm long with6mm dia bolts, other flange of cleat fixed to the angle hangers of 25x10x0.50mm of required length with nuts & bolts of required size and other end ofangle hanger fixed with intermediate G.I. channels 45x15x0.9 mm runningat the spacing of 1200 mm centre to centre, to which the ceiling section0.5 mm thick bottom wedge of 80 mm with tapered flanges of 26 mm eachhaving lips of 10.5 mm, at 450 mm centre to centre, shall be fixed in adirection perpendicular to G.I. intermediate channel with connecting clipsmade out of 2.64 mm dia x 230 mm long G.I. wire at every junction, includingfixing perimeter channels 0.5 mm thick 27 mm high having flanges of 20mm and 30 mm long, the perimeter of ceiling fixed to wall/partition with the |  |  |  | 0 | 0
|  | help of rawl plugs at 450 mm centre, with 25mm long dry wall screws @230 mm interval, including fixing of gypsum board to ceiling section andperimeter channel with the help of dry wall screws of size 3.5 x 25 mm at230 mm c/c, including jointing and finishing to a flush finish of tapered andsquare edges of the board with recomme-nded jointing compound , |  |  |  |  | 0
| 12.45.1 | 12.5 mm thick tapered edge gypsum plain board conformingto IS: 2095- Part I | 48.1626 | sqm | 907.1 | 1313.118 | 43688.2945 | #VALUE! | sqm
29 | 21.1.1.2 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) : For fixed portion: Powder coated aluminium (minimum thickness of powder coating 50 micron) | 115.83 | kg | 377.75 | 546.8309 | 43754.7825
30 | 21.1.2.2 | For shutters of doors, windows & ventilators including providing and fixing hinges/ pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately). Powder coated aluminium (minimum thickness of powder coating 50 micron) | 75.6 | Kg | 435.75 | 630.7917 | 32942.7
31 | 21.3.2 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.5 mm thickness | 15.12 | sqm | 1054.2 | 1526.0599 | 15939.504
32 | 21.8 | Filling the gap in between aluminium frame & adjacent RCC/Brick/Stone work by providing weather silicon sealant over backer rod of approved quality as per architectural drawings and direction of Enginner-in-charge complete. |  |  |  | 0 | 0
| 21.8.1 | Upto 5mm depth and 5mm width | 10 | Rm | 88.75 | 128.4745 | 887.5
33 | 21.18 | Providing and fixing 12 mm thick frameless toughened glass door shutter of approved brand and manufacture, including providing and fixing top & bottom pivot & spring type fixing arrangement and making necessary holes etc. for fixing required door fitings, all complete as per direction of Engineer-in-charge ( Door handle, lock and stopper etc. to be paid separately) | 2.7 | Sqm | 4746.3 | 6870.7439 | 12815.01
35 | 9.83 | Providing and fixing aluminium die cast body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 35 kg and door width upto 700 mm) with necessary accessories and screws etc. complete. | 2 | Each | 753.75 | 1091.1285 | 1507.5
36 | 9.97 | Providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade with necessary screws etc., complete. |  |  |  | 0 | 0
| 9.97.2 | 250 x 10mm | 8 | Each | 95.25 | 137.8839 | 762
| 9.97.4 | 150 x 10mm | 8 | Each | 65.35 | 94.6007 | 522.8
37 | 21.13 | Providing and fixing 100mm brass locks (best make of approved quality) for aluminum doors including necessary cutting and making good etc. complete | 8 | Each | 418.65 | 606.0377 | 3349.2
38 | 21.12.2 | Providing and fixing aluminium tubular handle bar 32 mm outer dia, 3.0 mm thick & 2100 mm long with SS screws etc .complete as per direction of Engineer-in-Charge. Powder coated minimum thickness 50 micron aluminium tubular handle bar. | 8 | Each | 508.55 | 736.177 | 4068.4
39 | 9.101 | Providing and fixing aluminium hanging floor door stopper ISI marked anodised (anodic coating note less than grade AC 10 as per IS : 1868) transparent or dyed to required colour and shade with necessary screws etc., complete. |  |  |  | 0 | 0
| 9.101.1 | Single rubber stopper | 3 | Each | 37.5 | 54.285 | 112.5
40 | 21.4 | Providing and fixing double action hydraulic floor spring of approved brand and manufacture IS : 6315 marked, for doors including cost of cutting floors as required, embedding in floors and cover plates with brass pivot and single piect M.S. sheet outer box with side plate etc., complete as per the direction of Engineer-in-charge. |  |  |  | 0 | 0
| 21.4.2 | With brass cover plate | 1 | Each | 2213.2 | 3203.8283 | 2213.2
41 | 9.149 | Providing and fixing casement handle made of zinc alloyed (white powder coated) for uPVC casement window with necessary screws etc. complete. | 4 | Each | 216.65 | 313.6225 | 866.6
42 | 9.68.1 | Providing and fixing oxidised M.S. casement stays (straight peg type) with necessary screws etc. Complete-300 mm weighing not less than 200 gms | 8 | Each | 36.2 | 52.4031 | 289.6
46 | 17.28.1.1 | Providing and fixing PVC Waste pipe for sink or wash basin including PVC waste fittings complete.:Semi rigid pipe 32mm dia | 2 | Each | 76.75 | 111.1033 | 153.5 | 2 | nos
47 | 17.34.1 | Providing and fixing Toilet paper holder . Make:Hindware,Cera,Jaquar etc..,:C.P Brass | 1 | Each | 415.9 | 602.0568 | 415.9 | 2 | nos
48 | 18.65 | Providing and fixing SS soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements. Weighing not less than 106 gms. | 1 | Each | 164.95 | 238.7816 | 164.95 | 3 | nos
49 | 17.31 | Providing and fixing 600 x 450mm bevelled edge mirror of superior glass (of approved quality) complete with 6mm thick hard board ground fixed to wooden cleats with C.P. brass screws and washers complete. | 1 | Each | 793.95 | 1149.322 | 793.95 | 1 | nos
50 | 17.73.2 | Providing and fixing SS towel rail complete with brackets fixed to wooden cleats with CP brass screws with concealed fitting arrangement of approved quality and colour. 600mm long towel rail with total length of 645mm, width 78mm and effective height of 88mm, weighing not less than 190gms. | 1 | Each | 541.5 | 783.8754 | 541.5 | 3 | nos
54 | 18.77 | Cutting holes upto 15 x 15 cm in R.C.C. floors and roofs for passing drain pipe etc. and repairing the hole after insertion of drain pipe etc. with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) including finishing complete. | 1 | Each | 193 | 279.3868 | 193
55 | 12.41.2 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A including jointing with seal ring conforming to IS : 5382 leaving 10 mm gap for thermal expansion.(i) Single socketed pipes. 110 mm diameter | 8 | RM | 231.65 | 335.3365 | 1853.2
57 | 18.58.2.1 | Providing and fixing PTMT grating of approved quality and colour.:Rectangular type with openable circular lid.150 mm nominal size square 100 mm diameter of the inner hinged round grating | 3 | Each | 220.45 | 319.1234 | 661.35
59 | 26.1 | Providing and supplying aluminium extruded tubular and other aluminium sections as per the architectural drawings and approved shop drawings , the aluminium quality as per grade 6063 T5 or T6 as per BS 1474,including super durable powder coating of 60-80 microns conforming to AAMA 2604 of required colour and shade as approved by the Engineer-in-Charge. ( The item includes cost of material such as cleats, sleeves, screws etc. necessary for fabrication of extruded aluminium frame work. Nothing extra shall be paid on this account). | 65 | Kg | 338.25 | 489.6507 | 21986.25
60 | 26.2 | Designing, fabricating, testing, protection, installing and fixing in positionsemi (grid) unitized system of structural glazing (with open joints) for linearas well as curvilinear portions of the building for all heights and all levels,including:a) Structural analysis & design and preparation of shop drawings for thespecified design loads conforming to IS 875 part III (the system mustpassed the proof test at 1.5 times design wind pressure without anyfailure), including functional design of the aluminum sections for fixing glazing panels of various thicknesses, aluminium cleats, sleeves and c) Providing and filling, two part pump filled, structural silicone sealant and one part weather silicone sealant compatible with the structuralsilicone sealant of required bite size in a clean and controlled factory /work shop environment , including double sided spacer tape, setting blocks and backer rod, all of approved grade, brand and manufacture,as per the approved sealant design, within and all around the perimeterd) Providing and fixing in position flashings of solid aluminium sheet mm thick and of sizes, shapes and profiles, as required as per the site conditions, to seal the gap between the building structure and all its interfaces with curtain glazing to make it watertighte) Making provision for drainage of moisture/ water that enters the curtainglazing system to make it watertight, by incorporating principles of required), making necessary holes of required sizes and of requirednumbers etc. complete. This item includes cost of all inputs ofsplice plates etc. gaskets, screws, toggles, nuts, bolts, clamps etc., structural and weather silicone sealants, flashings, fire stop (barrier)-cum-smoke seals, microwave cured EPDM gaskets for water tightness, pressure equalisation & drainage and protection against fire hazardincluding:b) Fabricating and supplying serrated M.S. hot dip galvanised / Aluminiumalloy of 6005 T5 brackets of required sizes, sections and profiles etc.to accommodate 3 Dimentional movement for achieving perfectverticality and fixing structural glazing system rigidly to theRCC/masonry/structural steel framework of building structure using stainless steel anchor fasteners/ bolts, nylon seperator to prevent bimetallic contacts with nuts and washers etc. of stainless steel grade 316, of the required capacity and in required numbers | 9.38 | Sqm | 2556.2 | 3700.3551 | 23977.156
|  | installation of glazed units, T&P, scaffolding and other incidental charges including wastages etc., enabling temporary structures and services, cranes or cradles etc. as described above and as specified. The item includes the cost of getting all the structural and functional design including shop drawings checked by a structural designer, dully approved by Engineer-in-charge. The item also includes the cost of all mock ups at site, cost of all samples of the individual components for testing in an approved laboratory, field tests on the assembled working structural glazing as specified, cleaning and protection till the handing over of the building for occupation. In the end, the Contractor shall provide a water tight structural glazing having all the performance characteristics etc. all complete as required, as per the Architectural drawings, as per item description, as specified, as per the approved shop drawings and as directed by the Engineerin-Charge. |  |  |  | 0 | 0
|  | Note:- 1. The cost of providing extruded aluminium frames, shadow boxes, extruded aluminium section capping for fixing in the grooves of the curtain glazing and vermin proof stainless steel wire mesh shall be paid for separately under relevant items under this subhead. However, for the purpose of payment, only the actual area of structural glazing (including width of grooves ) on the external face shall be measured in sqm. up to two decimal places. Note:-2. The following performance test are to be conducted on structural glazing system if area of structural glazing exceeds 2500 Sqm from the certified laboratories accreditated by NABL(National Accreditation Board for Testing and Calibration Laboratories), Department of Science & Technologies, India. Cost of testing is payable separately. The NIT approving authority will decide the necessity of testing on the basis of cost of the work, cost of the test and importance of the work. Performance Testing of Structural glazing system Tests to be conducted in the NBL Certified laboratories |  |  |  | 0 | 0
62 | 10.2 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete: | 70 | Kg | 73.95 | 107.05 | 5176.5
|  | TOTAL(PART-A) |  |  |  | 0 | #REF!

## LMR (hidden)
ESTIMATE FOR CIVILWORKS IN CONFERENCE HALL IN KAKKANADU FACTORY,COCHIN-PART-A
Item no. | DSR | Item Description | Qty | Unit | Rate | Rate+CI | Amount
34 | MR | Providing and fixing arrangement and making necessary holes etc. for fixing required door fitings, all complete as per direction of Engineer-in-charge Door handle, lock and stopper etc. | 6 | Each | 126
43 | LMR | Providing and fixing wash basin (counter type) with CI / MS brackets, 15mm CP brass Pillar taps, 32mm CP brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever required.: White Vitreous China Wash basin size 630 x 450mm with a single 15mm C.P brass piller tap. Make:Hindware,Cera,Jaquar etc.., (Lowest retail price of basin not less than Rs. 3000/each and Pillar tap not less than Rs. 2000/each. Materials to be selected by the Engineer in charge) | 2 | Each | 6732.75
44 | M.R | Providing and fixing white vitreous china Wall Mounted type water closet (European type W.C.pan) with seat and lid, 3/6 litre low level white vitrous Dual Flushing cistern and C.P flush bend with fitting and C.I brackets, 40mm flush bend, overflow arrangement with specials of standard make and mosquito proof coupling of approved municipal design complete including painting of fittings and brackets, cutting and making good the walls and floors wherever required. Make:Hindware,Cera,Jaquar etc.., WC pan with ISI marked white solid plastic seat and lid (Lowest retail price not less than 10,000/each. Materials to be selected by the Engineer in charge) | 2 | Each | 13797.5
45 | LMR | Providing and fixing C.P. brass long body bib cock of (2 in 1 type)approved quality conforming to IS standards and weighing not less than 690 gms.: 15 mm nominal bore: Make:Jauqar, Hindware, Parryware, crome | 2 | Each | 1540 |  |  | 2 | nos
51 | LMR | Providing & fixing of CP Health faucet. Hand operated spray unit( Instand type)).Make:Jauqar, Hindware, Parryware, crome., (Lowest retail price not less than 1200/each. Materials to be selected by the Engineer in charge) | 2 | Each | 2043 |  |  | 2
52 | LMR | Providing and fixing PVC pipes for water supply arrangements including cost pipes, fittings, solvent cement,testing of pipes, labour charges etc complete : Concealed work including cutting chases and making good the wall etc |  |  |  | 0
|  | 20mm nominal outer dia .Pipes. (10kg/cm2) | 20 | RM | 220
|  | 32mm nominal outer dia .Pipes. (10kg/cm2) | 20 | RM | 236
53 | LMR | Providing and fixing PVC soil, waste and vent pipe to IS : 13592 of SWR quality, including all fittings, like EG : Bends, Tees, Elbows, Collars, junction, inspection doors, cowls, offsets, access pipes, jointing with rubber ring / solvent cement by application of leak proof adhesive like FRP paste including cutting holes in walls and floors and making good. Make: Supreme, Finolex, Astral |  |  |  | 0
|  | 50mm dia (6kg / sq.cm) | 20 | RM | 260.45
|  | 63mm dia (6kg / sq.cm) | 25 | RM | 306
|  | 75mm dia (6kg / sq.cm) | 20 | RM | 407
|  | 110mm dia (6 kg / sq.cm) | 20 | RM | 557
56 | MR | Providing and fixing PVC floor trap self cleansing design with or without vent arm complete including cutting and making good the walls and floors. Make:Supreme,Finolex,Prince etc.., | 2 | Each | 519
|  | 110mm dia inlet 110mm dia outlet |  |  |  | 0 |  | 2
58 | LMR | Providing and fixing C.P. brass pillar cock (push type)approved quality conforming to IS standards and weighing not less than 690 gms.: 15 mm nominal bore for wash basins: Make:Jauqar, Hindware, Parryware, crome | 2 | Each | 2706 |  |  | 3 | nos
61 | LMR | Providing and fixing poly carbonate (multi wall 6mm or nearest size) sheet roofing of approved make and quality fixed with polymer coated J or L hooks, bolts and nuts of required diameter with necessary washers complete including the cost of M.S square tube 50x25mm 16 gauge fixed with MS flat 25x6mm including necessary nuts and bolts to support the roofing,painting witn two or more coatswaithsyntheticenamel paint over a priming coat of Zinchromate primer etc complete. | 6.22 | Sqm | 2785.59
63 | LMR | WALL PANEL for acoustic treatment - -Supply and fixing of Keiler/equivalent make 6 mm Polyester Fiber panel, fixed on GI Channel filled with 48kg/ dencityx 50 mm thick rock wool backing with black fleece cloth of 120 GSM. | 55.8885 | sqm | 5450
64 | LMR | Supplying and fixing white board(3x1.50m) with necessary arrangements | 4.5 |  | 1500
65 | LMR | Supply and installation of DCP type fire extinguisher of 6 kg. Capacity complete with initial charges and installation brackets complete with installation brackets with ISI mark IS:15638 | 1 | Each |  | 2800
|  | TOTAL(PART-A) |  |  |  | 0 | 0

## civil-+ELEab (6) (hidden)
ESTIMATE FOR CIVILWORKS IN CONFERENCE HALL IN KAKKANADU FACTORY,COCHIN-PART-A
Item no. | DSR | Item Description | Qty | Unit | Rate | Rate+CI | Amount
CIVIL WORKS(PART-A)
36 | MR | Providing and fixing arrangement and making necessary holes etc. for fixing required door fitings, all complete as per direction of Engineer-in-charge Door handle, lock and stopper etc. | 6 | Each | 126 |  | 756
45 | LMR | Providing and fixing wash basin (counter type) with CI / MS brackets, 15mm CP brass Pillar taps, 32mm CP brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever required.: White Vitreous China Wash basin size 630 x 450mm with a single 15mm C.P brass piller tap. Make:Hindware,Cera,Jaquar etc.., (Lowest retail price of basin not less than Rs. 3000/each and Pillar tap not less than Rs. 2000/each. Materials to be selected by the Engineer in charge) | 2 | Each | 6732.75 |  | 13465.5
46 | M.R | Providing and fixing white vitreous china Wall Mounted type water closet (European type W.C.pan) with seat and lid, 3/6 litre low level white vitrous Dual Flushing cistern and C.P flush bend with fitting and C.I brackets, 40mm flush bend, overflow arrangement with specials of standard make and mosquito proof coupling of approved municipal design complete including painting of fittings and brackets, cutting and making good the walls and floors wherever required. Make:Hindware,Cera,Jaquar etc.., WC pan with ISI marked white solid plastic seat and lid (Lowest retail price not less than 10,000/each. Materials to be selected by the Engineer in charge) | 2 | Each | 13797.5 |  | 27595
47 | LMR | Providing and fixing C.P. brass long body bib cock of (2 in 1 type)approved quality conforming to IS standards and weighing not less than 690 gms.: 15 mm nominal bore: Make:Jauqar, Hindware, Parryware, crome | 2 | Each | 1540 |  | 3080 | 2 | nos
53 | LMR | Providing & fixing of CP Health faucet. Hand operated spray unit( Instand type)).Make:Jauqar, Hindware, Parryware, crome., (Lowest retail price not less than 1200/each. Materials to be selected by the Engineer in charge) | 2 | Each | 2043 |  | 4086 | 2
54 | LMR | Providing and fixing PVC pipes for water supply arrangements including cost pipes, fittings, solvent cement,testing of pipes, labour charges etc complete : Concealed work including cutting chases and making good the wall etc |  |  |  | 0 | 0
|  | 20mm nominal outer dia .Pipes. (10kg/cm2) | 20 | RM | 220 |  | 4400
|  | 32mm nominal outer dia .Pipes. (10kg/cm2) | 20 | RM | 236 |  | 4720
55 | LMR | Providing and fixing PVC soil, waste and vent pipe to IS : 13592 of SWR quality, including all fittings, like EG : Bends, Tees, Elbows, Collars, junction, inspection doors, cowls, offsets, access pipes, jointing with rubber ring / solvent cement by application of leak proof adhesive like FRP paste including cutting holes in walls and floors and making good. Make: Supreme, Finolex, Astral |  |  |  | 0 | 0
|  | 50mm dia (6kg / sq.cm) | 20 | RM | 260.45 |  | 5209
|  | 63mm dia (6kg / sq.cm) | 25 | RM | 306 |  | 7650
|  | 75mm dia (6kg / sq.cm) | 20 | RM | 407 |  | 8140
|  | 110mm dia (6 kg / sq.cm) | 20 | RM | 557 |  | 11140
58 | MR | Providing and fixing PVC floor trap self cleansing design with or without vent arm complete including cutting and making good the walls and floors. Make:Supreme,Finolex,Prince etc.., | 2 | Each | 519 |  | 1038
|  | 110mm dia inlet 110mm dia outlet |  |  |  | 0 | 0 | 2
60 | LMR | Providing and fixing C.P. brass pillar cock (push type)approved quality conforming to IS standards and weighing not less than 690 gms.: 15 mm nominal bore for wash basins: Make:Jauqar, Hindware, Parryware, crome | 2 | Each | 2706 |  | 5412 | 3 | nos
63 | LMR | Providing and fixing poly carbonate (multi wall 6mm or nearest size) sheet roofing of approved make and quality fixed with polymer coated J or L hooks, bolts and nuts of required diameter with necessary washers complete including the cost of M.S square tube 50x25mm 16 gauge fixed with MS flat 25x6mm including necessary nuts and bolts to support the roofing,painting witn two or more coatswaithsyntheticenamel paint over a priming coat of Zinchromate primer etc complete. | 6.22 | Sqm | 2785.59 |  | 17326.3698
65 | LMR | WALL PANEL for acoustic treatment - -Supply and fixing of Keiler/equivalent make 6 mm Polyester Fiber panel, fixed on GI Channel filled with 48kg/ dencityx 50 mm thick rock wool backing with black fleece cloth of 120 GSM. | 64.955 | sqm | 5400 |  | 350757 |  |  | 984046.9406
66 | LMR | Supplying and fixing white board(3x1.50m) with necessary arrangements | 4.5 | sqm | 1500 |  | 6750
67 | LMR | Supply and installation of DCP type fire extinguisher of 6 kg. Capacity complete with initial charges and installation brackets complete with installation brackets with ISI mark IS:15638 | 1 | Each | 2800 |  | 2800
|  | TOTAL(PART-A) |  |  |  | 0 | 474324.8698 | 217104.12 |  | 2171014.12
LMR ITEMS
1 |  | Surface mounted Indoor,decorative box type fitting, Retro LED cat ref. LTT8-20 with 20W LED Lamp having high efficiency PMMA diffuser giving soft glare free light of Crompton or Equi | 9 | Each | 3278 |  | 29502
2 |  | Recess down lighter DN194B LED15S of Philips/Equi with lamp | 8 | Each | 2904 |  | 23232
3 |  | Supply of Green square down lighter recessed BBS175 1xDLED of Philips or Equi with Lamp | 4 | Each | 1992 |  | 7968
4 |  | Supply of Recess mounted full glow RC170B LED 29S of Philips or Equi with lamp | 8 | Each | 4646 |  | 37168
5 |  | Supply & installation of LED Lamp Non Dimmable 7/9W B22 on existing angle batten | 2 | Each | 545 |  | 1090
6 |  | Supply of Linnet - LCL-10-CDL,Sleek LED mirror light,with high out put diffuser, 2 feet size of Crompton or Equi | 1 | Each | 2091 |  | 2091
7 |  | Supply of Indoor down lighter,recessed mounted LED down lights with the option for fixed/ adjustable and spot options. BBS312 1xDLED of Philips or Equi | 6 | Each | 2788 |  | 16728
8 |  | Supply & Installation of LED strip light for indoor with driver, Beetle cat ref. LST20RGB of crompton or equi of 5 meter length | 6 | set | 3336 |  | 20016
9 |  | Supply of ceiling fan 1050/1200 mm sweep,230V,1Ph, complete with double ball bearing, motor blades, down rods, canopy, capacitor etc complete as required 5 star rating (Crompton Riviera / Usha Maxx Air / Khaitan Newtec) | 8 | Each | 2180 |  | 17440
10 |  | Supply and installation of Decorative Wall fan 400 mm sweep, 230V.1Ph, complete with Openable mesh Cover ,string Operated etc as required. (Crompton WM Wind Flo / Usha Helix high speed / Khaitan Merlin Hi speed) | 6 | Each | 2698 |  | 16188
11 |  | Supply and fitting 250 mm sweep automatic shutter Sleek and stylish design type exhaust fan complete with louvers and cable from ceiling rose / connector to fan. (Usha Crisp Air / Crompton Crossair / Khaitan Vento). | 2 | Each | 1393 |  | 2786
12 |  | S/F PVC holder: Supplying and fixing PVC batten/ angle holder including connection etc. as required. | 2 | Each | 71 |  | 142
13 |  | Supply & fixing INFORMATION OUTLET WITH FACE PLATE (concealed in modular work station raceways /gypboard partitions/ walls-with modular back box), TERMINATION AND TESTING CAT6 A (AMP/PANDUIT/Systimax) | 10 | Each | 760 |  | 7600
14 |  | Supply of Alluminium cable. Supply of the following sizes of Alluminium armoured PVC insulated, XLPE Power cable of 1.1kV grade to site including transporting and stacking charges at work site.. |  |  |  |  | 0
a |  | 4 X 16 sq. mm | 30 | Metre | 315 |  | 9450
b |  | 4 X 10 sq. mm | 15 | Metre | 278 |  | 4170
15 |  | Supplying and drawing of UTP 4 pair CAT -6A LAN cable in existing surface/ recessed PVC conduit as required, AMP/Molex make | 300 | Metre | 77 |  | 23100
16 |  | S&F MCCB in cubicle Pannel: Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required. |  |  |  |  | 0
|  | 63 Amp, 16 KA TP MCCB | 1 | 1 | 6188 |  | 6188
DSR ITEMS
17 |  | Point wiring in PVC conduit, with Modular type switch: Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
a |  | Group B | 5 | Point | 585 | 846.846 | 4234.23
b |  | Group C | 32 | Point | 718 | 1039.3768 | 33260.0576
18 |  | Twin control point wiring in PVC conduit, with modular type switch: Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. | 2 | Point | 770 | 1114.652 | 2229.304 |  |  | 224859
19 |  | Power plug wiring in PVC conduit ( 2x4 sq mm ): Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 1 No 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 50 | Metre | 162 | 234.5112 | 11725.56
20 |  | Circuit Sub main wiring in PVC Conduit: Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required |  |  |  | 0 | 0
| a | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | 60 | Metre | 106 | 153.4456 | 9206.736
| b | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 80 | Metre | 131 | 189.6356 | 15170.848
| c | 4 X 4 sq. mm + 2 X 4 sq. mm earth wire | 25 | Metre | 275 | 398.09 | 9952.25
| d | 4 X 6 sq. mm + 2 X 6 sq. mm earth wire | 25 | Metre | 389 | 563.1164 | 14077.91
|  | RE- WIRING IN PVC CONDUIT |  |  |  | 0 | 0
21 |  | Telephone wiring in existing conduit: Supplying and drawing following pair 0.5 sq mm FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. |  |  |  | 0 | 0
|  | 2 Pair | 50 | Metre | 18 | 26.0568 | 1302.84
|  | PVC CONDUIT, METAL BOXES |  | Metre |  | 0 | 0
22 |  | S/F PVC conduit: Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. |  |  |  | 0 | 0
| a | 20 mm | 100 | Metre | 146 | 211.3496 | 21134.96
| b | 25 mm | 250 | Metre | 152 | 220.0352 | 55008.8
| c | 40 mm | 20 | Metre | 110 | 159.236 | 3184.72
23 |  | S/F Modular type switch/ socket: Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. |  |  |  | 0 | 0
| a | Telephone socket outlet | 2 | Each | 95 | 137.522 | 275.044
24 |  | Supplying and fixing electronic fan regulator: Supplying and fixing stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | 8 | Each | 284 | 411.1184 | 3288.9472
25 |  | S/F Modular type blanking plates: Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | 12 | Each | 23 | 33.2948 | 399.5376
26 |  | S/F Modular boxes, base & cover plate: Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required. |  |  |  | 0 | 0
| a | 1 or 2 Module (75mmX75mm) | 20 | Each | 166 | 240.3016 | 4806.032
27 |  | S/F light plug point modular type accessaries: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). | 16 | Each | 303 | 438.6228 | 7017.9648
28 |  | S/F Power plug point with modular type switch: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 2 | Each | 395 | 571.802 | 1143.604
29 |  | S/F Ceiling rose: Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. | 15 | Each | 43 | 62.2468 | 933.702
30 |  | S/F call bell/buzzer: Supplying and fixing call bell/ buzzer suitable for single phase, 230 volts, complete as required. | 2 | Each | 61 | 88.3036 | 176.6072
31 |  | ITC Fluroscent/LED fitting directly on surface/celing: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | 35 | Each | 91 | 131.7316 | 4610.606
32 |  | ITC Fluroscent fitting with down rod: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc., including supplying and fixing ball and socket arrangement, 2 no. down rods of 20 mm dia X 1.6 mm thick steel conduit upto 30 cm length, painting and wiring the down rods and connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | 8 | Each | 233 | 337.2908 | 2698.3264
33 |  | S/F extra down rod: Providing and fixing extra conduit down rod of 20 mm dia, 2 X 10 cm length wiring with 2 X 1.5 sq. mm FR PVC insulated, copper conductor, single core cable including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | 16 | Each | 31 | 44.8756 | 718.0096
34 |  | ITC Ceiling fan: Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable etc. as required. | 8 | Each | 95 | 137.522 | 1100.176
35 |  | Extra down rod 15 mm dia 20 CM Length: Supplying and fixing extra conduit down rod of 20 cm length G.I. pipe 15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | 24 | Each | 27 | 39.0852 | 938.0448
36 |  | ITC Exhaust fan: Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. |  |  |  | 0 | 0
|  | Upto 450 mm sweep | 2 | Each | 204 | 295.3104 | 590.6208
37 |  | S/F SP MCB DB: Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) |  |  |  | 0 | 0
|  | 2 + 6/8 way, Double door | 2 | Each | 1041 | 1506.9516 | 3013.9032
38 |  | S/F Vertical Type Pre Wired TP MCB DB: Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required ,suitable for MCCB incomer.(But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.) |  |  |  | 0 | 0
| 2.9.5 | 4 way Double door | 1 | Each | 7901 | 11437.4876 | 11437.4876
39 |  | S/F 'C' series, MCB: Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | 0 | 0
a |  | Single pole | 8 | Each | 169 | 244.6444 | 1957.1552
40 |  | S/F S P MCB blanking plate: Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | 10 | Each | 7 | 10.1332 | 101.332
41 |  | S/F DP MCB isolator: Supplying and fixing following rating, double pole, 240 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | 0 | 0
|  | 40 amps | 2 | Each | 218 | 315.5768 | 631.1536
42 |  | S/F SPN RCCB: Supplying and fixing following rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  | Each |  | 0 | 0
|  | 25 amps | 2 | Each | 1645 | 2381.302 | 4762.604
43 |  | S/F 20A SPN MCB industrial socket outlet: Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 2 | Each | 954 | 1381.0104 | 2762.0208
44 |  | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 1 | Each | 141 | 204.1116 | 204.1116
45 |  | G.I Earth Pipe Electrode With Salt & Charcoal: Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 2 | Each | 3926 | 5683.2776 | 11366.5552
46 |  | Providing and fixing 4.00mm dia copper wire on surface or in recess: Providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 60 | metre | 86 | 124.4936 | 7469.616
47 |  | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. |  |  |  | 0 | 0
|  | Upto 35 sq. mm | 35 | metre | 606 | 877.2456 | 30703.596
48 |  | Supplying and making end termination with brass compression gland and aluminium lugs: Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. |  |  |  | 0 | 0
| 9.1.32 | 4 X 10 sq. mm (25mm) | 2 | Each | 193 | 279.3868 | 558.7736
| 9.1.33 | 4 X 16 sq. mm (28mm) | 2 | Each | 245 | 354.662 | 709.324
|  | TOTAL FOR PART-B |  |  |  |  | 509722.0708

## DSR (hidden)
ESTIMATE FOR CIVILWORKS IN CONFERENCE HALL IN KAKKANADU FACTORY,COCHIN-PART-A
Item no. | DSR | Item Description | Qty | Unit | Rate | Amount
CIVIL WORKS(PART-A)
1 | 15.2.2 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material as per direction of Engineer-in-charge. | 10 | Cum | 550.5 | 5505
2 | 15.3 | Demolishing R.C.C. work manually/ by mechanical means includingstacking of steel bars and disposal of unserviceable material as per direction of Engineer - in- charge. | 1 | Cum | 1302.3 | 1302.3
3 | 15.5 | Extra for cutting reinforcement bars manually/ by mechanical means inR.C.C. or R.B. work (Payment shall be made on the cross sectional areaof R.C.C. or R.B. work) as per direction of Engineer -in -charge. | 30 | Sqm | 450.45 | 13513.5 | 30
4 | 15.23.1 | Dismantling tile work in floors, dadoing and roofs laid in cement mortar including stacking material within 50 metres lead.For thickness of tiles up to 25 mm | 25 | Sqm | 28.2 | 705
5 | 15.5 | Dismantling of Water closets/wash basin/flushing cistern etc. of all types (C.I./PVC/Vitrious China) including stacking of useful materials near the site and disposal of unserviceable materials | 2 | Each | 519.87 | 1039.74 | 2 | Nos
6 | 15.6 | Disposal of building rubbish / malba / similar unserviceable, dismantled or waste materials by mechanical means including loading, transporting, unloading to approved municipal dumping ground or as approved by Engineer-in-charge, beyond 50 m initial lead, for all loads including all lifts involved. | 40 | Cum | 123.7 | 4948
7 | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30cm in depth. 1.5m in width as well as 10 sqm on plan) including disposal of excavated earth and lift upto 1.5m, disposed earth to be levelled and neatly dressed.:All kinds of soil | 3.375 | Cum | 155.6 | 525.15
8 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All works up to plinth level-.1:4:8 (1 Cement : 4 coarse sand : 8 graded stone aggregate 40mm nominal size) | 7.6855 | Cum | 4301.2 | 33057.0016
9 | 5.1.3 | Providing and laying in position specified grade of reinforced cementconcrete, excluding the cost of centering, shuttering, finishing andreinforcement - All work up to plinth level :1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) | 0.52 | Cum | 5725.9 | 2977.468
10 | 5.3 | Reinforced cement concrete work in beams, suspended floors, roofs havingslope up to 15° landings, balconies, shelves, chajjas, lintels, bands, plainwindow sills, staircases and spiral stair cases up to floor five level, excludingthe cost of centering, shuttering, finishing and reinforcement, with 1:2:4 (1cement : 2 coarse sand : 4 graded stone aggregate 20 mmnominal size) | 1.6233 | Cum | 6778.2 | 11002.8487
11 | 5.37 | Providing and laying in position ready mixed M-25 grade concrete for reinforced cement concrete work, using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , excluding the cost of centering, shuttering finishing and reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, improve workability without impairing strength and durability as per direction of the Engineer - in - charge. |  |  |  | 0 | 0
|  | (Note :- Cement content considered in this item is @ 330 kg/cum. Excess/less cement used as per design mix is payable/recoverable separately). |  |  |  | 0 | 0
| 5.37.2 | All work above plinth level up to floor V level -RCC work (M25 concrete) | 22.3373 | Cum | 7363 | 164469.1938
12 | 5.9 | Centering and shuttering including strutting, propping etc., and removal of form for, |  |  |  | 0 | 0
12.a | 5.9.1 | Foundations, Footings, bases of columns,etc for mass concrete. | 2.25 | Sqm | 196.45 | 442.0125
12.b | 5.9.6 | Columns and Pillars, Piers, Abutments, Posts and Struts. | 64 | Sqm | 453.35 | 29014.4
12.c | 5.9.3 | Suspended floors, roofs, landings, Balconies and access platform | 103 | Sqm | 453.35 | 46695.05
12.d | 5.9.5 | Lintel,beams,plinth beams,girders,bressumers and cantilevers | 74 | Sqm | 332.15 | 24579.1
12.e | 5.9.19 | Weather shade, Chajjas, corbels etc., including edges | 15 | Sqm | 492.35 | 7385.25
13 | 5.22.A.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending,placing in position and binding all complete above plinth level. :Thermo-Mechanically Treated bars | 2203.5283 | Kg | 68.1 | 150060.2786
14 | 6.4.2 | Brick work with F.P.S bricks of class designation 5.0 in superstructure above plinth level up to floor v level in all shapes an sizes in: Cement mortar 1: 6 (1 cement :6 coarse sand) | 24.1605 | Cum | 5426.15 | 131098.693
15 | 6.13.1 | Half brick masonry with F.P.S brick of class designation 7.5 in superstructure above plinth level up to floor V level : CM 1:3 (1 cement : 3 coarse sand) | 28.88 | Sqm | 692.8 | 20008.064
16 | 6.15 | Extra for providing and placing in position 2 Nos. 6mm dia M.S bars at every third course of half brick masonry (with FPS brick) | 28.88 | Sqm | 69.5 | 2007.16
17 | 13.2.1 | 15mm cement plaster on the rough side of single or half brick wall of mix : 1 : 4 (1 cement : 4 fine sand) up to 10m height for external walls | 74 | Sqm | 189.4 | 14015.6
18 | 13.1.1 | 12mm cement plaster on the rough side of single or half brick wall of mix : 1 : 4 (1 cement : 4 fine sand) for internal walls, column and beams etc | 305.1168 | Sqm | 163.35 | 49840.8293
19 | 13.16.1 | 6 mm cement plaster of mix : 1:3 (1 cement: 3 fine sand) for ceiling plastering | 93.1392 | Sqm | 134.7 | 12545.8502
20 | 13.8 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. | 398.256 | Sqm | 89.65 | 35703.6504
21 | 13.60.1 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade –Two or more coats on new work.-internal walls | 398.256 | Sqm | 80.5 | 32059.608
22 | 13.48.1 | Finishing walls with Acrylic Smooth exterior paint of required shade : New work (Two or more coat applied @ 1.67 ltr/10 sqmover and including priming coat of exterior primer applied @ 2.20 kg/ 10 sqm) | 74 | Sqm | 100 | 7400
23 | 13.48.3 | Painting Steel work with Delux Multi surface paint to give an even shade.Two or more coat applied @ 0.90 ltr/10sqm over an over an under coat of primer applied @ 0.80ltr/10aqm of approved brand or manufacture. | 3.315 | Sqm | 90 | 298.35
24 | 8.2.2.2 | Providing and fixing 18mm thick gang saw cut mirror polished premoulded and prepolished) machine cut for kitchen platforms, vanity counters, window sills , facias and similar locations of required size of approved shade, colour and texture laid over 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels. Granite of any colour and shade: Area of slab over 0.50 sqm.: Lowest retail price not less than Rs. 2500.00/m2( Granite to be selected by the Engineer in charge) | 0.9 | Sqm | 2463.55 | 2217.195
25 | 9.117.1 | Providing and fixing factory made UPVC door frame made of UPVC extruded section having an overall dimensions as below ( tolerance ± 1mm ), with wall thickness 2.0mm (± 0.2mm), corners of the door frame to be joined with galvanized brackets and stainless steel screws, joints mitered and plastic welded. The hinged side vertical of the frames reinforced by galvanized M.S. tube of size 19x19 mm and 1mm (± 0.1mm) wall thickness and 3 nos. Stainless steel hinged fixed to the frame complete as per manufacturers Specification and direction of engineering -in-change : Extruded section profile size 48x40 mm | 6.72 | M | 213.75 | 1436.4
26 | 9.118.1 | Providing and fixing existing door frames: 24 mm thick factory made PVC door shutters made of styles and rails of a UPVC hollow section of size 59x24 mm and wall thickness 2 mm (± 0.2mm) with in built edging on both sides. The styles and rails mitered and joint at the corners by means of M.S. galvanized / plastic brackets of size 75x220 mm having wall thickness 1.0 mm and stainless steel screws. The styles of the shutter reinforced by inserting galvanized M.S. tube of size 20x20 mm and 1mm (± 0.1mm) wall thickness. The lock rail made up of " H" section, a UPVC hollow section of size 100x24 mm and 2mm (± 0.2mm) wall thickness, fixed to the shutters styles by means of plastic/ galvanized M.S.'U' cleats. The shutter frame filled with a UPVC multi chambered single panel of size not less than 620mm, having over all thickness of 20mm and 1mm (± 0.1mm) wall thickness. The panes filled vertically and tie bar at two places by inserting horizontally 6mm galvanized M.S. rod and fastened with nuts and washers, complete as per manufacturer's specification and direction of Engineer- in - charge. (for W,C and bath room door shutter). | 6.72 | Sqm | 2718.6 | 18268.992
27 | 11.41.2 | Providing and laying polished vitrified floor tile in different sizes (thickness to be specified by the manufacturer) with Acid and / or Alkali resistant tiles with water absorptions less than 0.08% and confirming to IS:15622 of approved make in all colours and shades, laid on 20mm thick cement mortor 1:4 (1 cement:4 Coard sand) including grouting the joints with white cement and matching pigments etc. complete. (Lowest retail price not less than Rs. 880/m2) : Size of Tiles 60 x 60 cm (Tiles to be selected by the Engineer in charge) | 68.9249 | sqm | 1405.95 | 96904.9632
28 | 11.39 | Providing and laying rectified Glazed Ceramic floor tiles 300x300 mm or more (thickness to be specified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make in colours White, Ivory, Grey, Fume Red Brown, laid on 20mm thick cement mortar 1:4 (1 Cement : 4 Coarse sand) including grouting the joints with white cement and matching pigments etc., complete.(lowest price of tile not less than 650/m2) | 6.4904 | sqm | 950.05 | 6166.2045
29 | 11.4 | Providing and fixing Ist quality ceramic glazed wall tiles of size 300x450mm conforming to IS : 15622 (thickness to be specified by the manufacturer ) of approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados over 12 mm thick bed of cement Mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm including pointing in white cement mixed with pigment of matching shade complete.(.(lowest price of tile not less than 725/m2) | 25 | sqm | 1009.6 | 25240
30 | 12.45 | Providing and fixing false ceiling at all height including providing and fixingof frame work made of special sections, power pressed from M.S. sheets and galvanized with zinc coating of 120 gms/sqm (both side inclusive) asper IS : 277 and consisting of angle cleats of size 25 mm wide x 1.6 mmthick with flanges of 27 mm and 37mm, at 1200 mm centre to centre, oneflange fixed to the ceiling with dash fastener 12.5 mm dia x 50mm long with6mm dia bolts, other flange of cleat fixed to the angle hangers of 25x10x0.50mm of required length with nuts & bolts of required size and other end ofangle hanger fixed with intermediate G.I. channels 45x15x0.9 mm runningat the spacing of 1200 mm centre to centre, to which the ceiling section0.5 mm thick bottom wedge of 80 mm with tapered flanges of 26 mm eachhaving lips of 10.5 mm, at 450 mm centre to centre, shall be fixed in adirection perpendicular to G.I. intermediate channel with connecting clipsmade out of 2.64 mm dia x 230 mm long G.I. wire at every junction, includingfixing perimeter channels 0.5 mm thick 27 mm high having flanges of 20mm and 30 mm long, the perimeter of ceiling fixed to wall/partition with the |  |  |  | 0
|  | help of rawl plugs at 450 mm centre, with 25mm long dry wall screws @230 mm interval, including fixing of gypsum board to ceiling section andperimeter channel with the help of dry wall screws of size 3.5 x 25 mm at230 mm c/c, including jointing and finishing to a flush finish of tapered andsquare edges of the board with recomme-nded jointing compound , |  |  |  | 0
| 12.45.1 | 12.5 mm thick tapered edge gypsum plain board conformingto IS: 2095- Part I | 48.1626 | sqm | 907.1 | 43688.2945 | #VALUE! | sqm
31 | 21.1.1.2 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) : For fixed portion: Powder coated aluminium (minimum thickness of powder coating 50 micron) | 115.83 | kg | 377.75 | 43754.7825
32 | 21.1.2.2 | For shutters of doors, windows & ventilators including providing and fixing hinges/ pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately). Powder coated aluminium (minimum thickness of powder coating 50 micron) | 75.6 | Kg | 435.75 | 32942.7
33 | 21.3.2 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.5 mm thickness | 15.12 | sqm | 1054.2 | 15939.504
34 | 21.8 | Filling the gap in between aluminium frame & adjacent RCC/Brick/Stone work by providing weather silicon sealant over backer rod of approved quality as per architectural drawings and direction of Enginner-in-charge complete. |  |  |  | 0
| 21.8.1 | Upto 5mm depth and 5mm width | 10 | Rm | 88.75 | 887.5
35 | 21.18 | Providing and fixing 12 mm thick frameless toughened glass door shutter of approved brand and manufacture, including providing and fixing top & bottom pivot & spring type fixing arrangement and making necessary holes etc. for fixing required door fitings, all complete as per direction of Engineer-in-charge ( Door handle, lock and stopper etc. to be paid separately) | 2.7 | Sqm | 4746.3 | 12815.01
37 | 9.83 | Providing and fixing aluminium die cast body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 35 kg and door width upto 700 mm) with necessary accessories and screws etc. complete. | 2 | Each | 753.75 | 1507.5
38 | 9.97 | Providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade with necessary screws etc., complete. |  |  |  | 0
| 9.97.2 | 250 x 10mm | 8 | Each | 95.25 | 762
| 9.97.4 | 150 x 10mm | 8 | Each | 65.35 | 522.8
39 | 21.13 | Providing and fixing 100mm brass locks (best make of approved quality) for aluminum doors including necessary cutting and making good etc. complete | 8 | Each | 418.65 | 3349.2
40 | 21.12.2 | Providing and fixing aluminium tubular handle bar 32 mm outer dia, 3.0 mm thick & 2100 mm long with SS screws etc .complete as per direction of Engineer-in-Charge. Powder coated minimum thickness 50 micron aluminium tubular handle bar. | 8 | Each | 508.55 | 4068.4
41 | 9.101 | Providing and fixing aluminium hanging floor door stopper ISI marked anodised (anodic coating note less than grade AC 10 as per IS : 1868) transparent or dyed to required colour and shade with necessary screws etc., complete. |  |  |  | 0
| 9.101.1 | Single rubber stopper | 3 | Each | 37.5 | 112.5
42 | 21.4 | Providing and fixing double action hydraulic floor spring of approved brand and manufacture IS : 6315 marked, for doors including cost of cutting floors as required, embedding in floors and cover plates with brass pivot and single piect M.S. sheet outer box with side plate etc., complete as per the direction of Engineer-in-charge. |  |  |  | 0
| 21.4.2 | With brass cover plate | 1 | Each | 2213.2 | 2213.2
43 | 9.149 | Providing and fixing casement handle made of zinc alloyed (white powder coated) for uPVC casement window with necessary screws etc. complete. | 4 | Each | 216.65 | 866.6
44 | 9.68.1 | Providing and fixing oxidised M.S. casement stays (straight peg type) with necessary screws etc. Complete-300 mm weighing not less than 200 gms | 8 | Each | 36.2 | 289.6
48 | 17.28.1.1 | Providing and fixing PVC Waste pipe for sink or wash basin including PVC waste fittings complete.:Semi rigid pipe 32mm dia | 2 | Each | 76.75 | 153.5 | 2 | nos
49 | 17.34.1 | Providing and fixing Toilet paper holder . Make:Hindware,Cera,Jaquar etc..,:C.P Brass | 1 | Each | 415.9 | 415.9 | 2 | nos
50 | 18.65 | Providing and fixing SS soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements. Weighing not less than 106 gms. | 1 | Each | 164.95 | 164.95 | 3 | nos
51 | 17.31 | Providing and fixing 600 x 450mm bevelled edge mirror of superior glass (of approved quality) complete with 6mm thick hard board ground fixed to wooden cleats with C.P. brass screws and washers complete. | 1 | Each | 793.95 | 793.95 | 1 | nos
52 | 17.73.2 | Providing and fixing SS towel rail complete with brackets fixed to wooden cleats with CP brass screws with concealed fitting arrangement of approved quality and colour. 600mm long towel rail with total length of 645mm, width 78mm and effective height of 88mm, weighing not less than 190gms. | 1 | Each | 541.5 | 541.5 | 3 | nos
56 | 18.77 | Cutting holes upto 15 x 15 cm in R.C.C. floors and roofs for passing drain pipe etc. and repairing the hole after insertion of drain pipe etc. with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) including finishing complete. | 1 | Each | 193 | 193
57 | 12.41.2 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A including jointing with seal ring conforming to IS : 5382 leaving 10 mm gap for thermal expansion.(i) Single socketed pipes. 110 mm diameter | 8 | RM | 231.65 | 1853.2
59 | 18.58.2.1 | Providing and fixing PTMT grating of approved quality and colour.:Rectangular type with openable circular lid.150 mm nominal size square 100 mm diameter of the inner hinged round grating | 3 | Each | 220.45 | 661.35
61 | 26.1 | Providing and supplying aluminium extruded tubular and other aluminium sections as per the architectural drawings and approved shop drawings , the aluminium quality as per grade 6063 T5 or T6 as per BS 1474,including super durable powder coating of 60-80 microns conforming to AAMA 2604 of required colour and shade as approved by the Engineer-in-Charge. ( The item includes cost of material such as cleats, sleeves, screws etc. necessary for fabrication of extruded aluminium frame work. Nothing extra shall be paid on this account). | 65 | Kg | 338.25 | 21986.25
62 | 26.2 | Designing, fabricating, testing, protection, installing and fixing in positionsemi (grid) unitized system of structural glazing (with open joints) for linearas well as curvilinear portions of the building for all heights and all levels,including:a) Structural analysis & design and preparation of shop drawings for thespecified design loads conforming to IS 875 part III (the system mustpassed the proof test at 1.5 times design wind pressure without anyfailure), including functional design of the aluminum sections for fixing glazing panels of various thicknesses, aluminium cleats, sleeves and c) Providing and filling, two part pump filled, structural silicone sealant and one part weather silicone sealant compatible with the structuralsilicone sealant of required bite size in a clean and controlled factory /work shop environment , including double sided spacer tape, setting blocks and backer rod, all of approved grade, brand and manufacture,as per the approved sealant design, within and all around the perimeterd) Providing and fixing in position flashings of solid aluminium sheet mm thick and of sizes, shapes and profiles, as required as per the site conditions, to seal the gap between the building structure and all its interfaces with curtain glazing to make it watertighte) Making provision for drainage of moisture/ water that enters the curtainglazing system to make it watertight, by incorporating principles of required), making necessary holes of required sizes and of requirednumbers etc. complete. This item includes cost of all inputs ofsplice plates etc. gaskets, screws, toggles, nuts, bolts, clamps etc., structural and weather silicone sealants, flashings, fire stop (barrier)-cum-smoke seals, microwave cured EPDM gaskets for water tightness, pressure equalisation & drainage and protection against fire hazardincluding:b) Fabricating and supplying serrated M.S. hot dip galvanised / Aluminiumalloy of 6005 T5 brackets of required sizes, sections and profiles etc.to accommodate 3 Dimentional movement for achieving perfectverticality and fixing structural glazing system rigidly to theRCC/masonry/structural steel framework of building structure using stainless steel anchor fasteners/ bolts, nylon seperator to prevent bimetallic contacts with nuts and washers etc. of stainless steel grade 316, of the required capacity and in required numbers | 9.38 | Sqm | 2556.2 | 23977.156
|  | installation of glazed units, T&P, scaffolding and other incidental charges including wastages etc., enabling temporary structures and services, cranes or cradles etc. as described above and as specified. The item includes the cost of getting all the structural and functional design including shop drawings checked by a structural designer, dully approved by Engineer-in-charge. The item also includes the cost of all mock ups at site, cost of all samples of the individual components for testing in an approved laboratory, field tests on the assembled working structural glazing as specified, cleaning and protection till the handing over of the building for occupation. In the end, the Contractor shall provide a water tight structural glazing having all the performance characteristics etc. all complete as required, as per the Architectural drawings, as per item description, as specified, as per the approved shop drawings and as directed by the Engineerin-Charge. |  |  |  | 0
|  | Note:- 1. The cost of providing extruded aluminium frames, shadow boxes, extruded aluminium section capping for fixing in the grooves of the curtain glazing and vermin proof stainless steel wire mesh shall be paid for separately under relevant items under this subhead. However, for the purpose of payment, only the actual area of structural glazing (including width of grooves ) on the external face shall be measured in sqm. up to two decimal places. Note:-2. The following performance test are to be conducted on structural glazing system if area of structural glazing exceeds 2500 Sqm from the certified laboratories accreditated by NABL(National Accreditation Board for Testing and Calibration Laboratories), Department of Science & Technologies, India. Cost of testing is payable separately. The NIT approving authority will decide the necessity of testing on the basis of cost of the work, cost of the test and importance of the work. Performance Testing of Structural glazing system Tests to be conducted in the NBL Certified laboratories |  |  |  | 0
64 | 10.2 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete: | 70 | Kg | 73.95 | 5176.5
|  | TOTAL(PART-A) |  |  |  | 1172069.6998 |  |  | 2171014.12
LMR ITEMS
1 |  | Surface mounted Indoor,decorative box type fitting, Retro LED cat ref. LTT8-20 with 20W LED Lamp having high efficiency PMMA diffuser giving soft glare free light of Crompton or Equi | 9 | Each | 3278 | 29502
2 |  | Recess down lighter DN194B LED15S of Philips/Equi with lamp | 8 | Each | 2904 | 23232
3 |  | Supply of Green square down lighter recessed BBS175 1xDLED of Philips or Equi with Lamp | 4 | Each | 1992 | 7968
4 |  | Supply of Recess mounted full glow RC170B LED 29S of Philips or Equi with lamp | 8 | Each | 4646 | 37168
5 |  | Supply & installation of LED Lamp Non Dimmable 7/9W B22 on existing angle batten | 2 | Each | 545 | 1090
6 |  | Supply of Linnet - LCL-10-CDL,Sleek LED mirror light,with high out put diffuser, 2 feet size of Crompton or Equi | 1 | Each | 2091 | 2091
7 |  | Supply of Indoor down lighter,recessed mounted LED down lights with the option for fixed/ adjustable and spot options. BBS312 1xDLED of Philips or Equi | 6 | Each | 2788 | 16728
8 |  | Supply & Installation of LED strip light for indoor with driver, Beetle cat ref. LST20RGB of crompton or equi of 5 meter length | 6 | set | 3336 | 20016
9 |  | Supply of ceiling fan 1050/1200 mm sweep,230V,1Ph, complete with double ball bearing, motor blades, down rods, canopy, capacitor etc complete as required 5 star rating (Crompton Riviera / Usha Maxx Air / Khaitan Newtec) | 8 | Each | 2180 | 17440
10 |  | Supply and installation of Decorative Wall fan 400 mm sweep, 230V.1Ph, complete with Openable mesh Cover ,string Operated etc as required. (Crompton WM Wind Flo / Usha Helix high speed / Khaitan Merlin Hi speed) | 6 | Each | 2698 | 16188
11 |  | Supply and fitting 250 mm sweep automatic shutter Sleek and stylish design type exhaust fan complete with louvers and cable from ceiling rose / connector to fan. (Usha Crisp Air / Crompton Crossair / Khaitan Vento). | 2 | Each | 1393 | 2786
12 |  | S/F PVC holder: Supplying and fixing PVC batten/ angle holder including connection etc. as required. | 2 | Each | 71 | 142
13 |  | Supply & fixing INFORMATION OUTLET WITH FACE PLATE (concealed in modular work station raceways /gypboard partitions/ walls-with modular back box), TERMINATION AND TESTING CAT6 A (AMP/PANDUIT/Systimax) | 10 | Each | 760 | 7600
14 |  | Supply of Alluminium cable. Supply of the following sizes of Alluminium armoured PVC insulated, XLPE Power cable of 1.1kV grade to site including transporting and stacking charges at work site.. |  |  |  | 0
a |  | 4 X 16 sq. mm | 30 | Metre | 315 | 9450
b |  | 4 X 10 sq. mm | 15 | Metre | 278 | 4170
15 |  | Supplying and drawing of UTP 4 pair CAT -6A LAN cable in existing surface/ recessed PVC conduit as required, AMP/Molex make | 300 | Metre | 77 | 23100
16 |  | S&F MCCB in cubicle Pannel: Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required. |  |  |  | 0
|  | 63 Amp, 16 KA TP MCCB | 1 | 1 | 6188 | 6188
DSR ITEMS
17 |  | Point wiring in PVC conduit, with Modular type switch: Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
a |  | Group B | 5 | Point | 585 | #VALUE!
b |  | Group C | 32 | Point | 718 | #VALUE!
18 |  | Twin control point wiring in PVC conduit, with modular type switch: Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. | 2 | Point | 770 | #VALUE! |  |  | 224859
19 |  | Power plug wiring in PVC conduit ( 2x4 sq mm ): Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 1 No 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 50 | Metre | 162 | #VALUE!
20 |  | Circuit Sub main wiring in PVC Conduit: Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required |  |  |  | #VALUE!
| a | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | 60 | Metre | 106 | #VALUE!
| b | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 80 | Metre | 131 | #VALUE!
| c | 4 X 4 sq. mm + 2 X 4 sq. mm earth wire | 25 | Metre | 275 | #VALUE!
| d | 4 X 6 sq. mm + 2 X 6 sq. mm earth wire | 25 | Metre | 389 | #VALUE!
|  | RE- WIRING IN PVC CONDUIT |  |  |  | #VALUE!
21 |  | Telephone wiring in existing conduit: Supplying and drawing following pair 0.5 sq mm FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. |  |  |  | #VALUE!
|  | 2 Pair | 50 | Metre | 18 | #VALUE!
|  | PVC CONDUIT, METAL BOXES |  | Metre |  | #VALUE!
22 |  | S/F PVC conduit: Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. |  |  |  | #VALUE!
| a | 20 mm | 100 | Metre | 146 | #VALUE!
| b | 25 mm | 250 | Metre | 152 | #VALUE!
| c | 40 mm | 20 | Metre | 110 | #VALUE!
23 |  | S/F Modular type switch/ socket: Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. |  |  |  | #VALUE!
| a | Telephone socket outlet | 2 | Each | 95 | #VALUE!
24 |  | Supplying and fixing electronic fan regulator: Supplying and fixing stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | 8 | Each | 284 | #VALUE!
25 |  | S/F Modular type blanking plates: Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | 12 | Each | 23 | #VALUE!
26 |  | S/F Modular boxes, base & cover plate: Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required. |  |  |  | #VALUE!
| a | 1 or 2 Module (75mmX75mm) | 20 | Each | 166 | #VALUE!
27 |  | S/F light plug point modular type accessaries: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). | 16 | Each | 303 | #VALUE!
28 |  | S/F Power plug point with modular type switch: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 2 | Each | 395 | #VALUE!
29 |  | S/F Ceiling rose: Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. | 15 | Each | 43 | #VALUE!
30 |  | S/F call bell/buzzer: Supplying and fixing call bell/ buzzer suitable for single phase, 230 volts, complete as required. | 2 | Each | 61 | #VALUE!
31 |  | ITC Fluroscent/LED fitting directly on surface/celing: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | 35 | Each | 91 | #VALUE!
32 |  | ITC Fluroscent fitting with down rod: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc., including supplying and fixing ball and socket arrangement, 2 no. down rods of 20 mm dia X 1.6 mm thick steel conduit upto 30 cm length, painting and wiring the down rods and connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | 8 | Each | 233 | #VALUE!
33 |  | S/F extra down rod: Providing and fixing extra conduit down rod of 20 mm dia, 2 X 10 cm length wiring with 2 X 1.5 sq. mm FR PVC insulated, copper conductor, single core cable including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | 16 | Each | 31 | #VALUE!
34 |  | ITC Ceiling fan: Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable etc. as required. | 8 | Each | 95 | #VALUE!
35 |  | Extra down rod 15 mm dia 20 CM Length: Supplying and fixing extra conduit down rod of 20 cm length G.I. pipe 15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | 24 | Each | 27 | #VALUE!
36 |  | ITC Exhaust fan: Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. |  |  |  | #VALUE!
|  | Upto 450 mm sweep | 2 | Each | 204 | #VALUE!
37 |  | S/F SP MCB DB: Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) |  |  |  | #VALUE!
|  | 2 + 6/8 way, Double door | 2 | Each | 1041 | #VALUE!
38 |  | S/F Vertical Type Pre Wired TP MCB DB: Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required ,suitable for MCCB incomer.(But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.) |  |  |  | #VALUE!
| 2.9.5 | 4 way Double door | 1 | Each | 7901 | #VALUE!
39 |  | S/F 'C' series, MCB: Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | #VALUE!
a |  | Single pole | 8 | Each | 169 | #VALUE!
40 |  | S/F S P MCB blanking plate: Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | 10 | Each | 7 | #VALUE!
41 |  | S/F DP MCB isolator: Supplying and fixing following rating, double pole, 240 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | #VALUE!
|  | 40 amps | 2 | Each | 218 | #VALUE!
42 |  | S/F SPN RCCB: Supplying and fixing following rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  | Each |  | #VALUE!
|  | 25 amps | 2 | Each | 1645 | #VALUE!
43 |  | S/F 20A SPN MCB industrial socket outlet: Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 2 | Each | 954 | #VALUE!
44 |  | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 1 | Each | 141 | #VALUE!
45 |  | G.I Earth Pipe Electrode With Salt & Charcoal: Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 2 | Each | 3926 | #VALUE!
46 |  | Providing and fixing 4.00mm dia copper wire on surface or in recess: Providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 60 | metre | 86 | #VALUE!
47 |  | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. |  |  |  | #VALUE!
|  | Upto 35 sq. mm | 35 | metre | 606 | #VALUE!
48 |  | Supplying and making end termination with brass compression gland and aluminium lugs: Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. |  |  |  | #VALUE!
| 9.1.32 | 4 X 10 sq. mm (25mm) | 2 | Each | 193 | #VALUE!
| 9.1.33 | 4 X 16 sq. mm (28mm) | 2 | Each | 245 | #VALUE!
|  | TOTAL FOR PART-B |  |  |  | #VALUE!

## ab (hidden)
ABSTRACT FOR CIVIL&ELECTRICAL WORKS FOR SETTING UP OF CONFERENCE HALL AT KAKKANAD FACTORY,COCHIN
Item no. | Description | Amount
1 | CIVIL WORKS(PART-A)
2 | ELECTRICAL WORKS(PART-B)
| GRAND TOTAL(PART-A+B) |  | 30

## sc-civil
SCHEDULE FOR CIVIL WORKS FOR SETTING UP OF CONFERENCE HALL AT KAKKANADU FACTORY,COCHIN
Item no. | DSR | Item Description | Qty | Unit | Rate | Amount
PART-A( CIVIL WORKS)
1 | 15.2.2 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material as per direction of Engineer-in-charge. | 10 | Cum
2 | 15.3 | Demolishing R.C.C. work manually/ by mechanical means includingstacking of steel bars and disposal of unserviceable material as per direction of Engineer - in- charge. | 1 | Cum
3 | 15.5 | Extra for cutting reinforcement bars manually/ by mechanical means inR.C.C. or R.B. work (Payment shall be made on the cross sectional areaof R.C.C. or R.B. work) as per direction of Engineer -in -charge. | 30 | Sqm |  |  | 30
4 | 15.23.1 | Dismantling tile work in floors, dadoing and roofs laid in cement mortar including stacking material within 50 metres lead.For thickness of tiles up to 25 mm | 25 | Sqm
5 | 15.5 | Dismantling of Water closets/wash basin/flushing cistern etc. of all types (C.I./PVC/Vitrious China) including stacking of useful materials near the site and disposal of unserviceable materials | 2 | Each |  |  | 2 | Nos
6 | 15.6 | Disposal of building rubbish / malba / similar unserviceable, dismantled or waste materials by mechanical means including loading, transporting, unloading to approved municipal dumping ground or as approved by Engineer-in-charge, beyond 50 m initial lead, for all loads including all lifts involved. | 40 | Cum
7 | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30cm in depth. 1.5m in width as well as 10 sqm on plan) including disposal of excavated earth and lift upto 1.5m, disposed earth to be levelled and neatly dressed.:All kinds of soil | 3.375 | Cum
8 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All works up to plinth level-.1:4:8 (1 Cement : 4 coarse sand : 8 graded stone aggregate 40mm nominal size) | 7.6855 | Cum
9 | 5.1.3 | Providing and laying in position specified grade of reinforced cementconcrete, excluding the cost of centering, shuttering, finishing andreinforcement - All work up to plinth level :1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) | 0.52 | Cum
10 | 5.3 | Reinforced cement concrete work in beams, suspended floors, roofs havingslope up to 15° landings, shades balconies, shelves, chajjas, lintels, bands, plainwindow sills, staircases and spiral stair cases up to floor five level, excludingthe cost of centering, shuttering, finishing and reinforcement, with 1:2:4 (1cement : 2 coarse sand : 4 graded stone aggregate 20 mmnominal size) | 1.6233 | Cum
11 | 5.37 | Providing and laying in position ready mixed M-25 grade concrete for reinforced cement concrete work, using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , excluding the cost of centering, shuttering finishing and reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, improve workability without impairing strength and durability as per direction of the Engineer - in - charge. |  |  |  |  | 0
|  | (Note :- Cement content considered in this item is @ 330 kg/cum. Excess/less cement used as per design mix is payable/recoverable separately). |  |  |  |  | 0
| 5.37.2 | All work above plinth level up to floor V level -RCC work (M25 concrete) | 22.3373 | Cum
12 | 5.9 | Centering and shuttering including strutting, propping etc., and removal of form for, |  |  |  |  | 0
12.a | 5.9.1 | Foundations, Footings, bases of columns,etc for mass concrete. | 2.25 | Sqm
12.b | 5.9.6 | Columns and Pillars, Piers, Abutments, Posts and Struts. | 64 | Sqm
12.c | 5.9.3 | Suspended floors, roofs, landings, Balconies and access platform | 103 | Sqm
12.d | 5.9.5 | Lintel,beams,plinth beams,girders,bressumers and cantilevers | 74 | Sqm
12.e | 5.9.19 | Weather shade, Chajjas, corbels etc., including edges | 15 | Sqm
13 | 5.22.A.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending,placing in position and binding all complete above plinth level. :Thermo-Mechanically Treated bars | 2203.5283 | Kg
14 | 6.4.2 | Brick work with F.P.S bricks of class designation 5.0 in superstructure above plinth level up to floor v level in all shapes an sizes in: Cement mortar 1: 6 (1 cement :6 coarse sand) | 24.1605 | Cum
15 | 6.13.1 | Half brick masonry with F.P.S brick of class designation 7.5 in superstructure above plinth level up to floor V level : CM 1:3 (1 cement : 3 coarse sand) | 28.88 | Sqm
16 | 6.15 | Extra for providing and placing in position 2 Nos. 6mm dia M.S bars at every third course of half brick masonry (with FPS brick) | 28.88 | Sqm
17 | 13.2.1 | 15mm cement plaster on the rough side of single or half brick wall of mix : 1 : 4 (1 cement : 4 fine sand) up to 10m height for external walls | 74 | Sqm
18 | 13.1.1 | 12mm cement plaster on the rough side of single or half brick wall of mix : 1 : 4 (1 cement : 4 fine sand) for internal walls, column and beams etc | 305.1168 | Sqm
19 | 13.16.1 | 6 mm cement plaster of mix : 1:3 (1 cement: 3 fine sand) for ceiling plastering | 93.1392 | Sqm
20 | 13.8 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. | 398.256 | Sqm
21 | 13.60.1 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade –Two or more coats on new work.-internal walls | 398.256 | Sqm
22 | 13.48.1 | Finishing walls with Acrylic Smooth exterior paint of required shade : New work (Two or more coat applied @ 1.67 ltr/10 sqmover and including priming coat of exterior primer applied @ 2.20 kg/ 10 sqm) | 74 | Sqm
23 | 13.48.3 | Painting Steel work with Delux Multi surface paint to give an even shade.Two or more coat applied @ 0.90 ltr/10sqm over an over an under coat of primer applied @ 0.80ltr/10aqm of approved brand or manufacture. | 3.315 | Sqm
24 | 8.2.2.2 | Providing and fixing 18mm thick gang saw cut mirror polished premoulded and prepolished) machine cut for kitchen platforms, vanity counters, window sills , facias and similar locations of required size of approved shade, colour and texture laid over 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels. Granite of any colour and shade: Area of slab over 0.50 sqm.: Lowest retail price not less than Rs. 2500.00/m2( Granite to be selected by the Engineer in charge) | 0.9 | Sqm
25 | 9.117.1 | Providing and fixing factory made UPVC door frame made of UPVC extruded section having an overall dimensions as below ( tolerance ± 1mm ), with wall thickness 2.0mm (± 0.2mm), corners of the door frame to be joined with galvanized brackets and stainless steel screws, joints mitered and plastic welded. The hinged side vertical of the frames reinforced by galvanized M.S. tube of size 19x19 mm and 1mm (± 0.1mm) wall thickness and 3 nos. Stainless steel hinged fixed to the frame complete as per manufacturers Specification and direction of engineering -in-change : Extruded section profile size 48x40 mm | 6.72 | M
26 | 9.118.1 | Providing and fixing existing door frames: 24 mm thick factory made PVC door shutters made of styles and rails of a UPVC hollow section of size 59x24 mm and wall thickness 2 mm (± 0.2mm) with in built edging on both sides. The styles and rails mitered and joint at the corners by means of M.S. galvanized / plastic brackets of size 75x220 mm having wall thickness 1.0 mm and stainless steel screws. The styles of the shutter reinforced by inserting galvanized M.S. tube of size 20x20 mm and 1mm (± 0.1mm) wall thickness. The lock rail made up of " H" section, a UPVC hollow section of size 100x24 mm and 2mm (± 0.2mm) wall thickness, fixed to the shutters styles by means of plastic/ galvanized M.S.'U' cleats. The shutter frame filled with a UPVC multi chambered single panel of size not less than 620mm, having over all thickness of 20mm and 1mm (± 0.1mm) wall thickness. The panes filled vertically and tie bar at two places by inserting horizontally 6mm galvanized M.S. rod and fastened with nuts and washers, complete as per manufacturer's specification and direction of Engineer- in - charge. (for W,C and bath room door shutter). | 6.72 | Sqm
27 | 11.41.2 | Providing and laying polished vitrified floor tile in different sizes (thickness to be specified by the manufacturer) with Acid and / or Alkali resistant tiles with water absorptions less than 0.08% and confirming to IS:15622 of approved make in all colours and shades, laid on 20mm thick cement mortor 1:4 (1 cement:4 Coard sand) including grouting the joints with white cement and matching pigments etc. complete. (Lowest retail price not less than Rs. 880/m2) : Size of Tiles 60 x 60 cm (Tiles to be selected by the Engineer in charge) | 68.9249 | sqm
28 | 11.39 | Providing and laying rectified Glazed Ceramic floor tiles 300x300 mm or more (thickness to be specified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make in colours White, Ivory, Grey, Fume Red Brown, laid on 20mm thick cement mortar 1:4 (1 Cement : 4 Coarse sand) including grouting the joints with white cement and matching pigments etc., complete.(lowest price of tile not less than 650/m2) | 6.4904 | sqm
29 | 11.4 | Providing and fixing Ist quality ceramic glazed wall tiles of size 300x450mm conforming to IS : 15622 (thickness to be specified by the manufacturer ) of approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados over 12 mm thick bed of cement Mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm including pointing in white cement mixed with pigment of matching shade complete.(.(lowest price of tile not less than 725/m2) | 25 | sqm
30 | 12.45 | Providing and fixing false ceiling at all height including providing and fixingof frame work made of special sections, power pressed from M.S. sheets and galvanized with zinc coating of 120 gms/sqm (both side inclusive) asper IS : 277 and consisting of angle cleats of size 25 mm wide x 1.6 mmthick with flanges of 27 mm and 37mm, at 1200 mm centre to centre, oneflange fixed to the ceiling with dash fastener 12.5 mm dia x 50mm long with6mm dia bolts, other flange of cleat fixed to the angle hangers of 25x10x0.50mm of required length with nuts & bolts of required size and other end ofangle hanger fixed with intermediate G.I. channels 45x15x0.9 mm runningat the spacing of 1200 mm centre to centre, to which the ceiling section0.5 mm thick bottom wedge of 80 mm with tapered flanges of 26 mm eachhaving lips of 10.5 mm, at 450 mm centre to centre, shall be fixed in adirection perpendicular to G.I. intermediate channel with connecting clipsmade out of 2.64 mm dia x 230 mm long G.I. wire at every junction, includingfixing perimeter channels 0.5 mm thick 27 mm high having flanges of 20mm and 30 mm long, the perimeter of ceiling fixed to wall/partition with the
help of rawl plugs at 450 mm centre, with 25mm long dry wall screws @230 mm interval, including fixing of gypsum board to ceiling section andperimeter channel with the help of dry wall screws of size 3.5 x 25 mm at230 mm c/c, including jointing and finishing to a flush finish of tapered andsquare edges of the board with recomme-nded jointing compound ,
| 12.45.1 | 12.5 mm thick tapered edge gypsum plain board conformingto IS: 2095- Part I | 48.1626 | sqm |  |  | #VALUE! | sqm
31 | 21.1.1.2 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) : For fixed portion: Powder coated aluminium (minimum thickness of powder coating 50 micron) | 115.83 | kg
32 | 21.1.2.2 | For shutters of doors, windows & ventilators including providing and fixing hinges/ pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately). Powder coated aluminium (minimum thickness of powder coating 50 micron) | 75.6 | Kg
33 | 21.3.2 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.5 mm thickness | 15.12 | sqm
34 | 21.8 | Filling the gap in between aluminium frame & adjacent RCC/Brick/Stone work by providing weather silicon sealant over backer rod of approved quality as per architectural drawings and direction of Enginner-in-charge complete.
| 21.8.1 | Upto 5mm depth and 5mm width | 10 | Rm
35 | 21.18 | Providing and fixing 12 mm thick frameless toughened glass door shutter of approved brand and manufacture, including providing and fixing top & bottom pivot & spring type fixing arrangement and making necessary holes etc. for fixing required door fitings, all complete as per direction of Engineer-in-charge ( Door handle, lock and stopper etc. to be paid separately) | 2.7 | Sqm
36 | MR | Providing and fixing arrangement and making necessary holes etc. for fixing required door fitings, all complete as per direction of Engineer-in-charge Door handle, lock and stopper etc. | 6 | Each
37 | 9.83 | Providing and fixing aluminium die cast body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 35 kg and door width upto 700 mm) with necessary accessories and screws etc. complete. | 2 | Each
38 | 9.97 | Providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade with necessary screws etc., complete.
| 9.97.2 | 250 x 10mm | 8 | Each
| 9.97.4 | 150 x 10mm | 8 | Each
39 | 21.13 | Providing and fixing 100mm brass locks (best make of approved quality) for aluminum doors including necessary cutting and making good etc. complete | 8 | Each
40 | 21.12.2 | Providing and fixing aluminium tubular handle bar 32 mm outer dia, 3.0 mm thick & 2100 mm long with SS screws etc .complete as per direction of Engineer-in-Charge. Powder coated minimum thickness 50 micron aluminium tubular handle bar. | 8 | Each
41 | 9.101 | Providing and fixing aluminium hanging floor door stopper ISI marked anodised (anodic coating note less than grade AC 10 as per IS : 1868) transparent or dyed to required colour and shade with necessary screws etc., complete.
| 9.101.1 | Single rubber stopper | 3 | Each
42 | 21.4 | Providing and fixing double action hydraulic floor spring of approved brand and manufacture IS : 6315 marked, for doors including cost of cutting floors as required, embedding in floors and cover plates with brass pivot and single piect M.S. sheet outer box with side plate etc., complete as per the direction of Engineer-in-charge.
| 21.4.2 | With brass cover plate | 1 | Each
43 | 9.149 | Providing and fixing casement handle made of zinc alloyed (white powder coated) for uPVC casement window with necessary screws etc. complete. | 4 | Each
44 | 9.68.1 | Providing and fixing oxidised M.S. casement stays (straight peg type) with necessary screws etc. Complete-300 mm weighing not less than 200 gms | 8 | Each
45 | LMR | Providing and fixing wash basin (counter type) with CI / MS brackets, 15mm CP brass Pillar taps, 32mm CP brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever required.: White Vitreous China Wash basin size 630 x 450mm with a single 15mm C.P brass piller tap. Make:Hindware,Cera,Jaquar etc.., (Lowest retail price of basin not less than Rs. 3000/each and Pillar tap not less than Rs. 2000/each. Materials to be selected by the Engineer in charge) | 2 | Each
46 | M.R | Providing and fixing white vitreous china Wall Mounted type water closet (European type W.C.pan) with seat and lid, 3/6 litre low level white vitrous Dual Flushing cistern and C.P flush bend with fitting and C.I brackets, 40mm flush bend, overflow arrangement with specials of standard make and mosquito proof coupling of approved municipal design complete including painting of fittings and brackets, cutting and making good the walls and floors wherever required. Make:Hindware,Cera,Jaquar etc.., WC pan with ISI marked white solid plastic seat and lid (Lowest retail price not less than 10,000/each. Materials to be selected by the Engineer in charge) | 2 | Each
47 | LMR | Providing and fixing C.P. brass long body bib cock of (2 in 1 type)approved quality conforming to IS standards and weighing not less than 690 gms.: 15 mm nominal bore: Make:Jauqar, Hindware, Parryware, crome | 2 | Each |  |  | 2 | nos
48 | 17.28.1.1 | Providing and fixing PVC Waste pipe for sink or wash basin including PVC waste fittings complete.:Semi rigid pipe 32mm dia | 2 | Each |  |  | 2 | nos
49 | 17.34.1 | Providing and fixing Toilet paper holder . Make:Hindware,Cera,Jaquar etc..,:C.P Brass | 1 | Each |  |  | 2 | nos
50 | 18.65 | Providing and fixing SS soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements. Weighing not less than 106 gms. | 1 | Each |  |  | 3 | nos
51 | 17.31 | Providing and fixing 600 x 450mm bevelled edge mirror of superior glass (of approved quality) complete with 6mm thick hard board ground fixed to wooden cleats with C.P. brass screws and washers complete. | 1 | Each |  |  | 1 | nos
52 | 17.73.2 | Providing and fixing SS towel rail complete with brackets fixed to wooden cleats with CP brass screws with concealed fitting arrangement of approved quality and colour. 600mm long towel rail with total length of 645mm, width 78mm and effective height of 88mm, weighing not less than 190gms. | 1 | Each |  |  | 3 | nos
53 | LMR | Providing & fixing of CP Health faucet. Hand operated spray unit( Instand type)).Make:Jauqar, Hindware, Parryware, crome., (Lowest retail price not less than 1200/each. Materials to be selected by the Engineer in charge) | 2 | Each |  |  | 2
54 | LMR | Providing and fixing PVC pipes for water supply arrangements including cost pipes, fittings, solvent cement,testing of pipes, labour charges etc complete : Concealed work including cutting chases and making good the wall etc
|  | 20mm nominal outer dia .Pipes. (10kg/cm2) | 20 | RM
|  | 32mm nominal outer dia .Pipes. (10kg/cm2) | 20 | RM
55 | LMR | Providing and fixing PVC soil, waste and vent pipe to IS : 13592 of SWR quality, including all fittings, like EG : Bends, Tees, Elbows, Collars, junction, inspection doors, cowls, offsets, access pipes, jointing with rubber ring / solvent cement by application of leak proof adhesive like FRP paste including cutting holes in walls and floors and making good. Make: Supreme, Finolex, Astral
|  | 50mm dia (6kg / sq.cm) | 20 | RM
|  | 63mm dia (6kg / sq.cm) | 25 | RM
|  | 75mm dia (6kg / sq.cm) | 20 | RM
|  | 110mm dia (6 kg / sq.cm) | 20 | RM
56 | 18.77 | Cutting holes upto 15 x 15 cm in R.C.C. floors and roofs for passing drain pipe etc. and repairing the hole after insertion of drain pipe etc. with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) including finishing complete. | 1 | Each
57 | 12.41.2 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A including jointing with seal ring conforming to IS : 5382 leaving 10 mm gap for thermal expansion.(i) Single socketed pipes. 110 mm diameter | 8 | RM
58 | MR | Providing and fixing PVC floor trap self cleansing design with or without vent arm complete including cutting and making good the walls and floors. Make:Supreme,Finolex,Prince etc.., | 2 | Each
|  | 110mm dia inlet 110mm dia outlet |  |  |  |  | 2
59 | 18.58.2.1 | Providing and fixing PTMT grating of approved quality and colour.:Rectangular type with openable circular lid.150 mm nominal size square 100 mm diameter of the inner hinged round grating | 3 | Each
60 | LMR | Providing and fixing C.P. brass pillar cock (push type)approved quality conforming to IS standards and weighing not less than 690 gms.: 15 mm nominal bore for wash basins: Make:Jauqar, Hindware, Parryware, crome | 2 | Each |  |  | 3 | nos
61 | 26.1 | Providing and supplying aluminium extruded tubular and other aluminium sections as per the architectural drawings and approved shop drawings , the aluminium quality as per grade 6063 T5 or T6 as per BS 1474,including super durable powder coating of 60-80 microns conforming to AAMA 2604 of required colour and shade as approved by the Engineer-in-Charge. ( The item includes cost of material such as cleats, sleeves, screws etc. necessary for fabrication of extruded aluminium frame work. Nothing extra shall be paid on this account). | 65 | Kg
62 | 26.2 | Designing, fabricating, testing, protection, installing and fixing in positionsemi (grid) unitized system of structural glazing (with open joints) for linearas well as curvilinear portions of the building for all heights and all levels,including:a) Structural analysis & design and preparation of shop drawings for thespecified design loads conforming to IS 875 part III (the system mustpassed the proof test at 1.5 times design wind pressure without anyfailure), including functional design of the aluminum sections for fixing glazing panels of various thicknesses, aluminium cleats, sleeves and c) Providing and filling, two part pump filled, structural silicone sealant and one part weather silicone sealant compatible with the structuralsilicone sealant of required bite size in a clean and controlled factory /work shop environment , including double sided spacer tape, setting blocks and backer rod, all of approved grade, brand and manufacture,as per the approved sealant design, within and all around the perimeterd) Providing and fixing in position flashings of solid aluminium sheet mm thick and of sizes, shapes and profiles, as required as per the site conditions, to seal the gap between the building structure and all its interfaces with curtain glazing to make it watertighte) Making provision for drainage of moisture/ water that enters the curtainglazing system to make it watertight, by incorporating principles of required), making necessary holes of required sizes and of requirednumbers etc. complete. This item includes cost of all inputs ofsplice plates etc. gaskets, screws, toggles, nuts, bolts, clamps etc., structural and weather silicone sealants, flashings, fire stop (barrier)-cum-smoke seals, microwave cured EPDM gaskets for water tightness, pressure equalisation & drainage and protection against fire hazardincluding:b) Fabricating and supplying serrated M.S. hot dip galvanised / Aluminiumalloy of 6005 T5 brackets of required sizes, sections and profiles etc.to accommodate 3 Dimentional movement for achieving perfectverticality and fixing structural glazing system rigidly to theRCC/masonry/structural steel framework of building structure using stainless steel anchor fasteners/ bolts, nylon seperator to prevent bimetallic contacts with nuts and washers etc. of stainless steel grade 316, of the required capacity and in required numbers | 9.38 | Sqm
installation of glazed units, T&P, scaffolding and other incidental charges including wastages etc., enabling temporary structures and services, cranes or cradles etc. as described above and as specified. The item includes the cost of getting all the structural and functional design including shop drawings checked by a structural designer, dully approved by Engineer-in-charge. The item also includes the cost of all mock ups at site, cost of all samples of the individual components for testing in an approved laboratory, field tests on the assembled working structural glazing as specified, cleaning and protection till the handing over of the building for occupation. In the end, the Contractor shall provide a water tight structural glazing having all the performance characteristics etc. all complete as required, as per the Architectural drawings, as per item description, as specified, as per the approved shop drawings and as directed by the Engineerin-Charge.
Note:- 1. The cost of providing extruded aluminium frames, shadow boxes, extruded aluminium section capping for fixing in the grooves of the curtain glazing and vermin proof stainless steel wire mesh shall be paid for separately under relevant items under this subhead. However, for the purpose of payment, only the actual area of structural glazing (including width of grooves ) on the external face shall be measured in sqm. up to two decimal places. Note:-2. The following performance test are to be conducted on structural glazing system if area of structural glazing exceeds 2500 Sqm from the certified laboratories accreditated by NABL(National Accreditation Board for Testing and Calibration Laboratories), Department of Science & Technologies, India. Cost of testing is payable separately. The NIT approving authority will decide the necessity of testing on the basis of cost of the work, cost of the test and importance of the work. Performance Testing of Structural glazing system Tests to be conducted in the NBL Certified laboratories
63 | LMR | Providing and fixing poly carbonate (multi wall 6mm or nearest size) sheet roofing of approved make and quality fixed with polymer coated J or L hooks, bolts and nuts of required diameter with necessary washers complete including the cost of M.S square tube 50x25mm 16 gauge fixed with MS flat 25x6mm including necessary nuts and bolts to support the roofing,painting witn two or more coatswaithsyntheticenamel paint over a priming coat of Zinchromate primer etc complete. | 6.22 | Sqm
64 | 10.2 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete: | 70 | Kg
65 | LMR | WALL PANEL for acoustic treatment - -Supply and fixing of Keiler/equivalent make 6 mm Polyester Fiber panel, fixed on GI Channel filled with 48kg/ dencityx 50 mm thick rock wool backing with black fleece cloth of 120 GSM. | 64.955 | sqm |  |  |  |  | 509722.0708
66 | LMR | Supplying and fixing white board(3x1.50m) with necessary arrangements | 4.5 | sqm
|  | TOTAL(PART-A) |  |  |  |  | 217104.12 |  | 2171014.12

## civil-+ELEab -EL (hidden)
ESTIMATE FOR CIVILWORKS IN CONFERENCE HALL IN KAKKANADU FACTORY,COCHIN-PART-A
Item no. | DSR | Item Description | Qty | Unit | Rate | Rate+CI | Amount
CIVIL WORKS(PART-A)
1 | 15.2.2 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material as per direction of Engineer-in-charge. | 10 | Cum | 550.5 | 796.9038 | 7969.038
2 | 15.3 | Demolishing R.C.C. work manually/ by mechanical means includingstacking of steel bars and disposal of unserviceable material as per direction of Engineer - in- charge. | 1 | Cum | 1302.3 | 1885.2095 | 1885.2095
3 | 15.5 | Extra for cutting reinforcement bars manually/ by mechanical means inR.C.C. or R.B. work (Payment shall be made on the cross sectional areaof R.C.C. or R.B. work) as per direction of Engineer -in -charge. | 30 | Sqm | 450.45 | 652.0714 | 19562.1426 | 30
4 | 15.23.1 | Dismantling tile work in floors, dadoing and roofs laid in cement mortar including stacking material within 50 metres lead.For thickness of tiles up to 25 mm | 25 | Sqm | 28.2 | 40.8223 | 1020.558
5 | 15.5 | Dismantling of Water closets/wash basin/flushing cistern etc. of all types (C.I./PVC/Vitrious China) including stacking of useful materials near the site and disposal of unserviceable materials | 2 | Each | 519.87 | 752.5638 | 1505.1276 | 2 | Nos
6 | 15.6 | Disposal of building rubbish / malba / similar unserviceable, dismantled or waste materials by mechanical means including loading, transporting, unloading to approved municipal dumping ground or as approved by Engineer-in-charge, beyond 50 m initial lead, for all loads including all lifts involved. | 40 | Cum | 123.7 | 179.0681 | 7162.7248
7 | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30cm in depth. 1.5m in width as well as 10 sqm on plan) including disposal of excavated earth and lift upto 1.5m, disposed earth to be levelled and neatly dressed.:All kinds of soil | 3.375 | Cum | 155.6 | 225.2466 | 760.2071
8 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All works up to plinth level-.1:4:8 (1 Cement : 4 coarse sand : 8 graded stone aggregate 40mm nominal size) | #REF! | Cum | 4301.2 | 6226.4171 | #REF!
9 | 5.37 | Providing and laying in position ready mixed M-25 grade concrete for reinforced cement concrete work, using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , excluding the cost of centering, shuttering finishing and reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, improve workability without impairing strength and durability as per direction of the Engineer - in - charge. |  |  |  | 0 | 0 | 0
|  | (Note :- Cement content considered in this item is @ 330 kg/cum. Excess/less cement used as per design mix is payable/recoverable separately). |  |  |  | 0 | 0 | 0
| 5.37.2 | All work above plinth level up to floor V level -RCC work (M25 concrete) | 22.3373 | Cum | 7363 | 10658.6788 | 238085.605 | #VALUE!
10 | 5.9 | Centering and shuttering including strutting, propping etc., and removal of form for, |  |  |  | 0 | 0 | 0
10.a | 5.9.1 | Foundations, Footings, bases of columns,etc for mass concrete. | 2.25 | Sqm | 196.45 | 284.381 | 639.8573
10.a | 5.9.6 | Columns and Pillars, Piers, Abutments, Posts and Struts. | 64 | Sqm | 453.35 | 656.2695 | 42001.2454
10.b | 5.9.3 | Suspended floors, roofs, landings, Balconies and access platform | 103 | Sqm | 453.35 | 656.2695 | 67595.7544
10.c | 5.9.5 | Lintel,beams,plinth beams,girders,bressumers and cantilevers | 74 | Sqm | 332.15 | 480.8203 | 35580.7052
10.d | 5.9.19 | Weather shade, Chajjas, corbels etc., including edges | 15 | Sqm | 492.35 | 712.7259 | 10690.8879
11 | 5.22.A.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending,placing in position and binding all complete above plinth level. :Thermo-Mechanically Treated bars | 2203.5283 | Kg | 68.1 | 98.5816 | 217227.2593
12 | 6.4.2 | Brick work with F.P.S bricks of class designation 5.0 in superstructure above plinth level up to floor v level in all shapes an sizes in: Cement mortar 1: 6 (1 cement :6 coarse sand) | 24.1605 | Cum | 5426.15 | 7854.8947 | 189778.4679
13 | 6.13.1 | Half brick masonry with F.P.S brick of class designation 7.5 in superstructure above plinth level up to floor V level : CM 1:3 (1 cement : 3 coarse sand) | 28.88 | Sqm | 692.8 | 1002.8973 | 28963.6734
14 | 6.15 | Extra for providing and placing in position 2 Nos. 6mm dia M.S bars at every third course of half brick masonry (with FPS brick) | 28.88 | Sqm | 69.5 | 100.6082 | 2905.5648
15 | 13.2.1 | 15mm cement plaster on the rough side of single or half brick wall of mix : 1 : 4 (1 cement : 4 fine sand) up to 10m height for external walls | 74 | Sqm | 189.4 | 274.1754 | 20288.9826
16 | 13.1.1 | 12mm cement plaster on the rough side of single or half brick wall of mix : 1 : 4 (1 cement : 4 fine sand) for internal walls, column and beams etc | 305.1168 | Sqm | 163.35 | 236.4655 | 72149.5845
17 | 13.16.1 | 6 mm cement plaster of mix : 1:3 (1 cement: 3 fine sand) for ceiling plastering | 93.1392 | Sqm | 134.7 | 194.9917 | 18161.3728
18 | 13.8 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. | 398.256 | Sqm | 89.65 | 129.7773 | 51684.6043
19 | 13.60.1 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade –Two or more coats on new work.-internal walls | 398.256 | Sqm | 80.5 | 116.5318 | 46409.4885
20 | 13.48.1 | Finishing walls with Acrylic Smooth exterior paint of required shade : New work (Two or more coat applied @ 1.67 ltr/10 sqmover and including priming coat of exterior primer applied @ 2.20 kg/ 10 sqm) | 74 | Sqm | 100 | 144.76 | 10712.24
21 | 13.48.3 | Painting Steel work with Delux Multi surface paint to give an even shade.Two or more coat applied @ 0.90 ltr/10sqm over an over an under coat of primer applied @ 0.80ltr/10aqm of approved brand or manufacture. | 3.315 | Sqm | 90 | 130.284 | 431.8915
22 | 8.2.2.2 | Providing and fixing 18mm thick gang saw cut mirror polished premoulded and prepolished) machine cut for kitchen platforms, vanity counters, window sills , facias and similar locations of required size of approved shade, colour and texture laid over 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels. Granite of any colour and shade: Area of slab over 0.50 sqm.: Lowest retail price not less than Rs. 2500.00/m2( Granite to be selected by the Engineer in charge) | 0.9 | Sqm | 2463.55 | 3566.235 | 3209.6115
23 | 9.117.1 | Providing and fixing factory made UPVC door frame made of UPVC extruded section having an overall dimensions as below ( tolerance ± 1mm ), with wall thickness 2.0mm (± 0.2mm), corners of the door frame to be joined with galvanized brackets and stainless steel screws, joints mitered and plastic welded. The hinged side vertical of the frames reinforced by galvanized M.S. tube of size 19x19 mm and 1mm (± 0.1mm) wall thickness and 3 nos. Stainless steel hinged fixed to the frame complete as per manufacturers Specification and direction of engineering -in-change : Extruded section profile size 48x40 mm | 6.72 | M | 213.75 | 309.4245 | 2079.3326
24 | 9.118.1 | Providing and fixing existing door frames: 24 mm thick factory made PVC door shutters made of styles and rails of a UPVC hollow section of size 59x24 mm and wall thickness 2 mm (± 0.2mm) with in built edging on both sides. The styles and rails mitered and joint at the corners by means of M.S. galvanized / plastic brackets of size 75x220 mm having wall thickness 1.0 mm and stainless steel screws. The styles of the shutter reinforced by inserting galvanized M.S. tube of size 20x20 mm and 1mm (± 0.1mm) wall thickness. The lock rail made up of " H" section, a UPVC hollow section of size 100x24 mm and 2mm (± 0.2mm) wall thickness, fixed to the shutters styles by means of plastic/ galvanized M.S.'U' cleats. The shutter frame filled with a UPVC multi chambered single panel of size not less than 620mm, having over all thickness of 20mm and 1mm (± 0.1mm) wall thickness. The panes filled vertically and tie bar at two places by inserting horizontally 6mm galvanized M.S. rod and fastened with nuts and washers, complete as per manufacturer's specification and direction of Engineer- in - charge. (for W,C and bath room door shutter). | 6.72 | Sqm | 2718.6 | 3935.4454 | 26446.1928
25 | 11.41.2 | Providing and laying polished vitrified floor tile in different sizes (thickness to be specified by the manufacturer) with Acid and / or Alkali resistant tiles with water absorptions less than 0.08% and confirming to IS:15622 of approved make in all colours and shades, laid on 20mm thick cement mortor 1:4 (1 cement:4 Coard sand) including grouting the joints with white cement and matching pigments etc. complete. (Lowest retail price not less than Rs. 880/m2) : Size of Tiles 60 x 60 cm (Tiles to be selected by the Engineer in charge) | 68.9249 | sqm | 1405.95 | 2035.2532 | 140279.6247
26 | 11.39 | Providing and laying rectified Glazed Ceramic floor tiles 300x300 mm or more (thickness to be specified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make in colours White, Ivory, Grey, Fume Red Brown, laid on 20mm thick cement mortar 1:4 (1 Cement : 4 Coarse sand) including grouting the joints with white cement and matching pigments etc., complete.(lowest price of tile not less than 650/m2) | 6.4904 | sqm | 950.05 | 1375.2924 | 8926.1977
27 | 11.4 | Providing and fixing Ist quality ceramic glazed wall tiles of size 300x450mm conforming to IS : 15622 (thickness to be specified by the manufacturer ) of approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados over 12 mm thick bed of cement Mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm including pointing in white cement mixed with pigment of matching shade complete.(.(lowest price of tile not less than 725/m2) | 25 | sqm | 1009.6 | 1461.497 | 36537.424
28 | 12.45 | Providing and fixing false ceiling at all height including providing and fixingof frame work made of special sections, power pressed from M.S. sheets and galvanized with zinc coating of 120 gms/sqm (both side inclusive) asper IS : 277 and consisting of angle cleats of size 25 mm wide x 1.6 mmthick with flanges of 27 mm and 37mm, at 1200 mm centre to centre, oneflange fixed to the ceiling with dash fastener 12.5 mm dia x 50mm long with6mm dia bolts, other flange of cleat fixed to the angle hangers of 25x10x0.50mm of required length with nuts & bolts of required size and other end ofangle hanger fixed with intermediate G.I. channels 45x15x0.9 mm runningat the spacing of 1200 mm centre to centre, to which the ceiling section0.5 mm thick bottom wedge of 80 mm with tapered flanges of 26 mm eachhaving lips of 10.5 mm, at 450 mm centre to centre, shall be fixed in adirection perpendicular to G.I. intermediate channel with connecting clipsmade out of 2.64 mm dia x 230 mm long G.I. wire at every junction, includingfixing perimeter channels 0.5 mm thick 27 mm high having flanges of 20mm and 30 mm long, the perimeter of ceiling fixed to wall/partition with the |  |  |  | 0 | 0
help of rawl plugs at 450 mm centre, with 25mm long dry wall screws @230 mm interval, including fixing of gypsum board to ceiling section andperimeter channel with the help of dry wall screws of size 3.5 x 25 mm at230 mm c/c, including jointing and finishing to a flush finish of tapered andsquare edges of the board with recomme-nded jointing compound ,
| 12.45.1 | 12.5 mm thick tapered edge gypsum plain board conformingto IS: 2095- Part I | 48.1626 | sqm | 907.1 | 1313.118 | 63243.1751 | #VALUE! | sqm
29 | 21.1.1.2 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) : For fixed portion: Powder coated aluminium (minimum thickness of powder coating 50 micron) | 115.83 | kg | 377.75 | 546.8309 | 63339.4231
30 | 21.1.2.2 | For shutters of doors, windows & ventilators including providing and fixing hinges/ pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately). Powder coated aluminium (minimum thickness of powder coating 50 micron) | 75.6 | Kg | 435.75 | 630.7917 | 47687.8525
31 | 21.3.2 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.5 mm thickness | 15.12 | sqm | 1054.2 | 1526.0599 | 23074.026
32 | 21.8 | Filling the gap in between aluminium frame & adjacent RCC/Brick/Stone work by providing weather silicon sealant over backer rod of approved quality as per architectural drawings and direction of Enginner-in-charge complete. |  |  |  | 0 | 0
| 21.8.1 | Upto 5mm depth and 5mm width | 10 | Rm | 88.75 | 128.4745 | 1284.745
33 | 21.18 | Providing and fixing 12 mm thick frameless toughened glass door shutter of approved brand and manufacture, including providing and fixing top & bottom pivot & spring type fixing arrangement and making necessary holes etc. for fixing required door fitings, all complete as per direction of Engineer-in-charge ( Door handle, lock and stopper etc. to be paid separately) | 2.7 | Sqm | 4746.3 | 6870.7439 | 18551.0085
34 | MR | Providing and fixing arrangement and making necessary holes etc. for fixing required door fitings, all complete as per direction of Engineer-in-charge Door handle, lock and stopper etc. | 6 | Each | 126 |  | 756
35 | 9.83 | Providing and fixing aluminium die cast body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 35 kg and door width upto 700 mm) with necessary accessories and screws etc. complete. | 2 | Each | 753.75 | 1091.1285 | 2182.257
36 | 9.97 | Providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade with necessary screws etc., complete. |  |  |  | 0 | 0
| 9.97.2 | 250 x 10mm | 8 | Each | 95.25 | 137.8839 | 1103.0712
| 9.97.4 | 150 x 10mm | 8 | Each | 65.35 | 94.6007 | 756.8053
37 | 21.13 | Providing and fixing 100mm brass locks (best make of approved quality) for aluminum doors including necessary cutting and making good etc. complete | 8 | Each | 418.65 | 606.0377 | 4848.3019
38 | 21.12.2 | Providing and fixing aluminium tubular handle bar 32 mm outer dia, 3.0 mm thick & 2100 mm long with SS screws etc .complete as per direction of Engineer-in-Charge. Powder coated minimum thickness 50 micron aluminium tubular handle bar. | 8 | Each | 508.55 | 736.177 | 5889.4158
39 | 9.101 | Providing and fixing aluminium hanging floor door stopper ISI marked anodised (anodic coating note less than grade AC 10 as per IS : 1868) transparent or dyed to required colour and shade with necessary screws etc., complete. |  |  |  | 0 | 0
| 9.101.1 | Single rubber stopper | 3 | Each | 37.5 | 54.285 | 162.855
40 | 21.4 | Providing and fixing double action hydraulic floor spring of approved brand and manufacture IS : 6315 marked, for doors including cost of cutting floors as required, embedding in floors and cover plates with brass pivot and single piect M.S. sheet outer box with side plate etc., complete as per the direction of Engineer-in-charge. |  |  |  | 0 | 0
| 21.4.2 | With brass cover plate | 1 | Each | 2213.2 | 3203.8283 | 3203.8283
41 | 9.149 | Providing and fixing casement handle made of zinc alloyed (white powder coated) for uPVC casement window with necessary screws etc. complete. | 4 | Each | 216.65 | 313.6225 | 1254.4902
42 | 9.68.1 | Providing and fixing oxidised M.S. casement stays (straight peg type) with necessary screws etc. Complete-300 mm weighing not less than 200 gms | 8 | Each | 36.2 | 52.4031 | 419.225
43 | LMR | Providing and fixing wash basin (counter type) with CI / MS brackets, 15mm CP brass Pillar taps, 32mm CP brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever required.: White Vitreous China Wash basin size 630 x 450mm with a single 15mm C.P brass piller tap. Make:Hindware,Cera,Jaquar etc.., (Lowest retail price of basin not less than Rs. 3000/each and Pillar tap not less than Rs. 2000/each. Materials to be selected by the Engineer in charge) | 2 | Each | 6732.75 |  | 13465.5
44 | M.R | Providing and fixing white vitreous china Wall Mounted type water closet (European type W.C.pan) with seat and lid, 3/6 litre low level white vitrous Dual Flushing cistern and C.P flush bend with fitting and C.I brackets, 40mm flush bend, overflow arrangement with specials of standard make and mosquito proof coupling of approved municipal design complete including painting of fittings and brackets, cutting and making good the walls and floors wherever required. Make:Hindware,Cera,Jaquar etc.., WC pan with ISI marked white solid plastic seat and lid (Lowest retail price not less than 10,000/each. Materials to be selected by the Engineer in charge) | 2 | Each | 13797.5 |  | 27595
45 | LMR | Providing and fixing C.P. brass long body bib cock of (2 in 1 type)approved quality conforming to IS standards and weighing not less than 690 gms.: 15 mm nominal bore: Make:Jauqar, Hindware, Parryware, crome | 2 | Each | 1540 |  | 3080 | 2 | nos
46 | 17.28.1.1 | Providing and fixing PVC Waste pipe for sink or wash basin including PVC waste fittings complete.:Semi rigid pipe 32mm dia | 2 | Each | 76.75 | 111.1033 | 222.2066 | 2 | nos
47 | 17.34.1 | Providing and fixing Toilet paper holder . Make:Hindware,Cera,Jaquar etc..,:C.P Brass | 1 | Each | 415.9 | 602.0568 | 602.0568 | 2 | nos
48 | 18.65 | Providing and fixing SS soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements. Weighing not less than 106 gms. | 1 | Each | 164.95 | 238.7816 | 238.7816 | 3 | nos
49 | 17.31 | Providing and fixing 600 x 450mm bevelled edge mirror of superior glass (of approved quality) complete with 6mm thick hard board ground fixed to wooden cleats with C.P. brass screws and washers complete. | 1 | Each | 793.95 | 1149.322 | 1149.322 | 1 | nos
50 | 17.73.2 | Providing and fixing SS towel rail complete with brackets fixed to wooden cleats with CP brass screws with concealed fitting arrangement of approved quality and colour. 600mm long towel rail with total length of 645mm, width 78mm and effective height of 88mm, weighing not less than 190gms. | 1 | Each | 541.5 | 783.8754 | 783.8754 | 3 | nos
51 | LMR | Providing & fixing of CP Health faucet. Hand operated spray unit( Instand type)).Make:Jauqar, Hindware, Parryware, crome., (Lowest retail price not less than 1200/each. Materials to be selected by the Engineer in charge) | 2 | Each | 2043 |  | 4086 | 2
52 | LMR | Providing and fixing PVC pipes for water supply arrangements including cost pipes, fittings, solvent cement,testing of pipes, labour charges etc complete : Concealed work including cutting chases and making good the wall etc |  |  |  | 0 | 0
|  | 20mm nominal outer dia .Pipes. (10kg/cm2) | 20 | RM | 220 |  | 4400
|  | 32mm nominal outer dia .Pipes. (10kg/cm2) | 20 | RM | 236 |  | 4720
53 | LMR | Providing and fixing PVC soil, waste and vent pipe to IS : 13592 of SWR quality, including all fittings, like EG : Bends, Tees, Elbows, Collars, junction, inspection doors, cowls, offsets, access pipes, jointing with rubber ring / solvent cement by application of leak proof adhesive like FRP paste including cutting holes in walls and floors and making good. Make: Supreme, Finolex, Astral |  |  |  | 0 | 0
|  | 50mm dia (6kg / sq.cm) | 20 | RM | 260.45 |  | 5209
|  | 63mm dia (6kg / sq.cm) | 25 | RM | 306 |  | 7650
|  | 75mm dia (6kg / sq.cm) | 20 | RM | 407 |  | 8140
|  | 110mm dia (6 kg / sq.cm) | 20 | RM | 557 |  | 11140
54 | 18.77 | Cutting holes upto 15 x 15 cm in R.C.C. floors and roofs for passing drain pipe etc. and repairing the hole after insertion of drain pipe etc. with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) including finishing complete. | 1 | Each | 193 | 279.3868 | 279.3868
55 | 12.41.2 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A including jointing with seal ring conforming to IS : 5382 leaving 10 mm gap for thermal expansion.(i) Single socketed pipes. 110 mm diameter | 8 | RM | 231.65 | 335.3365 | 2682.6923
56 | MR | Providing and fixing PVC floor trap self cleansing design with or without vent arm complete including cutting and making good the walls and floors. Make:Supreme,Finolex,Prince etc.., | 2 | Each | 519 |  | 1038
|  | 110mm dia inlet 110mm dia outlet |  |  |  | 0 | 0 | 2
57 | 18.58.2.1 | Providing and fixing PTMT grating of approved quality and colour.:Rectangular type with openable circular lid.150 mm nominal size square 100 mm diameter of the inner hinged round grating | 3 | Each | 220.45 | 319.1234 | 957.3703
58 | LMR | Providing and fixing C.P. brass pillar cock (push type)approved quality conforming to IS standards and weighing not less than 690 gms.: 15 mm nominal bore for wash basins: Make:Jauqar, Hindware, Parryware, crome | 2 | Each | 2706 |  | 5412 | 3 | nos
59 | 26.1 | Providing and supplying aluminium extruded tubular and other aluminium sections as per the architectural drawings and approved shop drawings , the aluminium quality as per grade 6063 T5 or T6 as per BS 1474,including super durable powder coating of 60-80 microns conforming to AAMA 2604 of required colour and shade as approved by the Engineer-in-Charge. ( The item includes cost of material such as cleats, sleeves, screws etc. necessary for fabrication of extruded aluminium frame work. Nothing extra shall be paid on this account). | 65 | Kg | 338.25 | 489.6507 | 31827.2955
60 | 26.2 | Designing, fabricating, testing, protection, installing and fixing in positionsemi (grid) unitized system of structural glazing (with open joints) for linearas well as curvilinear portions of the building for all heights and all levels,including:a) Structural analysis & design and preparation of shop drawings for thespecified design loads conforming to IS 875 part III (the system mustpassed the proof test at 1.5 times design wind pressure without anyfailure), including functional design of the aluminum sections for fixing glazing panels of various thicknesses, aluminium cleats, sleeves and c) Providing and filling, two part pump filled, structural silicone sealant and one part weather silicone sealant compatible with the structuralsilicone sealant of required bite size in a clean and controlled factory /work shop environment , including double sided spacer tape, setting blocks and backer rod, all of approved grade, brand and manufacture,as per the approved sealant design, within and all around the perimeterd) Providing and fixing in position flashings of solid aluminium sheet mm thick and of sizes, shapes and profiles, as required as per the site conditions, to seal the gap between the building structure and all its interfaces with curtain glazing to make it watertighte) Making provision for drainage of moisture/ water that enters the curtainglazing system to make it watertight, by incorporating principles of required), making necessary holes of required sizes and of requirednumbers etc. complete. This item includes cost of all inputs ofsplice plates etc. gaskets, screws, toggles, nuts, bolts, clamps etc., structural and weather silicone sealants, flashings, fire stop (barrier)-cum-smoke seals, microwave cured EPDM gaskets for water tightness, pressure equalisation & drainage and protection against fire hazardincluding:b) Fabricating and supplying serrated M.S. hot dip galvanised / Aluminiumalloy of 6005 T5 brackets of required sizes, sections and profiles etc.to accommodate 3 Dimentional movement for achieving perfectverticality and fixing structural glazing system rigidly to theRCC/masonry/structural steel framework of building structure using stainless steel anchor fasteners/ bolts, nylon seperator to prevent bimetallic contacts with nuts and washers etc. of stainless steel grade 316, of the required capacity and in required numbers | 9.38 | Sqm | 2556.2 | 3700.3551 | 34709.331
|  | installation of glazed units, T&P, scaffolding and other incidental charges including wastages etc., enabling temporary structures and services, cranes or cradles etc. as described above and as specified. The item includes the cost of getting all the structural and functional design including shop drawings checked by a structural designer, dully approved by Engineer-in-charge. The item also includes the cost of all mock ups at site, cost of all samples of the individual components for testing in an approved laboratory, field tests on the assembled working structural glazing as specified, cleaning and protection till the handing over of the building for occupation. In the end, the Contractor shall provide a water tight structural glazing having all the performance characteristics etc. all complete as required, as per the Architectural drawings, as per item description, as specified, as per the approved shop drawings and as directed by the Engineerin-Charge. |  |  |  | 0 | 0
|  | Note:- 1. The cost of providing extruded aluminium frames, shadow boxes, extruded aluminium section capping for fixing in the grooves of the curtain glazing and vermin proof stainless steel wire mesh shall be paid for separately under relevant items under this subhead. However, for the purpose of payment, only the actual area of structural glazing (including width of grooves ) on the external face shall be measured in sqm. up to two decimal places. Note:-2. The following performance test are to be conducted on structural glazing system if area of structural glazing exceeds 2500 Sqm from the certified laboratories accreditated by NABL(National Accreditation Board for Testing and Calibration Laboratories), Department of Science & Technologies, India. Cost of testing is payable separately. The NIT approving authority will decide the necessity of testing on the basis of cost of the work, cost of the test and importance of the work. Performance Testing of Structural glazing system Tests to be conducted in the NBL Certified laboratories |  |  |  | 0 | 0
61 | LMR | Providing and fixing poly carbonate (multi wall 6mm or nearest size) sheet roofing of approved make and quality fixed with polymer coated J or L hooks, bolts and nuts of required diameter with necessary washers complete including the cost of M.S square tube 50x25mm 16 gauge fixed with MS flat 25x6mm including necessary nuts and bolts to support the roofing,painting witn two or more coatswaithsyntheticenamel paint over a priming coat of Zinchromate primer etc complete. | 6.22 | Sqm | 2785.59 |  | 17326.3698
62 | 10.2 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete: | 70 | Kg | 73.95 | 107.05 | 7493.5014
63 | LMR | WALL PANEL for acoustic treatment - -Supply and fixing of Keiler/equivalent make 6 mm Polyester Fiber panel, fixed on GI Channel filled with 48kg/ dencityx 50 mm thick rock wool backing with black fleece cloth of 120 GSM. | 55.8885 | sqm | 5450 |  | 304592.325
64 | LMR | Supplying and fixing white board(3x1.50m) with necessary arrangements | 4.5 |  | 1500 |  | 6750
65 | LMR | Supply and installation of DCP type fire extinguisher of 6 kg. Capacity complete with initial charges and installation brackets complete with installation brackets with ISI mark IS:15638 | 1 | Each |  | 2800 | 2800
|  | TOTAL(PART-A) |  |  |  | 0 | #REF!

## civil-+ELEab -ele (hidden)
ESTIMATE FOR ELECTRICAL WORKS IN CONFERENCE HALL IN KAKKANADU FACTORY,COCHIN-PART-B
Item no. | DSR-2014 | Item Description | Qty | Unit | Rate | Rate+CI | Amount
ELECTRICAL WORKS(PART-B)
LMR ITEMS
1 |  | Surface mounted Indoor,decorative box type fitting, Retro LED cat ref. LTT8-20 with 20W LED Lamp having high efficiency PMMA diffuser giving soft glare free light of Crompton or Equi | 9 | Each | 3278 |  | 29502
2 |  | Recess down lighter DN194B LED15S of Philips/Equi with lamp | 8 | Each | 2904 |  | 23232
3 |  | Supply of Green square down lighter recessed BBS175 1xDLED of Philips or Equi with Lamp | 4 | Each | 1992 |  | 7968
4 |  | Supply of Recess mounted full glow RC170B LED 29S of Philips or Equi with lamp | 8 | Each | 4646 |  | 37168
5 |  | Supply & installation of LED Lamp Non Dimmable 7/9W B22 on existing angle batten | 2 | Each | 545 |  | 1090
6 |  | Supply of Linnet - LCL-10-CDL,Sleek LED mirror light,with high out put diffuser, 2 feet size of Crompton or Equi | 1 | Each | 2091 |  | 2091
7 |  | Supply of Indoor down lighter,recessed mounted LED down lights with the option for fixed/ adjustable and spot options. BBS312 1xDLED of Philips or Equi | 6 | Each | 2788 |  | 16728
8 |  | Supply & Installation of LED strip light for indoor with driver, Beetle cat ref. LST20RGB of crompton or equi of 5 meter length | 6 | set | 3336 |  | 20016
9 |  | Supply of ceiling fan 1050/1200 mm sweep,230V,1Ph, complete with double ball bearing, motor blades, down rods, canopy, capacitor etc complete as required 5 star rating (Crompton Riviera / Usha Maxx Air / Khaitan Newtec) | 8 | Each | 2180 |  | 17440
10 |  | Supply and installation of Decorative Wall fan 400 mm sweep, 230V.1Ph, complete with Openable mesh Cover ,string Operated etc as required. (Crompton WM Wind Flo / Usha Helix high speed / Khaitan Merlin Hi speed) | 6 | Each | 2698 |  | 16188
11 |  | Supply and fitting 250 mm sweep automatic shutter Sleek and stylish design type exhaust fan complete with louvers and cable from ceiling rose / connector to fan. (Usha Crisp Air / Crompton Crossair / Khaitan Vento). | 2 | Each | 1393 |  | 2786
12 |  | S/F PVC holder: Supplying and fixing PVC batten/ angle holder including connection etc. as required. | 2 | Each | 71 |  | 142
13 |  | Supply & fixing INFORMATION OUTLET WITH FACE PLATE (concealed in modular work station raceways /gypboard partitions/ walls-with modular back box), TERMINATION AND TESTING CAT6 A (AMP/PANDUIT/Systimax) | 10 | Each | 760 |  | 7600
14 |  | Supply of Alluminium cable. Supply of the following sizes of Alluminium armoured PVC insulated, XLPE Power cable of 1.1kV grade to site including transporting and stacking charges at work site.. |  |  |  |  | 0
a |  | 4 X 16 sq. mm | 30 | Metre | 315 |  | 9450
b |  | 4 X 10 sq. mm | 15 | Metre | 278 |  | 4170
15 |  | Supplying and drawing of UTP 4 pair CAT -6A LAN cable in existing surface/ recessed PVC conduit as required, AMP/Molex make | 300 | Metre | 77 |  | 23100
16 |  | S&F MCCB in cubicle Pannel: Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required. |  |  |  |  | 0
|  | 63 Amp, 16 KA TP MCCB | 1 | 1 | 6188 |  | 6188
DSR ITEMS
17 |  | Point wiring in PVC conduit, with Modular type switch: Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
a |  | Group B | 5 | Point | 585 | 846.846 | 4234.23
b |  | Group C | 32 | Point | 718 | 1039.3768 | 33260.0576
18 |  | Twin control point wiring in PVC conduit, with modular type switch: Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. | 2 | Point | 770 | 1114.652 | 2229.304 | 224859
19 |  | Power plug wiring in PVC conduit ( 2x4 sq mm ): Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 1 No 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 50 | Metre | 162 | 234.5112 | 11725.56
20 |  | Circuit Sub main wiring in PVC Conduit: Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required |  |  |  | 0 | 0
| a | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | 60 | Metre | 106 | 153.4456 | 9206.736
| b | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 80 | Metre | 131 | 189.6356 | 15170.848
| c | 4 X 4 sq. mm + 2 X 4 sq. mm earth wire | 25 | Metre | 275 | 398.09 | 9952.25
| d | 4 X 6 sq. mm + 2 X 6 sq. mm earth wire | 25 | Metre | 389 | 563.1164 | 14077.91
|  | RE- WIRING IN PVC CONDUIT |  |  |  | 0 | 0
21 |  | Telephone wiring in existing conduit: Supplying and drawing following pair 0.5 sq mm FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. |  |  |  | 0 | 0
|  | 2 Pair | 50 | Metre | 18 | 26.0568 | 1302.84
|  | PVC CONDUIT, METAL BOXES |  | Metre |  | 0 | 0
22 |  | S/F PVC conduit: Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. |  |  |  | 0 | 0
| a | 20 mm | 100 | Metre | 146 | 211.3496 | 21134.96
| b | 25 mm | 250 | Metre | 152 | 220.0352 | 55008.8
| c | 40 mm | 20 | Metre | 110 | 159.236 | 3184.72
23 |  | S/F Modular type switch/ socket: Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. |  |  |  | 0 | 0
| a | Telephone socket outlet | 2 | Each | 95 | 137.522 | 275.044
24 |  | Supplying and fixing electronic fan regulator: Supplying and fixing stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | 8 | Each | 284 | 411.1184 | 3288.9472
25 |  | S/F Modular type blanking plates: Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | 12 | Each | 23 | 33.2948 | 399.5376
26 |  | S/F Modular boxes, base & cover plate: Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required. |  |  |  | 0 | 0
| a | 1 or 2 Module (75mmX75mm) | 20 | Each | 166 | 240.3016 | 4806.032
27 |  | S/F light plug point modular type accessaries: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). | 16 | Each | 303 | 438.6228 | 7017.9648
28 |  | S/F Power plug point with modular type switch: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 2 | Each | 395 | 571.802 | 1143.604
29 |  | S/F Ceiling rose: Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. | 15 | Each | 43 | 62.2468 | 933.702
30 |  | S/F call bell/buzzer: Supplying and fixing call bell/ buzzer suitable for single phase, 230 volts, complete as required. | 2 | Each | 61 | 88.3036 | 176.6072
31 |  | ITC Fluroscent/LED fitting directly on surface/celing: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | 35 | Each | 91 | 131.7316 | 4610.606
32 |  | ITC Fluroscent fitting with down rod: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc., including supplying and fixing ball and socket arrangement, 2 no. down rods of 20 mm dia X 1.6 mm thick steel conduit upto 30 cm length, painting and wiring the down rods and connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | 8 | Each | 233 | 337.2908 | 2698.3264
33 |  | S/F extra down rod: Providing and fixing extra conduit down rod of 20 mm dia, 2 X 10 cm length wiring with 2 X 1.5 sq. mm FR PVC insulated, copper conductor, single core cable including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | 16 | Each | 31 | 44.8756 | 718.0096
34 |  | ITC Ceiling fan: Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable etc. as required. | 8 | Each | 95 | 137.522 | 1100.176
35 |  | Extra down rod 15 mm dia 20 CM Length: Supplying and fixing extra conduit down rod of 20 cm length G.I. pipe 15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | 24 | Each | 27 | 39.0852 | 938.0448
36 |  | ITC Exhaust fan: Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. |  |  |  | 0 | 0
|  | Upto 450 mm sweep | 2 | Each | 204 | 295.3104 | 590.6208
37 |  | S/F SP MCB DB: Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) |  |  |  | 0 | 0
|  | 2 + 6/8 way, Double door | 2 | Each | 1041 | 1506.9516 | 3013.9032
38 |  | S/F Vertical Type Pre Wired TP MCB DB: Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required ,suitable for MCCB incomer.(But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.) |  |  |  | 0 | 0
| 2.9.5 | 4 way Double door | 1 | Each | 7901 | 11437.4876 | 11437.4876
39 |  | S/F 'C' series, MCB: Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | 0 | 0
a |  | Single pole | 8 | Each | 169 | 244.6444 | 1957.1552
40 |  | S/F S P MCB blanking plate: Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | 10 | Each | 7 | 10.1332 | 101.332
41 |  | S/F DP MCB isolator: Supplying and fixing following rating, double pole, 240 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | 0 | 0
|  | 40 amps | 2 | Each | 218 | 315.5768 | 631.1536
42 |  | S/F SPN RCCB: Supplying and fixing following rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  | Each |  | 0 | 0
|  | 25 amps | 2 | Each | 1645 | 2381.302 | 4762.604
43 |  | S/F 20A SPN MCB industrial socket outlet: Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 2 | Each | 954 | 1381.0104 | 2762.0208
44 |  | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 1 | Each | 141 | 204.1116 | 204.1116
45 |  | G.I Earth Pipe Electrode With Salt & Charcoal: Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 2 | Each | 3926 | 5683.2776 | 11366.5552
46 |  | Providing and fixing 4.00mm dia copper wire on surface or in recess: Providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 60 | metre | 86 | 124.4936 | 7469.616
47 |  | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. |  |  |  | 0 | 0
|  | Upto 35 sq. mm | 35 | metre | 606 | 877.2456 | 30703.596
48 |  | Supplying and making end termination with brass compression gland and aluminium lugs: Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. |  |  |  | 0 | 0
| 9.1.32 | 4 X 10 sq. mm (25mm) | 2 | Each | 193 | 279.3868 | 558.7736
| 9.1.33 | 4 X 16 sq. mm (28mm) | 2 | Each | 245 | 354.662 | 709.324
|  | TOTAL FOR PART-B |  |  |  |  | 509722.0708
Abraham Jacob
Project Engineer (Elec)
HLL Lifecare Ltd (ID -South)
Thiruvanathapuram

## civil-+ELEab (5) (hidden)
ESTIMATE FOR CIVIL&ELECTRICAL WORKS IN CONFERENCE HALL IN KAKKANADU FACTORY,COCHIN
Item no. | DSR | Item Description | Qty | Unit | Rate | Rate+CI | Amount
CIVIL WORKS(PART-A)
1 | 15.2.2 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material as per direction of Engineer-in-charge. | 10 | Cum | 550.5 | 796.9038 | 7969.038
2 | 15.3 | Demolishing R.C.C. work manually/ by mechanical means includingstacking of steel bars and disposal of unserviceable material as per direction of Engineer - in- charge. | 1 | Cum | 1302.3 | 1885.2095 | 1885.2095
3 | 15.5 | Extra for cutting reinforcement bars manually/ by mechanical means inR.C.C. or R.B. work (Payment shall be made on the cross sectional areaof R.C.C. or R.B. work) as per direction of Engineer -in -charge. | 30 | Sqm | 450.45 | 652.0714 | 19562.1426 | 30
4 | 15.23.1 | Dismantling tile work in floors, dadoing and roofs laid in cement mortar including stacking material within 50 metres lead.For thickness of tiles up to 25 mm | 25 | Sqm | 28.2 | 40.8223 | 1020.558
5 | 15.5 | Dismantling of Water closets/wash basin/flushing cistern etc. of all types (C.I./PVC/Vitrious China) including stacking of useful materials near the site and disposal of unserviceable materials | 2 | Each | 519.87 | 752.5638 | 1505.1276 | 2 | Nos
6 | 15.6 | Disposal of building rubbish / malba / similar unserviceable, dismantled or waste materials by mechanical means including loading, transporting, unloading to approved municipal dumping ground or as approved by Engineer-in-charge, beyond 50 m initial lead, for all loads including all lifts involved. | 40 | Cum | 123.7 | 179.0681 | 7162.7248
7 | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30cm in depth. 1.5m in width as well as 10 sqm on plan) including disposal of excavated earth and lift upto 1.5m, disposed earth to be levelled and neatly dressed.:All kinds of soil | 3.375 | Cum | 155.6 | 225.2466 | 760.2071
8 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All works up to plinth level-.1:4:8 (1 Cement : 4 coarse sand : 8 graded stone aggregate 40mm nominal size) | #REF! | Cum | 4301.2 | 6226.4171 | #REF!
9 | 5.37 | Providing and laying in position ready mixed M-25 grade concrete for reinforced cement concrete work, using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , excluding the cost of centering, shuttering finishing and reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, improve workability without impairing strength and durability as per direction of the Engineer - in - charge. |  |  |  | 0 | 0 | 0
|  | (Note :- Cement content considered in this item is @ 330 kg/cum. Excess/less cement used as per design mix is payable/recoverable separately). |  |  |  | 0 | 0 | 0
| 5.37.2 | All work above plinth level up to floor V level -RCC work (M25 concrete) | 22.3373 | Cum | 7363 | 10658.6788 | 238085.605 | #VALUE!
10 | 5.9 | Centering and shuttering including strutting, propping etc., and removal of form for, |  |  |  | 0 | 0 | 0
10.a | 5.9.1 | Foundations, Footings, bases of columns,etc for mass concrete. | 2.25 | Sqm | 196.45 | 284.381 | 639.8573
10.a | 5.9.6 | Columns and Pillars, Piers, Abutments, Posts and Struts. | 64 | Sqm | 453.35 | 656.2695 | 42001.2454
10.b | 5.9.3 | Suspended floors, roofs, landings, Balconies and access platform | 103 | Sqm | 453.35 | 656.2695 | 67595.7544
10.c | 5.9.5 | Lintel,beams,plinth beams,girders,bressumers and cantilevers | 74 | Sqm | 332.15 | 480.8203 | 35580.7052
10.d | 5.9.19 | Weather shade, Chajjas, corbels etc., including edges | 15 | Sqm | 492.35 | 712.7259 | 10690.8879
11 | 5.22.A.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending,placing in position and binding all complete above plinth level. :Thermo-Mechanically Treated bars | 2203.5283 | Kg | 68.1 | 98.5816 | 217227.2593
12 | 6.4.2 | Brick work with F.P.S bricks of class designation 5.0 in superstructure above plinth level up to floor v level in all shapes an sizes in: Cement mortar 1: 6 (1 cement :6 coarse sand) | 24.1605 | Cum | 5426.15 | 7854.8947 | 189778.4679
13 | 6.13.1 | Half brick masonry with F.P.S brick of class designation 7.5 in superstructure above plinth level up to floor V level : CM 1:3 (1 cement : 3 coarse sand) | 28.88 | Sqm | 692.8 | 1002.8973 | 28963.6734
14 | 6.15 | Extra for providing and placing in position 2 Nos. 6mm dia M.S bars at every third course of half brick masonry (with FPS brick) | 28.88 | Sqm | 69.5 | 100.6082 | 2905.5648
15 | 13.2.1 | 15mm cement plaster on the rough side of single or half brick wall of mix : 1 : 4 (1 cement : 4 fine sand) up to 10m height for external walls | 74 | Sqm | 189.4 | 274.1754 | 20288.9826
16 | 13.1.1 | 12mm cement plaster on the rough side of single or half brick wall of mix : 1 : 4 (1 cement : 4 fine sand) for internal walls, column and beams etc | 305.1168 | Sqm | 163.35 | 236.4655 | 72149.5845
17 | 13.16.1 | 6 mm cement plaster of mix : 1:3 (1 cement: 3 fine sand) for ceiling plastering | 93.1392 | Sqm | 134.7 | 194.9917 | 18161.3728
18 | 13.8 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. | 398.256 | Sqm | 89.65 | 129.7773 | 51684.6043
19 | 13.60.1 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade –Two or more coats on new work.-internal walls | 398.256 | Sqm | 80.5 | 116.5318 | 46409.4885
20 | 13.48.1 | Finishing walls with Acrylic Smooth exterior paint of required shade : New work (Two or more coat applied @ 1.67 ltr/10 sqmover and including priming coat of exterior primer applied @ 2.20 kg/ 10 sqm) | 74 | Sqm | 100 | 144.76 | 10712.24
21 | 13.48.3 | Painting Steel work with Delux Multi surface paint to give an even shade.Two or more coat applied @ 0.90 ltr/10sqm over an over an under coat of primer applied @ 0.80ltr/10aqm of approved brand or manufacture. | 3.315 | Sqm | 90 | 130.284 | 431.8915
22 | 8.2.2.2 | Providing and fixing 18mm thick gang saw cut mirror polished premoulded and prepolished) machine cut for kitchen platforms, vanity counters, window sills , facias and similar locations of required size of approved shade, colour and texture laid over 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels. Granite of any colour and shade: Area of slab over 0.50 sqm.: Lowest retail price not less than Rs. 2500.00/m2( Granite to be selected by the Engineer in charge) | 0.9 | Sqm | 2463.55 | 3566.235 | 3209.6115
23 | 9.117.1 | Providing and fixing factory made UPVC door frame made of UPVC extruded section having an overall dimensions as below ( tolerance ± 1mm ), with wall thickness 2.0mm (± 0.2mm), corners of the door frame to be joined with galvanized brackets and stainless steel screws, joints mitered and plastic welded. The hinged side vertical of the frames reinforced by galvanized M.S. tube of size 19x19 mm and 1mm (± 0.1mm) wall thickness and 3 nos. Stainless steel hinged fixed to the frame complete as per manufacturers Specification and direction of engineering -in-change : Extruded section profile size 48x40 mm | 6.72 | M | 213.75 | 309.4245 | 2079.3326
24 | 9.118.1 | Providing and fixing existing door frames: 24 mm thick factory made PVC door shutters made of styles and rails of a UPVC hollow section of size 59x24 mm and wall thickness 2 mm (± 0.2mm) with in built edging on both sides. The styles and rails mitered and joint at the corners by means of M.S. galvanized / plastic brackets of size 75x220 mm having wall thickness 1.0 mm and stainless steel screws. The styles of the shutter reinforced by inserting galvanized M.S. tube of size 20x20 mm and 1mm (± 0.1mm) wall thickness. The lock rail made up of " H" section, a UPVC hollow section of size 100x24 mm and 2mm (± 0.2mm) wall thickness, fixed to the shutters styles by means of plastic/ galvanized M.S.'U' cleats. The shutter frame filled with a UPVC multi chambered single panel of size not less than 620mm, having over all thickness of 20mm and 1mm (± 0.1mm) wall thickness. The panes filled vertically and tie bar at two places by inserting horizontally 6mm galvanized M.S. rod and fastened with nuts and washers, complete as per manufacturer's specification and direction of Engineer- in - charge. (for W,C and bath room door shutter). | 6.72 | Sqm | 2718.6 | 3935.4454 | 26446.1928
25 | 11.41.2 | Providing and laying polished vitrified floor tile in different sizes (thickness to be specified by the manufacturer) with Acid and / or Alkali resistant tiles with water absorptions less than 0.08% and confirming to IS:15622 of approved make in all colours and shades, laid on 20mm thick cement mortor 1:4 (1 cement:4 Coard sand) including grouting the joints with white cement and matching pigments etc. complete. (Lowest retail price not less than Rs. 880/m2) : Size of Tiles 60 x 60 cm (Tiles to be selected by the Engineer in charge) | 68.9249 | sqm | 1405.95 | 2035.2532 | 140279.6247
26 | 11.39 | Providing and laying rectified Glazed Ceramic floor tiles 300x300 mm or more (thickness to be specified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make in colours White, Ivory, Grey, Fume Red Brown, laid on 20mm thick cement mortar 1:4 (1 Cement : 4 Coarse sand) including grouting the joints with white cement and matching pigments etc., complete. | 6.4904 | sqm | 950.05 | 1375.2924 | 8926.1977
27 | 11.4 | Providing and fixing Ist quality ceramic glazed wall tiles of size 300x450mm conforming to IS : 15622 (thickness to be specified by the manufacturer ) of approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados over 12 mm thick bed of cement Mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm including pointing in white cement mixed with pigment of matching shade complete. | 25 | sqm | 1009.6 | 1461.497 | 36537.424
28 | 12.45 | Providing and fixing false ceiling at all height including providing and fixingof frame work made of special sections, power pressed from M.S. sheets and galvanized with zinc coating of 120 gms/sqm (both side inclusive) asper IS : 277 and consisting of angle cleats of size 25 mm wide x 1.6 mmthick with flanges of 27 mm and 37mm, at 1200 mm centre to centre, oneflange fixed to the ceiling with dash fastener 12.5 mm dia x 50mm long with6mm dia bolts, other flange of cleat fixed to the angle hangers of 25x10x0.50mm of required length with nuts & bolts of required size and other end ofangle hanger fixed with intermediate G.I. channels 45x15x0.9 mm runningat the spacing of 1200 mm centre to centre, to which the ceiling section0.5 mm thick bottom wedge of 80 mm with tapered flanges of 26 mm eachhaving lips of 10.5 mm, at 450 mm centre to centre, shall be fixed in adirection perpendicular to G.I. intermediate channel with connecting clipsmade out of 2.64 mm dia x 230 mm long G.I. wire at every junction, includingfixing perimeter channels 0.5 mm thick 27 mm high having flanges of 20mm and 30 mm long, the perimeter of ceiling fixed to wall/partition with the |  |  |  | 0 | 0
help of rawl plugs at 450 mm centre, with 25mm long dry wall screws @230 mm interval, including fixing of gypsum board to ceiling section andperimeter channel with the help of dry wall screws of size 3.5 x 25 mm at230 mm c/c, including jointing and finishing to a flush finish of tapered andsquare edges of the board with recomme-nded jointing compound ,
| 12.45.1 | 12.5 mm thick tapered edge gypsum plain board conformingto IS: 2095- Part I | 48.1626 | sqm | 907.1 | 1313.118 | 63243.1751 | #VALUE! | sqm
29 | 21.1.1.2 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) : For fixed portion: Powder coated aluminium (minimum thickness of powder coating 50 micron) | 115.83 | kg | 377.75 | 546.8309 | 63339.4231
30 | 21.1.2.2 | For shutters of doors, windows & ventilators including providing and fixing hinges/ pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately). Powder coated aluminium (minimum thickness of powder coating 50 micron) | 75.6 | Kg | 435.75 | 630.7917 | 47687.8525
31 | 21.3.2 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.5 mm thickness | 15.12 | sqm | 1054.2 | 1526.0599 | 23074.026
32 | 21.8 | Filling the gap in between aluminium frame & adjacent RCC/Brick/Stone work by providing weather silicon sealant over backer rod of approved quality as per architectural drawings and direction of Enginner-in-charge complete. |  |  |  | 0 | 0
| 21.8.1 | Upto 5mm depth and 5mm width | 10 | Rm | 88.75 | 128.4745 | 1284.745
33 | 21.18 | Providing and fixing 12 mm thick frameless toughened glass door shutter of approved brand and manufacture, including providing and fixing top & bottom pivot & spring type fixing arrangement and making necessary holes etc. for fixing required door fitings, all complete as per direction of Engineer-in-charge ( Door handle, lock and stopper etc. to be paid separately) | 2.7 | Sqm | 4746.3 | 6870.7439 | 18551.0085
34 | MR | Providing and fixing arrangement and making necessary holes etc. for fixing required door fitings, all complete as per direction of Engineer-in-charge Door handle, lock and stopper etc. | 6 | Each | 126 |  | 756
35 | 9.83 | Providing and fixing aluminium die cast body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 35 kg and door width upto 700 mm) with necessary accessories and screws etc. complete. | 2 | Each | 753.75 | 1091.1285 | 2182.257
36 | 9.97 | Providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade with necessary screws etc., complete. |  |  |  | 0 | 0
| 9.97.2 | 250 x 10mm | 8 | Each | 95.25 | 137.8839 | 1103.0712
| 9.97.4 | 150 x 10mm | 8 | Each | 65.35 | 94.6007 | 756.8053
37 | 21.13 | Providing and fixing 100mm brass locks (best make of approved quality) for aluminum doors including necessary cutting and making good etc. complete | 8 | Each | 418.65 | 606.0377 | 4848.3019
38 | 21.12.2 | Providing and fixing aluminium tubular handle bar 32 mm outer dia, 3.0 mm thick & 2100 mm long with SS screws etc .complete as per direction of Engineer-in-Charge. Powder coated minimum thickness 50 micron aluminium tubular handle bar. | 8 | Each | 508.55 | 736.177 | 5889.4158
39 | 9.101 | Providing and fixing aluminium hanging floor door stopper ISI marked anodised (anodic coating note less than grade AC 10 as per IS : 1868) transparent or dyed to required colour and shade with necessary screws etc., complete. |  |  |  | 0 | 0
| 9.101.1 | Single rubber stopper | 3 | Each | 37.5 | 54.285 | 162.855
40 | 21.4 | Providing and fixing double action hydraulic floor spring of approved brand and manufacture IS : 6315 marked, for doors including cost of cutting floors as required, embedding in floors and cover plates with brass pivot and single piect M.S. sheet outer box with side plate etc., complete as per the direction of Engineer-in-charge. |  |  |  | 0 | 0
| 21.4.2 | With brass cover plate | 1 | Each | 2213.2 | 3203.8283 | 3203.8283
41 | 9.149 | Providing and fixing casement handle made of zinc alloyed (white powder coated) for uPVC casement window with necessary screws etc. complete. | 4 | Each | 216.65 | 313.6225 | 1254.4902
42 | 9.68.1 | Providing and fixing oxidised M.S. casement stays (straight peg type) with necessary screws etc. Complete-300 mm weighing not less than 200 gms | 8 | Each | 36.2 | 52.4031 | 419.225
43 | LMR | Providing and fixing wash basin (counter type) with CI / MS brackets, 15mm CP brass Pillar taps, 32mm CP brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever required.: White Vitreous China Wash basin size 630 x 450mm with a single 15mm C.P brass piller tap. Make:Hindware,Cera,Jaquar etc.., (Lowest retail price of basin not less than Rs. 3000/each and Pillar tap not less than Rs. 2000/each. Materials to be selected by the Engineer in charge) | 2 | Each | 6732.75 |  | 13465.5
44 | M.R | Providing and fixing white vitreous china Wall Mounted type water closet (European type W.C.pan) with seat and lid, 3/6 litre low level white vitrous Dual Flushing cistern and C.P flush bend with fitting and C.I brackets, 40mm flush bend, overflow arrangement with specials of standard make and mosquito proof coupling of approved municipal design complete including painting of fittings and brackets, cutting and making good the walls and floors wherever required. Make:Hindware,Cera,Jaquar etc.., WC pan with ISI marked white solid plastic seat and lid (Lowest retail price not less than 10,000/each. Materials to be selected by the Engineer in charge) | 2 | Each | 13797.5 |  | 27595
45 | LMR | Providing and fixing C.P. brass long body bib cock of (2 in 1 type)approved quality conforming to IS standards and weighing not less than 690 gms.: 15 mm nominal bore: Make:Jauqar, Hindware, Parryware, crome | 2 | Each | 1540 |  | 3080 | 2 | nos
46 | 17.28.1.1 | Providing and fixing PVC Waste pipe for sink or wash basin including PVC waste fittings complete.:Semi rigid pipe 32mm dia | 2 | Each | 76.75 | 111.1033 | 222.2066 | 2 | nos
47 | 17.34.1 | Providing and fixing Toilet paper holder . Make:Hindware,Cera,Jaquar etc..,:C.P Brass | 1 | Each | 415.9 | 602.0568 | 602.0568 | 2 | nos
48 | 18.65 | Providing and fixing SS soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements. Weighing not less than 106 gms. | 1 | Each | 164.95 | 238.7816 | 238.7816 | 3 | nos
49 | 17.31 | Providing and fixing 600 x 450mm bevelled edge mirror of superior glass (of approved quality) complete with 6mm thick hard board ground fixed to wooden cleats with C.P. brass screws and washers complete. | 1 | Each | 793.95 | 1149.322 | 1149.322 | 1 | nos
50 | 17.73.2 | Providing and fixing SS towel rail complete with brackets fixed to wooden cleats with CP brass screws with concealed fitting arrangement of approved quality and colour. 600mm long towel rail with total length of 645mm, width 78mm and effective height of 88mm, weighing not less than 190gms. | 1 | Each | 541.5 | 783.8754 | 783.8754 | 3 | nos
51 | LMR | Providing & fixing of CP Health faucet. Hand operated spray unit( Instand type)).Make:Jauqar, Hindware, Parryware, crome., (Lowest retail price not less than 1200/each. Materials to be selected by the Engineer in charge) | 2 | Each | 2043 |  | 4086 | 2
52 | LMR | Providing and fixing PVC pipes for water supply arrangements including cost pipes, fittings, solvent cement,testing of pipes, labour charges etc complete : Concealed work including cutting chases and making good the wall etc |  |  |  | 0 | 0
|  | 20mm nominal outer dia .Pipes. (10kg/cm2) | 20 | RM | 220 |  | 4400
|  | 32mm nominal outer dia .Pipes. (10kg/cm2) | 20 | RM | 236 |  | 4720
53 | LMR | Providing and fixing PVC soil, waste and vent pipe to IS : 13592 of SWR quality, including all fittings, like EG : Bends, Tees, Elbows, Collars, junction, inspection doors, cowls, offsets, access pipes, jointing with rubber ring / solvent cement by application of leak proof adhesive like FRP paste including cutting holes in walls and floors and making good. Make: Supreme, Finolex, Astral |  |  |  | 0 | 0
|  | 50mm dia (6kg / sq.cm) | 20 | RM | 260.45 |  | 5209
|  | 63mm dia (6kg / sq.cm) | 25 | RM | 306 |  | 7650
|  | 75mm dia (6kg / sq.cm) | 20 | RM | 407 |  | 8140
|  | 110mm dia (6 kg / sq.cm) | 20 | RM | 557 |  | 11140
54 | 18.77 | Cutting holes upto 15 x 15 cm in R.C.C. floors and roofs for passing drain pipe etc. and repairing the hole after insertion of drain pipe etc. with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) including finishing complete. | 1 | Each | 193 | 279.3868 | 279.3868
55 | 12.41.2 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A including jointing with seal ring conforming to IS : 5382 leaving 10 mm gap for thermal expansion.(i) Single socketed pipes. 110 mm diameter | 8 | RM | 231.65 | 335.3365 | 2682.6923
56 | MR | Providing and fixing PVC floor trap self cleansing design with or without vent arm complete including cutting and making good the walls and floors. Make:Supreme,Finolex,Prince etc.., | 2 | Each | 519 |  | 1038
|  | 110mm dia inlet 110mm dia outlet |  |  |  | 0 | 0 | 2
57 | 18.58.2.1 | Providing and fixing PTMT grating of approved quality and colour.:Rectangular type with openable circular lid.150 mm nominal size square 100 mm diameter of the inner hinged round grating | 3 | Each | 220.45 | 319.1234 | 957.3703
58 | LMR | Providing and fixing C.P. brass pillar cock (push type)approved quality conforming to IS standards and weighing not less than 690 gms.: 15 mm nominal bore for wash basins: Make:Jauqar, Hindware, Parryware, crome | 2 | Each | 2706 |  | 5412 | 3 | nos
59 | 26.1 | Providing and supplying aluminium extruded tubular and other aluminium sections as per the architectural drawings and approved shop drawings , the aluminium quality as per grade 6063 T5 or T6 as per BS 1474,including super durable powder coating of 60-80 microns conforming to AAMA 2604 of required colour and shade as approved by the Engineer-in-Charge. ( The item includes cost of material such as cleats, sleeves, screws etc. necessary for fabrication of extruded aluminium frame work. Nothing extra shall be paid on this account). | 65 | Kg | 338.25 | 489.6507 | 31827.2955
60 | 26.2 | Designing, fabricating, testing, protection, installing and fixing in positionsemi (grid) unitized system of structural glazing (with open joints) for linearas well as curvilinear portions of the building for all heights and all levels,including:a) Structural analysis & design and preparation of shop drawings for thespecified design loads conforming to IS 875 part III (the system mustpassed the proof test at 1.5 times design wind pressure without anyfailure), including functional design of the aluminum sections for fixing glazing panels of various thicknesses, aluminium cleats, sleeves and c) Providing and filling, two part pump filled, structural silicone sealant and one part weather silicone sealant compatible with the structuralsilicone sealant of required bite size in a clean and controlled factory /work shop environment , including double sided spacer tape, setting blocks and backer rod, all of approved grade, brand and manufacture,as per the approved sealant design, within and all around the perimeterd) Providing and fixing in position flashings of solid aluminium sheet mm thick and of sizes, shapes and profiles, as required as per the site conditions, to seal the gap between the building structure and all its interfaces with curtain glazing to make it watertighte) Making provision for drainage of moisture/ water that enters the curtainglazing system to make it watertight, by incorporating principles of required), making necessary holes of required sizes and of requirednumbers etc. complete. This item includes cost of all inputs ofsplice plates etc. gaskets, screws, toggles, nuts, bolts, clamps etc., structural and weather silicone sealants, flashings, fire stop (barrier)-cum-smoke seals, microwave cured EPDM gaskets for water tightness, pressure equalisation & drainage and protection against fire hazardincluding:b) Fabricating and supplying serrated M.S. hot dip galvanised / Aluminiumalloy of 6005 T5 brackets of required sizes, sections and profiles etc.to accommodate 3 Dimentional movement for achieving perfectverticality and fixing structural glazing system rigidly to theRCC/masonry/structural steel framework of building structure using stainless steel anchor fasteners/ bolts, nylon seperator to prevent bimetallic contacts with nuts and washers etc. of stainless steel grade 316, of the required capacity and in required numbers | 9.38 | Sqm | 2556.2 | 3700.3551 | 34709.331
|  | installation of glazed units, T&P, scaffolding and other incidental charges including wastages etc., enabling temporary structures and services, cranes or cradles etc. as described above and as specified. The item includes the cost of getting all the structural and functional design including shop drawings checked by a structural designer, dully approved by Engineer-in-charge. The item also includes the cost of all mock ups at site, cost of all samples of the individual components for testing in an approved laboratory, field tests on the assembled working structural glazing as specified, cleaning and protection till the handing over of the building for occupation. In the end, the Contractor shall provide a water tight structural glazing having all the performance characteristics etc. all complete as required, as per the Architectural drawings, as per item description, as specified, as per the approved shop drawings and as directed by the Engineerin-Charge. |  |  |  | 0 | 0
|  | Note:- 1. The cost of providing extruded aluminium frames, shadow boxes, extruded aluminium section capping for fixing in the grooves of the curtain glazing and vermin proof stainless steel wire mesh shall be paid for separately under relevant items under this subhead. However, for the purpose of payment, only the actual area of structural glazing (including width of grooves ) on the external face shall be measured in sqm. up to two decimal places. Note:-2. The following performance test are to be conducted on structural glazing system if area of structural glazing exceeds 2500 Sqm from the certified laboratories accreditated by NABL(National Accreditation Board for Testing and Calibration Laboratories), Department of Science & Technologies, India. Cost of testing is payable separately. The NIT approving authority will decide the necessity of testing on the basis of cost of the work, cost of the test and importance of the work. Performance Testing of Structural glazing system Tests to be conducted in the NBL Certified laboratories |  |  |  | 0 | 0
61 | LMR | Providing and fixing poly carbonate (multi wall 6mm or nearest size) sheet roofing of approved make and quality fixed with polymer coated J or L hooks, bolts and nuts of required diameter with necessary washers complete including the cost of M.S square tube 50x25mm 16 gauge fixed with MS flat 25x6mm including necessary nuts and bolts to support the roofing,painting witn two or more coatswaithsyntheticenamel paint over a priming coat of Zinchromate primer etc complete. | 6.22 | Sqm | 2785.59 |  | 17326.3698
62 | 10.2 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete: | 70 | Kg | 73.95 | 107.05 | 7493.5014
63 | LMR | WALL PANEL for acoustic treatment - -Supply and fixing of Keiler/equivalent make 6 mm Polyester Fiber panel, fixed on GI Channel filled with 48kg/ dencityx 50 mm thick rock wool backing with black fleece cloth of 120 GSM. | 55.8885 | sqm | 5450 |  | 304592.325
64 | LMR | Supplying and fixing white board(3x1.50m) with necessary arrangements | 4.5 |  | 1500 |  | 6750
65 | LMR | Supply and installation of DCP type fire extinguisher of 6 kg. Capacity complete with initial charges and installation brackets complete with installation brackets with ISI mark IS:15638 | 1 | Each |  | 2800 | 2800
|  | TOTAL(PART-A) |  |  |  | 0 | #REF!
ELECTRICAL WORKS(PART-B)
LMR ITEMS
1 |  | Surface mounted Indoor,decorative box type fitting, Retro LED cat ref. LTT8-20 with 20W LED Lamp having high efficiency PMMA diffuser giving soft glare free light of Crompton or Equi | 9 | Each | 3278 |  | 29502
2 |  | Recess down lighter DN194B LED15S of Philips/Equi with lamp | 8 | Each | 2904 |  | 23232
3 |  | Supply of Green square down lighter recessed BBS175 1xDLED of Philips or Equi with Lamp | 4 | Each | 1992 |  | 7968
4 |  | Supply of Recess mounted full glow RC170B LED 29S of Philips or Equi with lamp | 8 | Each | 4646 |  | 37168
5 |  | Supply & installation of LED Lamp Non Dimmable 7/9W B22 on existing angle batten | 2 | Each | 545 |  | 1090
6 |  | Supply of Linnet - LCL-10-CDL,Sleek LED mirror light,with high out put diffuser, 2 feet size of Crompton or Equi | 1 | Each | 2091 |  | 2091
7 |  | Supply of Indoor down lighter,recessed mounted LED down lights with the option for fixed/ adjustable and spot options. BBS312 1xDLED of Philips or Equi | 6 | Each | 2788 |  | 16728
8 |  | Supply & Installation of LED strip light for indoor with driver, Beetle cat ref. LST20RGB of crompton or equi of 5 meter length | 6 | set | 3336 |  | 20016
9 |  | Supply of ceiling fan 1050/1200 mm sweep,230V,1Ph, complete with double ball bearing, motor blades, down rods, canopy, capacitor etc complete as required 5 star rating (Crompton Riviera / Usha Maxx Air / Khaitan Newtec) | 8 | Each | 2180 |  | 17440
10 |  | Supply and installation of Decorative Wall fan 400 mm sweep, 230V.1Ph, complete with Openable mesh Cover ,string Operated etc as required. (Crompton WM Wind Flo / Usha Helix high speed / Khaitan Merlin Hi speed) | 6 | Each | 2698 |  | 16188
11 |  | Supply and fitting 250 mm sweep automatic shutter Sleek and stylish design type exhaust fan complete with louvers and cable from ceiling rose / connector to fan. (Usha Crisp Air / Crompton Crossair / Khaitan Vento). | 2 | Each | 1393 |  | 2786
12 |  | S/F PVC holder: Supplying and fixing PVC batten/ angle holder including connection etc. as required. | 2 | Each | 71 |  | 142
13 |  | Supply & fixing INFORMATION OUTLET WITH FACE PLATE (concealed in modular work station raceways /gypboard partitions/ walls-with modular back box), TERMINATION AND TESTING CAT6 A (AMP/PANDUIT/Systimax) | 10 | Each | 760 |  | 7600
14 |  | Supply of Alluminium cable. Supply of the following sizes of Alluminium armoured PVC insulated, XLPE Power cable of 1.1kV grade to site including transporting and stacking charges at work site.. |  |  |  |  | 0
a |  | 4 X 16 sq. mm | 30 | Metre | 315 |  | 9450
b |  | 4 X 10 sq. mm | 15 | Metre | 278 |  | 4170
15 |  | Supplying and drawing of UTP 4 pair CAT -6A LAN cable in existing surface/ recessed PVC conduit as required, AMP/Molex make | 300 | Metre | 77 |  | 23100
16 |  | S&F MCCB in cubicle Pannel: Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required. |  |  |  |  | 0
|  | 63 Amp, 16 KA TP MCCB | 1 | 1 | 6188 | 6188 | 6188
DSR ITEMS
17 |  | Point wiring in PVC conduit, with Modular type switch: Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
a |  | Group B | 5 | Point | 585 | 846.846 | 4234.23
b |  | Group C | 32 | Point | 718 | 1039.3768 | 33260.0576
18 |  | Twin control point wiring in PVC conduit, with modular type switch: Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. | 2 | Point | 770 | 1114.652 | 2229.304 |  |  | 224859
19 |  | Power plug wiring in PVC conduit ( 2x4 sq mm ): Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 1 No 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 50 | Metre | 162 | 234.5112 | 11725.56
20 |  | Circuit Sub main wiring in PVC Conduit: Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required |  |  |  | 0 | 0
| a | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | 60 | Metre | 106 | 153.4456 | 9206.736
| b | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 80 | Metre | 131 | 189.6356 | 15170.848
| c | 4 X 4 sq. mm + 2 X 4 sq. mm earth wire | 25 | Metre | 275 | 398.09 | 9952.25
| d | 4 X 6 sq. mm + 2 X 6 sq. mm earth wire | 25 | Metre | 389 | 563.1164 | 14077.91
|  | RE- WIRING IN PVC CONDUIT |  |  |  | 0 | 0
21 |  | Telephone wiring in existing conduit: Supplying and drawing following pair 0.5 sq mm FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. |  |  |  | 0 | 0
|  | 2 Pair | 50 | Metre | 18 | 26.0568 | 1302.84
|  | PVC CONDUIT, METAL BOXES |  | Metre |  | 0 | 0
22 |  | S/F PVC conduit: Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. |  |  |  | 0 | 0
| a | 20 mm | 100 | Metre | 146 | 211.3496 | 21134.96
| b | 25 mm | 250 | Metre | 152 | 220.0352 | 55008.8
| c | 40 mm | 20 | Metre | 110 | 159.236 | 3184.72
23 |  | S/F Modular type switch/ socket: Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. |  |  |  | 0 | 0
| a | Telephone socket outlet | 2 | Each | 95 | 137.522 | 275.044
24 |  | Supplying and fixing electronic fan regulator: Supplying and fixing stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | 8 | Each | 284 | 411.1184 | 3288.9472
25 |  | S/F Modular type blanking plates: Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | 12 | Each | 23 | 33.2948 | 399.5376
26 |  | S/F Modular boxes, base & cover plate: Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required. |  |  |  | 0 | 0
| a | 1 or 2 Module (75mmX75mm) | 20 | Each | 166 | 240.3016 | 4806.032
27 |  | S/F light plug point modular type accessaries: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). | 16 | Each | 303 | 438.6228 | 7017.9648
28 |  | S/F Power plug point with modular type switch: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 2 | Each | 395 | 571.802 | 1143.604
29 |  | S/F Ceiling rose: Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. | 15 | Each | 43 | 62.2468 | 933.702
30 |  | S/F call bell/buzzer: Supplying and fixing call bell/ buzzer suitable for single phase, 230 volts, complete as required. | 2 | Each | 61 | 88.3036 | 176.6072
31 |  | ITC Fluroscent/LED fitting directly on surface/celing: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | 35 | Each | 91 | 131.7316 | 4610.606
32 |  | ITC Fluroscent fitting with down rod: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc., including supplying and fixing ball and socket arrangement, 2 no. down rods of 20 mm dia X 1.6 mm thick steel conduit upto 30 cm length, painting and wiring the down rods and connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | 8 | Each | 233 | 337.2908 | 2698.3264
33 |  | S/F extra down rod: Providing and fixing extra conduit down rod of 20 mm dia, 2 X 10 cm length wiring with 2 X 1.5 sq. mm FR PVC insulated, copper conductor, single core cable including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | 16 | Each | 31 | 44.8756 | 718.0096
34 |  | ITC Ceiling fan: Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable etc. as required. | 8 | Each | 95 | 137.522 | 1100.176
35 |  | Extra down rod 15 mm dia 20 CM Length: Supplying and fixing extra conduit down rod of 20 cm length G.I. pipe 15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | 24 | Each | 27 | 39.0852 | 938.0448
36 |  | ITC Exhaust fan: Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. |  |  |  | 0 | 0
|  | Upto 450 mm sweep | 2 | Each | 204 | 295.3104 | 590.6208
37 |  | S/F SP MCB DB: Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) |  |  |  | 0 | 0
|  | 2 + 6/8 way, Double door | 2 | Each | 1041 | 1506.9516 | 3013.9032
38 |  | S/F Vertical Type Pre Wired TP MCB DB: Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required ,suitable for MCCB incomer.(But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.) |  |  |  | 0 | 0
| 2.9.5 | 4 way Double door | 1 | Each | 7901 | 11437.4876 | 11437.4876
39 |  | S/F 'C' series, MCB: Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | 0 | 0
a |  | Single pole | 8 | Each | 169 | 244.6444 | 1957.1552
40 |  | S/F S P MCB blanking plate: Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | 10 | Each | 7 | 10.1332 | 101.332
41 |  | S/F DP MCB isolator: Supplying and fixing following rating, double pole, 240 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | 0 | 0
|  | 40 amps | 2 | Each | 218 | 315.5768 | 631.1536
42 |  | S/F SPN RCCB: Supplying and fixing following rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  | Each |  | 0 | 0
|  | 25 amps | 2 | Each | 1645 | 2381.302 | 4762.604
43 |  | S/F 20A SPN MCB industrial socket outlet: Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 2 | Each | 954 | 1381.0104 | 2762.0208
44 |  | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 1 | Each | 141 | 204.1116 | 204.1116
45 |  | G.I Earth Pipe Electrode With Salt & Charcoal: Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 2 | Each | 3926 | 5683.2776 | 11366.5552
46 |  | Providing and fixing 4.00mm dia copper wire on surface or in recess: Providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 60 | metre | 86 | 124.4936 | 7469.616
47 |  | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. |  |  |  | 0 | 0
|  | Upto 35 sq. mm | 35 | metre | 606 | 877.2456 | 30703.596
48 |  | Supplying and making end termination with brass compression gland and aluminium lugs: Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. |  |  |  | 0 | 0
| 9.1.32 | 4 X 10 sq. mm (25mm) | 2 | Each | 193 | 279.3868 | 558.7736
| 9.1.33 | 4 X 16 sq. mm (28mm) | 2 | Each | 245 | 354.662 | 709.324
|  | TOTAL FOR PART-B |  |  |  |  | 509722.0708
|  | GRAND TOTAL(PARTA+PART-B) |  |  |  |  | #REF!

## FURNTURE (hidden)
ESTIMATE FOR FURNITURE WORKS IN CONFERENCE HALL IN KAKKANADU FACTORY,COCHIN
SI.NO | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
1 | Supply of table of size 100x60x75cm with keyboard tray, C P U open stand with one drawer cum cupboard and other sections made of 18mm pre-laminated particle board with 2mm PVC edge band lippings including all hardwares | 1 | EACH | 9200 | 9200
2 | Supply of revolving &tilting medium back chairwith permanent contact mechanism,gas lift , fixed arms with Nylon base,Twin wheel nylon castors |  |  |  | 0
| Seat and Back-Twin ply with high density cushion in artifical leather finish in black colour | 25 | EACH | 4500 | 112500
3 | Supply and providing of 24 seater conference table having over all dimension of 6000mmL *2000mmW *750mm H as shown inthe drawing. Top should be made of 36 mm thick and base material made of 18 mm thick marine plywood with 2 mm thick PVC edge banding.. Concealed wire carrying capacity and Access flap for accessing Data/Electrical sockets access from top. Powder coated switch mounting tray made of 0.8 mm and 1.2 mm MS sheet. | 1 | EACH | 108775 | 108775
4 | Supply and providing of Podium with over all dimension of 700mmL *600mmW *1100mm H of 18 mm thick marine plywood board with 2 mm thick PVC edge banding including platform for hand supportand provision ofr mike | 1 | Each | 15000 | 15000
| TOTAL AMOUNT FOR FURNITURE |  |  |  | 245475

## dsr ) (hidden)
ESTIMATE FOR CIVIL&ELECTRICAL WORKS IN CONFERENCE HALL IN KAKKANADU FACTORY,COCHIN
Item no. | DSR | Item Description | Qty | Unit | Rate | Rate+CI | Amount | Amount
CIVIL WORKS(PART-A)
1 | 15.2.2 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material as per direction of Engineer-in-charge. | 10 | Cum | 550.5 | 796.9038 | 7969.038 | 5505
2 | 15.3 | Demolishing R.C.C. work manually/ by mechanical means includingstacking of steel bars and disposal of unserviceable material as per direction of Engineer - in- charge. | 1 | Cum | 1302.3 | 1885.2095 | 1885.2095 | 1302.3
3 | 15.5 | Extra for cutting reinforcement bars manually/ by mechanical means inR.C.C. or R.B. work (Payment shall be made on the cross sectional areaof R.C.C. or R.B. work) as per direction of Engineer -in -charge. | 30 | Sqm | 450.45 | 652.0714 | 19562.1426 | 13513.5
4 | 15.23.1 | Dismantling tile work in floors, dadoing and roofs laid in cement mortar including stacking material within 50 metres lead.For thickness of tiles up to 25 mm | 25 | Sqm | 28.2 | 40.8223 | 1020.558 | 705
5 | 15.5 | Dismantling of Water closets/wash basin/flushing cistern etc. of all types (C.I./PVC/Vitrious China) including stacking of useful materials near the site and disposal of unserviceable materials | 2 | Each | 519.87 | 752.5638 | 1505.1276 | 1039.74 | Nos
6 | 15.6 | Disposal of building rubbish / malba / similar unserviceable, dismantled or waste materials by mechanical means including loading, transporting, unloading to approved municipal dumping ground or as approved by Engineer-in-charge, beyond 50 m initial lead, for all loads including all lifts involved. | 40 | Cum | 123.7 | 179.0681 | 7162.7248 | 4948
7 | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30cm in depth. 1.5m in width as well as 10 sqm on plan) including disposal of excavated earth and lift upto 1.5m, disposed earth to be levelled and neatly dressed.:All kinds of soil | 3.375 | Cum | 155.6 | 225.2466 | 760.2071 | 525.15
8 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All works up to plinth level-.1:4:8 (1 Cement : 4 coarse sand : 8 graded stone aggregate 40mm nominal size) | #REF! | Cum | 4301.2 | 6226.4171 | #REF! | #REF!
9 | 5.37 | Providing and laying in position ready mixed M-25 grade concrete for reinforced cement concrete work, using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , excluding the cost of centering, shuttering finishing and reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, improve workability without impairing strength and durability as per direction of the Engineer - in - charge. |  |  |  | 0 | 0 | 0
|  | (Note :- Cement content considered in this item is @ 330 kg/cum. Excess/less cement used as per design mix is payable/recoverable separately). |  |  |  | 0 | 0 | 0
| 5.37.2 | All work above plinth level up to floor V level -RCC work (M25 concrete) | 22.3373 | Cum | 7363 | 10658.6788 | 238085.605 | 164469.1938
10 | 5.9 | Centering and shuttering including strutting, propping etc., and removal of form for, |  |  |  | 0 | 0 | 0
10.a | 5.9.1 | Foundations, Footings, bases of columns,etc for mass concrete. | 2.25 | Sqm | 196.45 | 284.381 | 639.8573 | 442.0125
10.a | 5.9.6 | Columns and Pillars, Piers, Abutments, Posts and Struts. | 64 | Sqm | 453.35 | 656.2695 | 42001.2454 | 29014.4
10.b | 5.9.3 | Suspended floors, roofs, landings, Balconies and access platform | 103 | Sqm | 453.35 | 656.2695 | 67595.7544 | 46695.05
10.c | 5.9.5 | Lintel,beams,plinth beams,girders,bressumers and cantilevers | 74 | Sqm | 332.15 | 480.8203 | 35580.7052 | 24579.1
10.d | 5.9.19 | Weather shade, Chajjas, corbels etc., including edges | 15 | Sqm | 492.35 | 712.7259 | 10690.8879 | 7385.25
11 | 5.22.A.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending,placing in position and binding all complete above plinth level. :Thermo-Mechanically Treated bars | 2203.5283 | Kg | 68.1 | 98.5816 | 217227.2593 | 150060.2786
12 | 6.4.2 | Brick work with F.P.S bricks of class designation 5.0 in superstructure above plinth level up to floor v level in all shapes an sizes in: Cement mortar 1: 6 (1 cement :6 coarse sand) | 24.1605 | Cum | 5426.15 | 7854.8947 | 189778.4679 | 131098.693
13 | 6.13.1 | Half brick masonry with F.P.S brick of class designation 7.5 in superstructure above plinth level up to floor V level : CM 1:3 (1 cement : 3 coarse sand) | 28.88 | Sqm | 692.8 | 1002.8973 | 28963.6734 | 20008.064
14 | 6.15 | Extra for providing and placing in position 2 Nos. 6mm dia M.S bars at every third course of half brick masonry (with FPS brick) | 28.88 | Sqm | 69.5 | 100.6082 | 2905.5648 | 2007.16
15 | 13.2.1 | 15mm cement plaster on the rough side of single or half brick wall of mix : 1 : 4 (1 cement : 4 fine sand) up to 10m height for external walls | 74 | Sqm | 189.4 | 274.1754 | 20288.9826 | 14015.6
16 | 13.1.1 | 12mm cement plaster on the rough side of single or half brick wall of mix : 1 : 4 (1 cement : 4 fine sand) for internal walls, column and beams etc | 305.1168 | Sqm | 163.35 | 236.4655 | 72149.5845 | 49840.8293
17 | 13.16.1 | 6 mm cement plaster of mix : 1:3 (1 cement: 3 fine sand) for ceiling plastering | 93.1392 | Sqm | 134.7 | 194.9917 | 18161.3728 | 12545.8502
18 | 13.8 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. | 398.256 | Sqm | 89.65 | 129.7773 | 51684.6043 | 35703.6504
19 | 13.60.1 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade –Two or more coats on new work.-internal walls | 398.256 | Sqm | 80.5 | 116.5318 | 46409.4885 | 32059.608
20 | 13.48.1 | Finishing walls with Acrylic Smooth exterior paint of required shade : New work (Two or more coat applied @ 1.67 ltr/10 sqmover and including priming coat of exterior primer applied @ 2.20 kg/ 10 sqm) | 74 | Sqm | 100 | 144.76 | 10712.24 | 7400
21 | 13.48.3 | Painting Steel work with Delux Multi surface paint to give an even shade.Two or more coat applied @ 0.90 ltr/10sqm over an over an under coat of primer applied @ 0.80ltr/10aqm of approved brand or manufacture. | 3.315 | Sqm | 90 | 130.284 | 431.8915 | 298.35
22 | 8.2.2.2 | Providing and fixing 18mm thick gang saw cut mirror polished premoulded and prepolished) machine cut for kitchen platforms, vanity counters, window sills , facias and similar locations of required size of approved shade, colour and texture laid over 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels. Granite of any colour and shade: Area of slab over 0.50 sqm.: Lowest retail price not less than Rs. 2500.00/m2( Granite to be selected by the Engineer in charge) | 0.9 | Sqm | 2463.55 | 3566.235 | 3209.6115 | 2217.195
23 | 9.117.1 | Providing and fixing factory made UPVC door frame made of UPVC extruded section having an overall dimensions as below ( tolerance ± 1mm ), with wall thickness 2.0mm (± 0.2mm), corners of the door frame to be joined with galvanized brackets and stainless steel screws, joints mitered and plastic welded. The hinged side vertical of the frames reinforced by galvanized M.S. tube of size 19x19 mm and 1mm (± 0.1mm) wall thickness and 3 nos. Stainless steel hinged fixed to the frame complete as per manufacturers Specification and direction of engineering -in-change : Extruded section profile size 48x40 mm | 6.72 | M | 213.75 | 309.4245 | 2079.3326 | 1436.4
24 | 9.118.1 | Providing and fixing existing door frames: 24 mm thick factory made PVC door shutters made of styles and rails of a UPVC hollow section of size 59x24 mm and wall thickness 2 mm (± 0.2mm) with in built edging on both sides. The styles and rails mitered and joint at the corners by means of M.S. galvanized / plastic brackets of size 75x220 mm having wall thickness 1.0 mm and stainless steel screws. The styles of the shutter reinforced by inserting galvanized M.S. tube of size 20x20 mm and 1mm (± 0.1mm) wall thickness. The lock rail made up of " H" section, a UPVC hollow section of size 100x24 mm and 2mm (± 0.2mm) wall thickness, fixed to the shutters styles by means of plastic/ galvanized M.S.'U' cleats. The shutter frame filled with a UPVC multi chambered single panel of size not less than 620mm, having over all thickness of 20mm and 1mm (± 0.1mm) wall thickness. The panes filled vertically and tie bar at two places by inserting horizontally 6mm galvanized M.S. rod and fastened with nuts and washers, complete as per manufacturer's specification and direction of Engineer- in - charge. (for W,C and bath room door shutter). | 6.72 | Sqm | 2718.6 | 3935.4454 | 26446.1928 | 18268.992
25 | 11.41.2 | Providing and laying polished vitrified floor tile in different sizes (thickness to be specified by the manufacturer) with Acid and / or Alkali resistant tiles with water absorptions less than 0.08% and confirming to IS:15622 of approved make in all colours and shades, laid on 20mm thick cement mortor 1:4 (1 cement:4 Coard sand) including grouting the joints with white cement and matching pigments etc. complete. (Lowest retail price not less than Rs. 880/m2) : Size of Tiles 60 x 60 cm (Tiles to be selected by the Engineer in charge) | 68.9249 | sqm | 1405.95 | 2035.2532 | 140279.6247 | 96904.9632
26 | 11.39 | Providing and laying rectified Glazed Ceramic floor tiles 300x300 mm or more (thickness to be specified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make in colours White, Ivory, Grey, Fume Red Brown, laid on 20mm thick cement mortar 1:4 (1 Cement : 4 Coarse sand) including grouting the joints with white cement and matching pigments etc., complete. | 6.4904 | sqm | 950.05 | 1375.2924 | 8926.1977 | 6166.2045
27 | 11.4 | Providing and fixing Ist quality ceramic glazed wall tiles of size 300x450mm conforming to IS : 15622 (thickness to be specified by the manufacturer ) of approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados over 12 mm thick bed of cement Mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm including pointing in white cement mixed with pigment of matching shade complete. | 25 | sqm | 1009.6 | 1461.497 | 36537.424 | 25240
28 | 12.45 | Providing and fixing false ceiling at all height including providing and fixingof frame work made of special sections, power pressed from M.S. sheets and galvanized with zinc coating of 120 gms/sqm (both side inclusive) asper IS : 277 and consisting of angle cleats of size 25 mm wide x 1.6 mmthick with flanges of 27 mm and 37mm, at 1200 mm centre to centre, oneflange fixed to the ceiling with dash fastener 12.5 mm dia x 50mm long with6mm dia bolts, other flange of cleat fixed to the angle hangers of 25x10x0.50mm of required length with nuts & bolts of required size and other end ofangle hanger fixed with intermediate G.I. channels 45x15x0.9 mm runningat the spacing of 1200 mm centre to centre, to which the ceiling section0.5 mm thick bottom wedge of 80 mm with tapered flanges of 26 mm eachhaving lips of 10.5 mm, at 450 mm centre to centre, shall be fixed in adirection perpendicular to G.I. intermediate channel with connecting clipsmade out of 2.64 mm dia x 230 mm long G.I. wire at every junction, includingfixing perimeter channels 0.5 mm thick 27 mm high having flanges of 20mm and 30 mm long, the perimeter of ceiling fixed to wall/partition with the |  |  |  | 0 | 0 | 0
|  | help of rawl plugs at 450 mm centre, with 25mm long dry wall screws @230 mm interval, including fixing of gypsum board to ceiling section andperimeter channel with the help of dry wall screws of size 3.5 x 25 mm at230 mm c/c, including jointing and finishing to a flush finish of tapered andsquare edges of the board with recomme-nded jointing compound , | [5 empty] | 0
| 12.45.1 | 12.5 mm thick tapered edge gypsum plain board conformingto IS: 2095- Part I | 48.1626 | sqm | 907.1 | 1313.118 | 63243.1751 | 43688.2945 | sqm
29 | 21.1.1.2 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) : For fixed portion: Powder coated aluminium (minimum thickness of powder coating 50 micron) | 115.83 | kg | 377.75 | 546.8309 | 63339.4231 | 43754.7825
30 | 21.1.2.2 | For shutters of doors, windows & ventilators including providing and fixing hinges/ pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately). Powder coated aluminium (minimum thickness of powder coating 50 micron) | 75.6 | Kg | 435.75 | 630.7917 | 47687.8525 | 32942.7
31 | 21.3.2 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.5 mm thickness | 15.12 | sqm | 1054.2 | 1526.0599 | 23074.026 | 15939.504
32 | 21.8 | Filling the gap in between aluminium frame & adjacent RCC/Brick/Stone work by providing weather silicon sealant over backer rod of approved quality as per architectural drawings and direction of Enginner-in-charge complete. |  |  |  | 0 | 0 | 0
| 21.8.1 | Upto 5mm depth and 5mm width | 10 | Rm | 88.75 | 128.4745 | 1284.745 | 887.5
33 | 21.18 | Providing and fixing 12 mm thick frameless toughened glass door shutter of approved brand and manufacture, including providing and fixing top & bottom pivot & spring type fixing arrangement and making necessary holes etc. for fixing required door fitings, all complete as per direction of Engineer-in-charge ( Door handle, lock and stopper etc. to be paid separately) | 2.7 | Sqm | 4746.3 | 6870.7439 | 18551.0085 | 12815.01
35 | 9.83 | Providing and fixing aluminium die cast body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 35 kg and door width upto 700 mm) with necessary accessories and screws etc. complete. | 2 | Each | 753.75 | 1091.1285 | 2182.257 | 1507.5
36 | 9.97 | Providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade with necessary screws etc., complete. |  |  |  | 0 | 0 | 0
| 9.97.2 | 250 x 10mm | 8 | Each | 95.25 | 137.8839 | 1103.0712 | 762
| 9.97.4 | 150 x 10mm | 8 | Each | 65.35 | 94.6007 | 756.8053 | 522.8
37 | 21.13 | Providing and fixing 100mm brass locks (best make of approved quality) for aluminum doors including necessary cutting and making good etc. complete | 8 | Each | 418.65 | 606.0377 | 4848.3019 | 3349.2
38 | 21.12.2 | Providing and fixing aluminium tubular handle bar 32 mm outer dia, 3.0 mm thick & 2100 mm long with SS screws etc .complete as per direction of Engineer-in-Charge. Powder coated minimum thickness 50 micron aluminium tubular handle bar. | 8 | Each | 508.55 | 736.177 | 5889.4158 | 4068.4
39 | 9.101 | Providing and fixing aluminium hanging floor door stopper ISI marked anodised (anodic coating note less than grade AC 10 as per IS : 1868) transparent or dyed to required colour and shade with necessary screws etc., complete. |  |  |  | 0 | 0 | 0
| 9.101.1 | Single rubber stopper | 3 | Each | 37.5 | 54.285 | 162.855 | 112.5
40 | 21.4 | Providing and fixing double action hydraulic floor spring of approved brand and manufacture IS : 6315 marked, for doors including cost of cutting floors as required, embedding in floors and cover plates with brass pivot and single piect M.S. sheet outer box with side plate etc., complete as per the direction of Engineer-in-charge. |  |  |  | 0 | 0 | 0
| 21.4.2 | With brass cover plate | 1 | Each | 2213.2 | 3203.8283 | 3203.8283 | 2213.2
41 | 9.149 | Providing and fixing casement handle made of zinc alloyed (white powder coated) for uPVC casement window with necessary screws etc. complete. | 4 | Each | 216.65 | 313.6225 | 1254.4902 | 866.6
42 | 9.68.1 | Providing and fixing oxidised M.S. casement stays (straight peg type) with necessary screws etc. Complete-300 mm weighing not less than 200 gms | 8 | Each | 36.2 | 52.4031 | 419.225 | 289.6
43 | 17.3.1 | Providing and fixing white vitreous china pedestal type water closet (European type) with seat and lid, 10 litre low level white vitreous china flushing cistern & C.P. flush bend with fittings & C.I.brackets, 40mm flush bend, overflow arrangement with specials of standard make and mosquito proof coupling of approved municipal design complete including painting of fittings and brackets, cutting and making good the walls and floors wherever required : W.C. pan with ISI marked white solid plastic seat and lid.(Make: Hindware, Jaquar, Parryware) | 2 | Each | 4784.6 | 6926.187 | 13852.3739 | 9569.2
44 | 17.7.1 | Providing and fixing wash basin/counter wash basin with C.I. brackets, 15 mm C.P. brass pillar taps,32 mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever require White Vitreous China Wash basin size 630x450 mm with a pair of 15 mm C.P. brass pillar taps. (Make: Hindware, Jaquar, Parryware) | 2 | Each | 2331.15 | 3374.5727 | 6749.1455 | 4662.3
46 | 17.28.1.1 | Providing and fixing PVC Waste pipe for sink or wash basin including PVC waste fittings complete.:Semi rigid pipe 32mm dia | 2 | Each | 76.75 | 111.1033 | 222.2066 | 153.5 | nos
47 | 17.34.1 | Providing and fixing Toilet paper holder . Make:Hindware,Cera,Jaquar etc..,:C.P Brass | 1 | Each | 415.9 | 602.0568 | 602.0568 | 415.9 | nos
48 | 18.65 | Providing and fixing SS soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements. Weighing not less than 106 gms. | 1 | Each | 164.95 | 238.7816 | 238.7816 | 164.95 | nos
49 | 17.31 | Providing and fixing 600 x 450mm bevelled edge mirror of superior glass (of approved quality) complete with 6mm thick hard board ground fixed to wooden cleats with C.P. brass screws and washers complete. | 1 | Each | 793.95 | 1149.322 | 1149.322 | 793.95 | nos
50 | 17.73.2 | Providing and fixing SS towel rail complete with brackets fixed to wooden cleats with CP brass screws with concealed fitting arrangement of approved quality and colour. 600mm long towel rail with total length of 645mm, width 78mm and effective height of 88mm, weighing not less than 190gms. | 1 | Each | 541.5 | 783.8754 | 783.8754 | 541.5 | nos
54 | 18.77 | Cutting holes upto 15 x 15 cm in R.C.C. floors and roofs for passing drain pipe etc. and repairing the hole after insertion of drain pipe etc. with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) including finishing complete. | 1 | Each | 193 | 279.3868 | 279.3868 | 193
55 | 12.41.2 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A including jointing with seal ring conforming to IS : 5382 leaving 10 mm gap for thermal expansion.(i) Single socketed pipes. 110 mm diameter | 8 | RM | 231.65 | 335.3365 | 2682.6923 | 1853.2
57 | 18.58.2.1 | Providing and fixing PTMT grating of approved quality and colour.:Rectangular type with openable circular lid.150 mm nominal size square 100 mm diameter of the inner hinged round grating | 3 | Each | 220.45 | 319.1234 | 957.3703 | 661.35
59 | 26.1 | Providing and supplying aluminium extruded tubular and other aluminium sections as per the architectural drawings and approved shop drawings , the aluminium quality as per grade 6063 T5 or T6 as per BS 1474,including super durable powder coating of 60-80 microns conforming to AAMA 2604 of required colour and shade as approved by the Engineer-in-Charge. ( The item includes cost of material such as cleats, sleeves, screws etc. necessary for fabrication of extruded aluminium frame work. Nothing extra shall be paid on this account). | 65 | Kg | 338.25 | 489.6507 | 31827.2955 | 21986.25
60 | 26.2 | Designing, fabricating, testing, protection, installing and fixing in positionsemi (grid) unitized system of structural glazing (with open joints) for linearas well as curvilinear portions of the building for all heights and all levels,including:a) Structural analysis & design and preparation of shop drawings for thespecified design loads conforming to IS 875 part III (the system mustpassed the proof test at 1.5 times design wind pressure without anyfailure), including functional design of the aluminum sections for fixing glazing panels of various thicknesses, aluminium cleats, sleeves and c) Providing and filling, two part pump filled, structural silicone sealant and one part weather silicone sealant compatible with the structuralsilicone sealant of required bite size in a clean and controlled factory /work shop environment , including double sided spacer tape, setting blocks and backer rod, all of approved grade, brand and manufacture,as per the approved sealant design, within and all around the perimeterd) Providing and fixing in position flashings of solid aluminium sheet mm thick and of sizes, shapes and profiles, as required as per the site conditions, to seal the gap between the building structure and all its interfaces with curtain glazing to make it watertighte) Making provision for drainage of moisture/ water that enters the curtainglazing system to make it watertight, by incorporating principles of required), making necessary holes of required sizes and of requirednumbers etc. complete. This item includes cost of all inputs ofsplice plates etc. gaskets, screws, toggles, nuts, bolts, clamps etc., structural and weather silicone sealants, flashings, fire stop (barrier)-cum-smoke seals, microwave cured EPDM gaskets for water tightness, pressure equalisation & drainage and protection against fire hazardincluding:b) Fabricating and supplying serrated M.S. hot dip galvanised / Aluminiumalloy of 6005 T5 brackets of required sizes, sections and profiles etc.to accommodate 3 Dimentional movement for achieving perfectverticality and fixing structural glazing system rigidly to theRCC/masonry/structural steel framework of building structure using stainless steel anchor fasteners/ bolts, nylon seperator to prevent bimetallic contacts with nuts and washers etc. of stainless steel grade 316, of the required capacity and in required numbers | 9.38 | Sqm | 2556.2 | 3700.3551 | 34709.331 | 23977.156
|  | installation of glazed units, T&P, scaffolding and other incidental charges including wastages etc., enabling temporary structures and services, cranes or cradles etc. as described above and as specified. The item includes the cost of getting all the structural and functional design including shop drawings checked by a structural designer, dully approved by Engineer-in-charge. The item also includes the cost of all mock ups at site, cost of all samples of the individual components for testing in an approved laboratory, field tests on the assembled working structural glazing as specified, cleaning and protection till the handing over of the building for occupation. In the end, the Contractor shall provide a water tight structural glazing having all the performance characteristics etc. all complete as required, as per the Architectural drawings, as per item description, as specified, as per the approved shop drawings and as directed by the Engineerin-Charge. |  |  |  | 0 | 0 | 0
|  | Note:- 1. The cost of providing extruded aluminium frames, shadow boxes, extruded aluminium section capping for fixing in the grooves of the curtain glazing and vermin proof stainless steel wire mesh shall be paid for separately under relevant items under this subhead. However, for the purpose of payment, only the actual area of structural glazing (including width of grooves ) on the external face shall be measured in sqm. up to two decimal places. Note:-2. The following performance test are to be conducted on structural glazing system if area of structural glazing exceeds 2500 Sqm from the certified laboratories accreditated by NABL(National Accreditation Board for Testing and Calibration Laboratories), Department of Science & Technologies, India. Cost of testing is payable separately. The NIT approving authority will decide the necessity of testing on the basis of cost of the work, cost of the test and importance of the work. Performance Testing of Structural glazing system Tests to be conducted in the NBL Certified laboratories |  |  |  | 0 | 0 | 0
62 | 10.2 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete: | 70 | Kg | 73.95 | 107.05 | 7493.5014 | 5176.5
|  | dsr |  |  |  | 0 | #REF! | #REF! |  | 1291150
|  | LMR | [5 empty] | #REF!
|  | CI | [5 empty] | #REF!
#REF!
|  | ELECTRICAL WORKS(PART-B) | [5 empty] | 0
|  | LMR ITEMS | [5 empty] | 0
1 |  | Surface mounted Indoor,decorative box type fitting, Retro LED cat ref. LTT8-20 with 20W LED Lamp having high efficiency PMMA diffuser giving soft glare free light of Crompton or Equi | 9 | Each | 3278 |  | 29502 | 29502
2 |  | Recess down lighter DN194B LED15S of Philips/Equi with lamp | 8 | Each | 2904 |  | 23232 | 23232
3 |  | Supply of Green square down lighter recessed BBS175 1xDLED of Philips or Equi with Lamp | 4 | Each | 1992 |  | 7968 | 7968
4 |  | Supply of Recess mounted full glow RC170B LED 29S of Philips or Equi with lamp | 8 | Each | 4646 |  | 37168 | 37168
5 |  | Supply & installation of LED Lamp Non Dimmable 7/9W B22 on existing angle batten | 2 | Each | 545 |  | 1090 | 1090
6 |  | Supply of Linnet - LCL-10-CDL,Sleek LED mirror light,with high out put diffuser, 2 feet size of Crompton or Equi | 1 | Each | 2091 |  | 2091 | 2091
7 |  | Supply of Indoor down lighter,recessed mounted LED down lights with the option for fixed/ adjustable and spot options. BBS312 1xDLED of Philips or Equi | 6 | Each | 2788 |  | 16728 | 16728
8 |  | Supply & Installation of LED strip light for indoor with driver, Beetle cat ref. LST20RGB of crompton or equi of 5 meter length | 6 | set | 3336 |  | 20016 | 20016
9 |  | Supply of ceiling fan 1050/1200 mm sweep,230V,1Ph, complete with double ball bearing, motor blades, down rods, canopy, capacitor etc complete as required 5 star rating (Crompton Riviera / Usha Maxx Air / Khaitan Newtec) | 8 | Each | 2180 |  | 17440 | 17440
10 |  | Supply and installation of Decorative Wall fan 400 mm sweep, 230V.1Ph, complete with Openable mesh Cover ,string Operated etc as required. (Crompton WM Wind Flo / Usha Helix high speed / Khaitan Merlin Hi speed) | 6 | Each | 2698 |  | 16188 | 16188
11 |  | Supply and fitting 250 mm sweep automatic shutter Sleek and stylish design type exhaust fan complete with louvers and cable from ceiling rose / connector to fan. (Usha Crisp Air / Crompton Crossair / Khaitan Vento). | 2 | Each | 1393 |  | 2786 | 2786
12 |  | S/F PVC holder: Supplying and fixing PVC batten/ angle holder including connection etc. as required. | 2 | Each | 71 |  | 142 | 142
13 |  | Supply & fixing INFORMATION OUTLET WITH FACE PLATE (concealed in modular work station raceways /gypboard partitions/ walls-with modular back box), TERMINATION AND TESTING CAT6 A (AMP/PANDUIT/Systimax) | 10 | Each | 760 |  | 7600 | 7600
14 |  | Supply of Alluminium cable. Supply of the following sizes of Alluminium armoured PVC insulated, XLPE Power cable of 1.1kV grade to site including transporting and stacking charges at work site.. |  |  |  |  | 0 | 0
a |  | 4 X 16 sq. mm | 30 | Metre | 315 |  | 9450 | 9450
b |  | 4 X 10 sq. mm | 15 | Metre | 278 |  | 4170 | 4170
15 |  | Supplying and drawing of UTP 4 pair CAT -6A LAN cable in existing surface/ recessed PVC conduit as required, AMP/Molex make | 300 | Metre | 77 |  | 23100 | 23100
16 |  | S&F MCCB in cubicle Pannel: Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required. |  |  |  |  | 0 | 0
|  | 63 Amp, 16 KA TP MCCB | 1 | 1 | 6188 | 6188 | 6188 | 6188
|  | DSR ITEMS | [5 empty] | 224859
17 |  | Point wiring in PVC conduit, with Modular type switch: Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. | [5 empty] | 0
a |  | Group B | 5 | Point | 585 | 846.846 | 4234.23 | 2925
b |  | Group C | 32 | Point | 718 | 1039.3768 | 33260.0576 | 22976
18 |  | Twin control point wiring in PVC conduit, with modular type switch: Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. | 2 | Point | 770 | 1114.652 | 2229.304 | 1540 |  | 224859
19 |  | Power plug wiring in PVC conduit ( 2x4 sq mm ): Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 1 No 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 50 | Metre | 162 | 234.5112 | 11725.56 | 8100
20 |  | Circuit Sub main wiring in PVC Conduit: Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required |  |  |  | 0 | 0 | 0
| a | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | 60 | Metre | 106 | 153.4456 | 9206.736 | 6360
| b | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 80 | Metre | 131 | 189.6356 | 15170.848 | 10480
| c | 4 X 4 sq. mm + 2 X 4 sq. mm earth wire | 25 | Metre | 275 | 398.09 | 9952.25 | 6875
| d | 4 X 6 sq. mm + 2 X 6 sq. mm earth wire | 25 | Metre | 389 | 563.1164 | 14077.91 | 9725
|  | RE- WIRING IN PVC CONDUIT |  |  |  | 0 | 0 | 0
21 |  | Telephone wiring in existing conduit: Supplying and drawing following pair 0.5 sq mm FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. |  |  |  | 0 | 0 | 0
|  | 2 Pair | 50 | Metre | 18 | 26.0568 | 1302.84 | 900
|  | PVC CONDUIT, METAL BOXES |  | Metre |  | 0 | 0 | 0
22 |  | S/F PVC conduit: Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. |  |  |  | 0 | 0 | 0
| a | 20 mm | 100 | Metre | 146 | 211.3496 | 21134.96 | 14600
| b | 25 mm | 250 | Metre | 152 | 220.0352 | 55008.8 | 38000
| c | 40 mm | 20 | Metre | 110 | 159.236 | 3184.72 | 2200
23 |  | S/F Modular type switch/ socket: Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. |  |  |  | 0 | 0 | 0
| a | Telephone socket outlet | 2 | Each | 95 | 137.522 | 275.044 | 190
24 |  | Supplying and fixing electronic fan regulator: Supplying and fixing stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | 8 | Each | 284 | 411.1184 | 3288.9472 | 2272
25 |  | S/F Modular type blanking plates: Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | 12 | Each | 23 | 33.2948 | 399.5376 | 276
26 |  | S/F Modular boxes, base & cover plate: Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required. |  |  |  | 0 | 0 | 0
| a | 1 or 2 Module (75mmX75mm) | 20 | Each | 166 | 240.3016 | 4806.032 | 3320
27 |  | S/F light plug point modular type accessaries: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). | 16 | Each | 303 | 438.6228 | 7017.9648 | 4848
28 |  | S/F Power plug point with modular type switch: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 2 | Each | 395 | 571.802 | 1143.604 | 790
29 |  | S/F Ceiling rose: Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. | 15 | Each | 43 | 62.2468 | 933.702 | 645
30 |  | S/F call bell/buzzer: Supplying and fixing call bell/ buzzer suitable for single phase, 230 volts, complete as required. | 2 | Each | 61 | 88.3036 | 176.6072 | 122
31 |  | ITC Fluroscent/LED fitting directly on surface/celing: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | 35 | Each | 91 | 131.7316 | 4610.606 | 3185
32 |  | ITC Fluroscent fitting with down rod: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc., including supplying and fixing ball and socket arrangement, 2 no. down rods of 20 mm dia X 1.6 mm thick steel conduit upto 30 cm length, painting and wiring the down rods and connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | 8 | Each | 233 | 337.2908 | 2698.3264 | 1864
33 |  | S/F extra down rod: Providing and fixing extra conduit down rod of 20 mm dia, 2 X 10 cm length wiring with 2 X 1.5 sq. mm FR PVC insulated, copper conductor, single core cable including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | 16 | Each | 31 | 44.8756 | 718.0096 | 496
34 |  | ITC Ceiling fan: Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable etc. as required. | 8 | Each | 95 | 137.522 | 1100.176 | 760
35 |  | Extra down rod 15 mm dia 20 CM Length: Supplying and fixing extra conduit down rod of 20 cm length G.I. pipe 15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | 24 | Each | 27 | 39.0852 | 938.0448 | 648
36 |  | ITC Exhaust fan: Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. |  |  |  | 0 | 0 | 0
|  | Upto 450 mm sweep | 2 | Each | 204 | 295.3104 | 590.6208 | 408
37 |  | S/F SP MCB DB: Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) |  |  |  | 0 | 0 | 0
|  | 2 + 6/8 way, Double door | 2 | Each | 1041 | 1506.9516 | 3013.9032 | 2082
38 |  | S/F Vertical Type Pre Wired TP MCB DB: Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required ,suitable for MCCB incomer.(But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.) |  |  |  | 0 | 0 | 0
| 2.9.5 | 4 way Double door | 1 | Each | 7901 | 11437.4876 | 11437.4876 | 7901
39 |  | S/F 'C' series, MCB: Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | 0 | 0 | 0
a |  | Single pole | 8 | Each | 169 | 244.6444 | 1957.1552 | 1352
40 |  | S/F S P MCB blanking plate: Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | 10 | Each | 7 | 10.1332 | 101.332 | 70
41 |  | S/F DP MCB isolator: Supplying and fixing following rating, double pole, 240 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | 0 | 0 | 0
|  | 40 amps | 2 | Each | 218 | 315.5768 | 631.1536 | 436
42 |  | S/F SPN RCCB: Supplying and fixing following rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  | Each |  | 0 | 0 | 0
|  | 25 amps | 2 | Each | 1645 | 2381.302 | 4762.604 | 3290
43 |  | S/F 20A SPN MCB industrial socket outlet: Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 2 | Each | 954 | 1381.0104 | 2762.0208 | 1908
44 |  | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 1 | Each | 141 | 204.1116 | 204.1116 | 141
45 |  | G.I Earth Pipe Electrode With Salt & Charcoal: Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 2 | Each | 3926 | 5683.2776 | 11366.5552 | 7852
46 |  | Providing and fixing 4.00mm dia copper wire on surface or in recess: Providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 60 | metre | 86 | 124.4936 | 7469.616 | 5160
47 |  | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. |  |  |  | 0 | 0 | 0
|  | Upto 35 sq. mm | 35 | metre | 606 | 877.2456 | 30703.596 | 21210
48 |  | Supplying and making end termination with brass compression gland and aluminium lugs: Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. |  |  |  | 0 | 0 | 0
| 9.1.32 | 4 X 10 sq. mm (25mm) | 2 | Each | 193 | 279.3868 | 558.7736 | 386
| 9.1.33 | 4 X 16 sq. mm (28mm) | 2 | Each | 245 | 354.662 | 709.324 | 490
|  | TOTAL FOR PART-B |  |  |  |  | 509722.0708 | 449718
|  | GRAND TOTAL(PARTA+PART-B) |  |  |  |  | #REF!

## GSAB (hidden)
GENERAL ABSTRACT FOR THE SETTING UP OF CONFERENCE HALL IN KAKKANADU FACTORY,COCHIN
SI.NO | DESCRIPTION | AMOUNT
1 | CIVIL WORKS | 2171012.9672 | 2680735.038
2 | ELECTRICAL WORKS | 509722.0708
3 | AIRCONDITIONING WORKS | 168500
4 | FURNITURES | 245475
| TOTAL | 3094710.038
| ADD-5%CONTINGENCY | 154735.5019
| GRAND TOTAL | 3249445.5399
Note on C3: hll301982:

## ele (hidden)
Renovation Works at HLL Kakkanadu factory - Confrence Hall - Electrical Estimate(Part-B)
| Description | Unit | Quantity | SR-2014/LMR | Amount
1 | Surface mounted Indoor,decorative box type fitting, Retro LED cat ref. LTT8-20 with 20W LED Lamp having high efficiency PMMA diffuser giving soft glare free light of Crompton or Equi | Each | 9 | 3278 | 29502 | LMR
2 | Recess down lighter DN194B LED15S of Philips/Equi with lamp | Each | 8 | 2904 | 23232 | LMR
3 | Supply of Green square down lighter recessed BBS175 1xDLED of Philips or Equi with Lamp | Each | 4 | 1992 | 7968 | LMR
4 | Supply of Recess mounted full glow RC170B LED 29S of Philips or Equi with lamp | Each | 8 | 4646 | 37168 | LMR
5 | Supply & installation of LED Lamp Non Dimmable 7/9W B22 on existing angle batten | Each | 2 | 545 | 1090 | LMR
6 | Supply of Linnet - LCL-10-CDL,Sleek LED mirror light,with high out put diffuser, 2 feet size of Crompton or Equi | Each | 1 | 2091 | 2091 | LMR
7 | Supply of Indoor down lighter,recessed mounted LED down lights with the option for fixed/ adjustable and spot options. BBS312 1xDLED of Philips or Equi | Each | 6 | 2788 | 16728 | LMR
8 | Supply & Installation of LED strip light for indoor with driver, Beetle cat ref. LST20RGB of crompton or equi of 5 meter length | Set | 6 | 3336 | 20016 | LMR
9 | Supply of ceiling fan 1050/1200 mm sweep,230V,1Ph, complete with double ball bearing, motor blades, down rods, canopy, capacitor etc complete as required 5 star rating (Crompton Riviera / Usha Maxx Air / Khaitan Newtec) | Each | 8 | 2180 | 17440 | LMR
10 | Supply and installation of Decorative Wall fan 400 mm sweep, 230V.1Ph, complete with Openable mesh Cover ,string Operated etc as required. (Crompton WM Wind Flo / Usha Helix high speed / Khaitan Merlin Hi speed) | Each | 6 | 2698 | 16188 | LMR
11 | Supply and fitting 250 mm sweep automatic shutter Sleek and stylish design type exhaust fan complete with louvers and cable from ceiling rose / connector to fan. (Usha Crisp Air / Crompton Crossair / Khaitan Vento). | Each | 2 | 1393 | 2786 | LMR
12 | S/F PVC holder: Supplying and fixing PVC batten/ angle holder including connection etc. as required. | Each | 2 | 71 | 142 | LMR
13 | Supply & fixing INFORMATION OUTLET WITH FACE PLATE (concealed in modular work station raceways /gypboard partitions/ walls-with modular back box), TERMINATION AND TESTING CAT6 A (AMP/PANDUIT/Systimax) | Each | 10 | 760 | 7600 | LMR
14 | Supply of Alluminium cable. Supply of the following sizes of Alluminium armoured PVC insulated, XLPE Power cable of 1.1kV grade to site including transporting and stacking charges at work site.. |  |  |  |  | LMR
a | 4 X 16 sq. mm | Metre | 30 | 315 | 9450 | LMR
b | 4 X 10 sq. mm | Metre | 15 | 278 | 4170 | LMR
15 | Supplying and drawing of UTP 4 pair CAT -6A LAN cable in existing surface/ recessed PVC conduit as required, AMP/Molex make | Metre | 300 | 77 | 23100 | LMR
16 | S&F MCCB in cubicle Pannel: Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required. |  |  |  |  | LMR
| 63 Amp, 16 KA TP MCCB | Each | 1 | 6188 | 6188 | LMR
| Total LMR |  |  |  | 224859
17 | Point wiring in PVC conduit, with Modular type switch: Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
a | Group B | Point | 5 | 585 | 2925 | SR-2014
b | Group C | Point | 32 | 718 | 22976 | SR-2014
18 | Twin control point wiring in PVC conduit, with modular type switch: Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. | Point | 2 | 770 | 1540 | SR-2014
19 | Power plug wiring in PVC conduit ( 2x4 sq mm ): Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 1 No 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | Metre | 50 | 162 | 8100 | SR-2014
20 | Circuit Sub main wiring in PVC Conduit: Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required
a | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | Metre | 60 | 106 | 6360 | SR-2014
b | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | Metre | 80 | 131 | 10480 | SR-2014
c | 4 X 4 sq. mm + 2 X 4 sq. mm earth wire | Metre | 25 | 275 | 6875 | SR-2014
d | 4 X 6 sq. mm + 2 X 6 sq. mm earth wire | Metre | 25 | 389 | 9725 | SR-2014
| RE- WIRING IN PVC CONDUIT |  |  |  |  | SR-2014
21 | Telephone wiring in existing conduit: Supplying and drawing following pair 0.5 sq mm FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required.
| 2 Pair | Metre | 50 | 18 | 900 | SR-2014
| PVC CONDUIT, METAL BOXES |  |  |  |  | SR-2014
22 | S/F PVC conduit: Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
a | 20 mm | Metre | 100 | 146 | 14600 | SR-2014
b | 25 mm | Metre | 250 | 152 | 38000 | SR-2014
c | 40 mm | Metre | 20 | 110 | 2200 | SR-2014
23 | S/F Modular type switch/ socket: Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
a | Telephone socket outlet | Each | 2 | 95 | 190 | SR-2014
24 | Supplying and fixing electronic fan regulator: Supplying and fixing stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | Each | 8 | 284 | 2272 | SR-2014
25 | S/F Modular type blanking plates: Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | Each | 12 | 23 | 276 | SR-2014
26 | S/F Modular boxes, base & cover plate: Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.
a | 1 or 2 Module (75mmX75mm) | Each | 20 | 166 | 3320 | SR-2014
27 | S/F light plug point modular type accessaries: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). | Each | 16 | 303 | 4848 | SR-2014
28 | S/F Power plug point with modular type switch: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | Each | 2 | 395 | 790 | SR-2014
29 | S/F Ceiling rose: Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. | Each | 15 | 43 | 645 | SR-2014
30 | S/F call bell/buzzer: Supplying and fixing call bell/ buzzer suitable for single phase, 230 volts, complete as required. | Each | 2 | 61 | 122 | SR-2014
31 | ITC Fluroscent/LED fitting directly on surface/celing: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | Each | 35 | 91 | 3185 | SR-2014
32 | ITC Fluroscent fitting with down rod: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc., including supplying and fixing ball and socket arrangement, 2 no. down rods of 20 mm dia X 1.6 mm thick steel conduit upto 30 cm length, painting and wiring the down rods and connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | Each | 8 | 233 | 1864 | SR-2014
33 | S/F extra down rod: Providing and fixing extra conduit down rod of 20 mm dia, 2 X 10 cm length wiring with 2 X 1.5 sq. mm FR PVC insulated, copper conductor, single core cable including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | Each | 16 | 31 | 496 | SR-2014
34 | ITC Ceiling fan: Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable etc. as required. | Each | 8 | 95 | 760 | SR-2014
35 | Extra down rod 15 mm dia 20 CM Length: Supplying and fixing extra conduit down rod of 20 cm length G.I. pipe 15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | Each | 24 | 27 | 648 | SR-2014
36 | ITC Exhaust fan: Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required.
| Upto 450 mm sweep | Each | 2 | 204 | 408 | SR-2014
37 | S/F SP MCB DB: Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
| 2 + 6/8 way, Double door | Each | 2 | 1041 | 2082 | SR-2014
38 | S/F Vertical Type Pre Wired TP MCB DB: Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required ,suitable for MCCB incomer.(But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.)
2.9.5 | 4 way Double door | Each | 1 | 7901 | 7901 | SR-2014
39 | S/F 'C' series, MCB: Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | Single pole | Each | 8 | 169 | 1352 | SR-2014
40 | S/F S P MCB blanking plate: Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | Each | 10 | 7 | 70 | SR-2014
41 | S/F DP MCB isolator: Supplying and fixing following rating, double pole, 240 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
| 40 amps | Each | 2 | 218 | 436 | SR-2014
42 | S/F SPN RCCB: Supplying and fixing following rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
| 25 amps | Each | 2 | 1645 | 3290 | SR-2014
43 | S/F 20A SPN MCB industrial socket outlet: Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | Each | 2 | 954 | 1908 | SR-2014
44 | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | Each | 1 | 141 | 141 | SR-2014
45 | G.I Earth Pipe Electrode With Salt & Charcoal: Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | Each | 2 | 3926 | 7852 | SR-2014
46 | Providing and fixing 4.00mm dia copper wire on surface or in recess: Providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | Metre | 60 | 86 | 5160 | SR-2014
47 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
| Upto 35 sq. mm | Metre | 35 | 606 | 21210 | SR-2014
48 | Supplying and making end termination with brass compression gland and aluminium lugs: Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
9.1.32 | 4 X 10 sq. mm (25mm) | Each | 2 | 193 | 386 | SR-2014
9.1.33 | 4 X 16 sq. mm (28mm) | Each | 2 | 245 | 490 | SR-2014
| Total Amount in SR-2014 |  |  |  | 196783
ABSTRACT
| Total SR |  |  |  | 196783
| Add CI - 44.76% |  |  |  | 88080.0708 | 284863.0708
| Total LMR |  |  |  | 224859
| Grand Total Electrical |  |  |  | 509722.0708
| Say |  |  |  | 510000
Rupees Five Lakhs and Ten Thousand Only
Abraham Jacob
Project Engineer (Elec)
HLL Lifecare Ltd (ID -South)
Thiruvanathapuram

## AC (hidden)
Estimate for Air Conditioning Works inConference hall in Kakkanadu factory,Cochin-PART©
Sl No | Item Description | Unit | Quantity | Rate |  | Amount (Rs)
|  |  |  | DSR | NDSR | DSR | NDSR
1 | Supply, installation, testing and commissioning Ceiling Suspended Cassette type room Air-conditioner following capacity unit Single phase, compact cooling coil, electronic expansion valve, suction air grill, in built drain pump coated with silver ions to prevent slime, mould and bacterial growth, air filter with anti-mould and anti bacterial treatment & decorative panel. Out door unit with highly energy efficient Compressor with copper coils, first charge refrigarant gas and with MS stand. Unit to be capable of maintaining 22±1° C indoor condition with cordless remote with various features like 3 speed, auto manual selection etc also. Unit capable of 30 meter maximum interunit piping length and 15 maximum installation level difference. Decorative panel to be part of supply of units.
A | 2 TR, 800 CFM | Nos | 2 |  | 75000 |  | 150000
2 | Supply & installation Copper Refrigerant piping suitable for Cassette units, duly insulated with closed cell elastomeric nitrile rubber insulation, class-o, covered with two layers of shield coating, complete with elbows, T joints, sleeves etc., with GSS slotted rail supporting arrangement from ceiling/wall and GI clamp for individual pipes. | Rmts | 10 |  | 1000 |  | 10000
3 | Supply, installation, testing and commissioning PVC drain pipe ISI marked, connecting the drain lines from the indoor units to floor sump, with 9mm nitrile rubber insulation as per specification.
A | 25 mm Dia | Rmts | 15 |  | 200 |  | 3000
B | 32 mm Dia | Rmts | 10 |  | 220 |  | 2200
4 | Supply, Laying and Fixing of control wiring of suitable size required from the Indoor to outdoor units for all units as per specification. | Rmts | 15 |  | 220 |  | 3300
168500
One Lakh Sixty Eight Thousand and Five Hundred Rupees Only

## civil-+ELEab (hidden)
ESTIMATE FOR CIVILWORKS IN CONFERENCE HALL IN KAKKANADU FACTORY,COCHIN-PART-A
Item no. | DSR | Item Description | Qty | Unit | Rate | Rate+CI | Amount
CIVIL WORKS(PART-A)
1 | 15.2.2 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material as per direction of Engineer-in-charge. | 10 | Cum | 550.5 | 796.9038 | 7969.038
2 | 15.3 | Demolishing R.C.C. work manually/ by mechanical means includingstacking of steel bars and disposal of unserviceable material as per direction of Engineer - in- charge. | 1 | Cum | 1302.3 | 1885.2095 | 1885.2095
3 | 15.5 | Extra for cutting reinforcement bars manually/ by mechanical means inR.C.C. or R.B. work (Payment shall be made on the cross sectional areaof R.C.C. or R.B. work) as per direction of Engineer -in -charge. | 30 | Sqm | 450.45 | 652.0714 | 19562.1426 | 30
4 | 15.23.1 | Dismantling tile work in floors, dadoing and roofs laid in cement mortar including stacking material within 50 metres lead.For thickness of tiles up to 25 mm | 25 | Sqm | 28.2 | 40.8223 | 1020.558
5 | 15.5 | Dismantling of Water closets/wash basin/flushing cistern etc. of all types (C.I./PVC/Vitrious China) including stacking of useful materials near the site and disposal of unserviceable materials | 2 | Each | 519.87 | 752.5638 | 1505.1276 | 2 | Nos
6 | 15.6 | Disposal of building rubbish / malba / similar unserviceable, dismantled or waste materials by mechanical means including loading, transporting, unloading to approved municipal dumping ground or as approved by Engineer-in-charge, beyond 50 m initial lead, for all loads including all lifts involved. | 40 | Cum | 123.7 | 179.0681 | 7162.7248
7 | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30cm in depth. 1.5m in width as well as 10 sqm on plan) including disposal of excavated earth and lift upto 1.5m, disposed earth to be levelled and neatly dressed.:All kinds of soil | 3.375 | Cum | 155.6 | 225.2466 | 760.2071
8 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All works up to plinth level-.1:4:8 (1 Cement : 4 coarse sand : 8 graded stone aggregate 40mm nominal size) | 7.6855 | Cum | 4301.2 | 6226.4171 | 47853.3156
9 | 5.1.3 | Providing and laying in position specified grade of reinforced cementconcrete, excluding the cost of centering, shuttering, finishing andreinforcement - All work up to plinth level :1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) | 0.52 | Cum | 5725.9 | 8288.8128 | 4310.1827
10 | 5.3 | Reinforced cement concrete work in beams, suspended floors, roofs havingslope up to 15° landings, balconies, shelves, chajjas, lintels, bands, plainwindow sills, staircases and spiral stair cases up to floor five level, excludingthe cost of centering, shuttering, finishing and reinforcement, with 1:2:4 (1cement : 2 coarse sand : 4 graded stone aggregate 20 mmnominal size) | 1.6233 | Cum | 6778.2 | 9812.1223 | 15927.7238
11 | 5.37 | Providing and laying in position ready mixed M-25 grade concrete for reinforced cement concrete work, using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , excluding the cost of centering, shuttering finishing and reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, improve workability without impairing strength and durability as per direction of the Engineer - in - charge. |  |  |  | 0 | 0 | 0
|  | (Note :- Cement content considered in this item is @ 330 kg/cum. Excess/less cement used as per design mix is payable/recoverable separately). |  |  |  | 0 | 0 | 0
| 5.37.2 | All work above plinth level up to floor V level -RCC work (M25 concrete) | 22.3373 | Cum | 7363 | 10658.6788 | 238085.605
12 | 5.9 | Centering and shuttering including strutting, propping etc., and removal of form for, |  |  |  | 0 | 0 | 0
12.a | 5.9.1 | Foundations, Footings, bases of columns,etc for mass concrete. | 2.25 | Sqm | 196.45 | 284.381 | 639.8573
12.b | 5.9.6 | Columns and Pillars, Piers, Abutments, Posts and Struts. | 64 | Sqm | 453.35 | 656.2695 | 42001.2454
12.c | 5.9.3 | Suspended floors, roofs, landings, Balconies and access platform | 103 | Sqm | 453.35 | 656.2695 | 67595.7544
12.d | 5.9.5 | Lintel,beams,plinth beams,girders,bressumers and cantilevers | 74 | Sqm | 332.15 | 480.8203 | 35580.7052
12.e | 5.9.19 | Weather shade, Chajjas, corbels etc., including edges | 15 | Sqm | 492.35 | 712.7259 | 10690.8879
13 | 5.22.A.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending,placing in position and binding all complete above plinth level. :Thermo-Mechanically Treated bars | 2203.5283 | Kg | 68.1 | 98.5816 | 217227.2593
14 | 6.4.2 | Brick work with F.P.S bricks of class designation 5.0 in superstructure above plinth level up to floor v level in all shapes an sizes in: Cement mortar 1: 6 (1 cement :6 coarse sand) | 24.1605 | Cum | 5426.15 | 7854.8947 | 189778.4679
15 | 6.13.1 | Half brick masonry with F.P.S brick of class designation 7.5 in superstructure above plinth level up to floor V level : CM 1:3 (1 cement : 3 coarse sand) | 28.88 | Sqm | 692.8 | 1002.8973 | 28963.6734
16 | 6.15 | Extra for providing and placing in position 2 Nos. 6mm dia M.S bars at every third course of half brick masonry (with FPS brick) | 28.88 | Sqm | 69.5 | 100.6082 | 2905.5648
17 | 13.2.1 | 15mm cement plaster on the rough side of single or half brick wall of mix : 1 : 4 (1 cement : 4 fine sand) up to 10m height for external walls | 74 | Sqm | 189.4 | 274.1754 | 20288.9826
18 | 13.1.1 | 12mm cement plaster on the rough side of single or half brick wall of mix : 1 : 4 (1 cement : 4 fine sand) for internal walls, column and beams etc | 305.1168 | Sqm | 163.35 | 236.4655 | 72149.5845
19 | 13.16.1 | 6 mm cement plaster of mix : 1:3 (1 cement: 3 fine sand) for ceiling plastering | 93.1392 | Sqm | 134.7 | 194.9917 | 18161.3728
20 | 13.8 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. | 398.256 | Sqm | 89.65 | 129.7773 | 51684.6043
21 | 13.60.1 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade –Two or more coats on new work.-internal walls | 398.256 | Sqm | 80.5 | 116.5318 | 46409.4885
22 | 13.48.1 | Finishing walls with Acrylic Smooth exterior paint of required shade : New work (Two or more coat applied @ 1.67 ltr/10 sqmover and including priming coat of exterior primer applied @ 2.20 kg/ 10 sqm) | 74 | Sqm | 100 | 144.76 | 10712.24
23 | 13.48.3 | Painting Steel work with Delux Multi surface paint to give an even shade.Two or more coat applied @ 0.90 ltr/10sqm over an over an under coat of primer applied @ 0.80ltr/10aqm of approved brand or manufacture. | 3.315 | Sqm | 90 | 130.284 | 431.8915
24 | 8.2.2.2 | Providing and fixing 18mm thick gang saw cut mirror polished premoulded and prepolished) machine cut for kitchen platforms, vanity counters, window sills , facias and similar locations of required size of approved shade, colour and texture laid over 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels. Granite of any colour and shade: Area of slab over 0.50 sqm.: Lowest retail price not less than Rs. 2500.00/m2( Granite to be selected by the Engineer in charge) | 0.9 | Sqm | 2463.55 | 3566.235 | 3209.6115
25 | 9.117.1 | Providing and fixing factory made UPVC door frame made of UPVC extruded section having an overall dimensions as below ( tolerance ± 1mm ), with wall thickness 2.0mm (± 0.2mm), corners of the door frame to be joined with galvanized brackets and stainless steel screws, joints mitered and plastic welded. The hinged side vertical of the frames reinforced by galvanized M.S. tube of size 19x19 mm and 1mm (± 0.1mm) wall thickness and 3 nos. Stainless steel hinged fixed to the frame complete as per manufacturers Specification and direction of engineering -in-change : Extruded section profile size 48x40 mm | 6.72 | M | 213.75 | 309.4245 | 2079.3326
26 | 9.118.1 | Providing and fixing existing door frames: 24 mm thick factory made PVC door shutters made of styles and rails of a UPVC hollow section of size 59x24 mm and wall thickness 2 mm (± 0.2mm) with in built edging on both sides. The styles and rails mitered and joint at the corners by means of M.S. galvanized / plastic brackets of size 75x220 mm having wall thickness 1.0 mm and stainless steel screws. The styles of the shutter reinforced by inserting galvanized M.S. tube of size 20x20 mm and 1mm (± 0.1mm) wall thickness. The lock rail made up of " H" section, a UPVC hollow section of size 100x24 mm and 2mm (± 0.2mm) wall thickness, fixed to the shutters styles by means of plastic/ galvanized M.S.'U' cleats. The shutter frame filled with a UPVC multi chambered single panel of size not less than 620mm, having over all thickness of 20mm and 1mm (± 0.1mm) wall thickness. The panes filled vertically and tie bar at two places by inserting horizontally 6mm galvanized M.S. rod and fastened with nuts and washers, complete as per manufacturer's specification and direction of Engineer- in - charge. (for W,C and bath room door shutter). | 6.72 | Sqm | 2718.6 | 3935.4454 | 26446.1928
27 | 11.41.2 | Providing and laying polished vitrified floor tile in different sizes (thickness to be specified by the manufacturer) with Acid and / or Alkali resistant tiles with water absorptions less than 0.08% and confirming to IS:15622 of approved make in all colours and shades, laid on 20mm thick cement mortor 1:4 (1 cement:4 Coard sand) including grouting the joints with white cement and matching pigments etc. complete. (Lowest retail price not less than Rs. 880/m2) : Size of Tiles 60 x 60 cm (Tiles to be selected by the Engineer in charge) | 68.9249 | sqm | 1405.95 | 2035.2532 | 140279.6247
28 | 11.39 | Providing and laying rectified Glazed Ceramic floor tiles 300x300 mm or more (thickness to be specified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make in colours White, Ivory, Grey, Fume Red Brown, laid on 20mm thick cement mortar 1:4 (1 Cement : 4 Coarse sand) including grouting the joints with white cement and matching pigments etc., complete.(lowest price of tile not less than 650/m2) | 6.4904 | sqm | 950.05 | 1375.2924 | 8926.1977
29 | 11.4 | Providing and fixing Ist quality ceramic glazed wall tiles of size 300x450mm conforming to IS : 15622 (thickness to be specified by the manufacturer ) of approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados over 12 mm thick bed of cement Mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm including pointing in white cement mixed with pigment of matching shade complete.(.(lowest price of tile not less than 725/m2) | 25 | sqm | 1009.6 | 1461.497 | 36537.424
30 | 12.45 | Providing and fixing false ceiling at all height including providing and fixingof frame work made of special sections, power pressed from M.S. sheets and galvanized with zinc coating of 120 gms/sqm (both side inclusive) asper IS : 277 and consisting of angle cleats of size 25 mm wide x 1.6 mmthick with flanges of 27 mm and 37mm, at 1200 mm centre to centre, oneflange fixed to the ceiling with dash fastener 12.5 mm dia x 50mm long with6mm dia bolts, other flange of cleat fixed to the angle hangers of 25x10x0.50mm of required length with nuts & bolts of required size and other end ofangle hanger fixed with intermediate G.I. channels 45x15x0.9 mm runningat the spacing of 1200 mm centre to centre, to which the ceiling section0.5 mm thick bottom wedge of 80 mm with tapered flanges of 26 mm eachhaving lips of 10.5 mm, at 450 mm centre to centre, shall be fixed in adirection perpendicular to G.I. intermediate channel with connecting clipsmade out of 2.64 mm dia x 230 mm long G.I. wire at every junction, includingfixing perimeter channels 0.5 mm thick 27 mm high having flanges of 20mm and 30 mm long, the perimeter of ceiling fixed to wall/partition with the |  |  |  | 0 | 0
help of rawl plugs at 450 mm centre, with 25mm long dry wall screws @230 mm interval, including fixing of gypsum board to ceiling section andperimeter channel with the help of dry wall screws of size 3.5 x 25 mm at230 mm c/c, including jointing and finishing to a flush finish of tapered andsquare edges of the board with recomme-nded jointing compound ,
| 12.45.1 | 12.5 mm thick tapered edge gypsum plain board conformingto IS: 2095- Part I | 48.1626 | sqm | 907.1 | 1313.118 | 63243.1751 | #VALUE! | sqm
31 | 21.1.1.2 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) : For fixed portion: Powder coated aluminium (minimum thickness of powder coating 50 micron) | 115.83 | kg | 377.75 | 546.8309 | 63339.4231
32 | 21.1.2.2 | For shutters of doors, windows & ventilators including providing and fixing hinges/ pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately). Powder coated aluminium (minimum thickness of powder coating 50 micron) | 75.6 | Kg | 435.75 | 630.7917 | 47687.8525
33 | 21.3.2 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.5 mm thickness | 15.12 | sqm | 1054.2 | 1526.0599 | 23074.026
34 | 21.8 | Filling the gap in between aluminium frame & adjacent RCC/Brick/Stone work by providing weather silicon sealant over backer rod of approved quality as per architectural drawings and direction of Enginner-in-charge complete. |  |  |  | 0 | 0
| 21.8.1 | Upto 5mm depth and 5mm width | 10 | Rm | 88.75 | 128.4745 | 1284.745
35 | 21.18 | Providing and fixing 12 mm thick frameless toughened glass door shutter of approved brand and manufacture, including providing and fixing top & bottom pivot & spring type fixing arrangement and making necessary holes etc. for fixing required door fitings, all complete as per direction of Engineer-in-charge ( Door handle, lock and stopper etc. to be paid separately) | 2.7 | Sqm | 4746.3 | 6870.7439 | 18551.0085
36 | MR | Providing and fixing arrangement and making necessary holes etc. for fixing required door fitings, all complete as per direction of Engineer-in-charge Door handle, lock and stopper etc. | 6 | Each | 126 |  | 756
37 | 9.83 | Providing and fixing aluminium die cast body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 35 kg and door width upto 700 mm) with necessary accessories and screws etc. complete. | 2 | Each | 753.75 | 1091.1285 | 2182.257
38 | 9.97 | Providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade with necessary screws etc., complete. |  |  |  | 0 | 0
| 9.97.2 | 250 x 10mm | 8 | Each | 95.25 | 137.8839 | 1103.0712
| 9.97.4 | 150 x 10mm | 8 | Each | 65.35 | 94.6007 | 756.8053
39 | 21.13 | Providing and fixing 100mm brass locks (best make of approved quality) for aluminum doors including necessary cutting and making good etc. complete | 8 | Each | 418.65 | 606.0377 | 4848.3019
40 | 21.12.2 | Providing and fixing aluminium tubular handle bar 32 mm outer dia, 3.0 mm thick & 2100 mm long with SS screws etc .complete as per direction of Engineer-in-Charge. Powder coated minimum thickness 50 micron aluminium tubular handle bar. | 8 | Each | 508.55 | 736.177 | 5889.4158
41 | 9.101 | Providing and fixing aluminium hanging floor door stopper ISI marked anodised (anodic coating note less than grade AC 10 as per IS : 1868) transparent or dyed to required colour and shade with necessary screws etc., complete. |  |  |  | 0 | 0
| 9.101.1 | Single rubber stopper | 3 | Each | 37.5 | 54.285 | 162.855
42 | 21.4 | Providing and fixing double action hydraulic floor spring of approved brand and manufacture IS : 6315 marked, for doors including cost of cutting floors as required, embedding in floors and cover plates with brass pivot and single piect M.S. sheet outer box with side plate etc., complete as per the direction of Engineer-in-charge. |  |  |  | 0 | 0
| 21.4.2 | With brass cover plate | 1 | Each | 2213.2 | 3203.8283 | 3203.8283
43 | 9.149 | Providing and fixing casement handle made of zinc alloyed (white powder coated) for uPVC casement window with necessary screws etc. complete. | 4 | Each | 216.65 | 313.6225 | 1254.4902
44 | 9.68.1 | Providing and fixing oxidised M.S. casement stays (straight peg type) with necessary screws etc. Complete-300 mm weighing not less than 200 gms | 8 | Each | 36.2 | 52.4031 | 419.225
45 | LMR | Providing and fixing wash basin (counter type) with CI / MS brackets, 15mm CP brass Pillar taps, 32mm CP brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever required.: White Vitreous China Wash basin size 630 x 450mm with a single 15mm C.P brass piller tap. Make:Hindware,Cera,Jaquar etc.., (Lowest retail price of basin not less than Rs. 3000/each and Pillar tap not less than Rs. 2000/each. Materials to be selected by the Engineer in charge) | 2 | Each | 6732.75 |  | 13465.5
46 | M.R | Providing and fixing white vitreous china Wall Mounted type water closet (European type W.C.pan) with seat and lid, 3/6 litre low level white vitrous Dual Flushing cistern and C.P flush bend with fitting and C.I brackets, 40mm flush bend, overflow arrangement with specials of standard make and mosquito proof coupling of approved municipal design complete including painting of fittings and brackets, cutting and making good the walls and floors wherever required. Make:Hindware,Cera,Jaquar etc.., WC pan with ISI marked white solid plastic seat and lid (Lowest retail price not less than 10,000/each. Materials to be selected by the Engineer in charge) | 2 | Each | 13797.5 |  | 27595
47 | LMR | Providing and fixing C.P. brass long body bib cock of (2 in 1 type)approved quality conforming to IS standards and weighing not less than 690 gms.: 15 mm nominal bore: Make:Jauqar, Hindware, Parryware, crome | 2 | Each | 1540 |  | 3080 | 2 | nos
48 | 17.28.1.1 | Providing and fixing PVC Waste pipe for sink or wash basin including PVC waste fittings complete.:Semi rigid pipe 32mm dia | 2 | Each | 76.75 | 111.1033 | 222.2066 | 2 | nos
49 | 17.34.1 | Providing and fixing Toilet paper holder . Make:Hindware,Cera,Jaquar etc..,:C.P Brass | 1 | Each | 415.9 | 602.0568 | 602.0568 | 2 | nos
50 | 18.65 | Providing and fixing SS soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements. Weighing not less than 106 gms. | 1 | Each | 164.95 | 238.7816 | 238.7816 | 3 | nos
51 | 17.31 | Providing and fixing 600 x 450mm bevelled edge mirror of superior glass (of approved quality) complete with 6mm thick hard board ground fixed to wooden cleats with C.P. brass screws and washers complete. | 1 | Each | 793.95 | 1149.322 | 1149.322 | 1 | nos
52 | 17.73.2 | Providing and fixing SS towel rail complete with brackets fixed to wooden cleats with CP brass screws with concealed fitting arrangement of approved quality and colour. 600mm long towel rail with total length of 645mm, width 78mm and effective height of 88mm, weighing not less than 190gms. | 1 | Each | 541.5 | 783.8754 | 783.8754 | 3 | nos
53 | LMR | Providing & fixing of CP Health faucet. Hand operated spray unit( Instand type)).Make:Jauqar, Hindware, Parryware, crome., (Lowest retail price not less than 1200/each. Materials to be selected by the Engineer in charge) | 2 | Each | 2043 |  | 4086 | 2
54 | LMR | Providing and fixing PVC pipes for water supply arrangements including cost pipes, fittings, solvent cement,testing of pipes, labour charges etc complete : Concealed work including cutting chases and making good the wall etc |  |  |  | 0 | 0
|  | 20mm nominal outer dia .Pipes. (10kg/cm2) | 20 | RM | 220 |  | 4400
|  | 32mm nominal outer dia .Pipes. (10kg/cm2) | 20 | RM | 236 |  | 4720
55 | LMR | Providing and fixing PVC soil, waste and vent pipe to IS : 13592 of SWR quality, including all fittings, like EG : Bends, Tees, Elbows, Collars, junction, inspection doors, cowls, offsets, access pipes, jointing with rubber ring / solvent cement by application of leak proof adhesive like FRP paste including cutting holes in walls and floors and making good. Make: Supreme, Finolex, Astral |  |  |  | 0 | 0
|  | 50mm dia (6kg / sq.cm) | 20 | RM | 260.45 |  | 5209
|  | 63mm dia (6kg / sq.cm) | 25 | RM | 306 |  | 7650
|  | 75mm dia (6kg / sq.cm) | 20 | RM | 407 |  | 8140
|  | 110mm dia (6 kg / sq.cm) | 20 | RM | 557 |  | 11140
56 | 18.77 | Cutting holes upto 15 x 15 cm in R.C.C. floors and roofs for passing drain pipe etc. and repairing the hole after insertion of drain pipe etc. with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) including finishing complete. | 1 | Each | 193 | 279.3868 | 279.3868
57 | 12.41.2 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A including jointing with seal ring conforming to IS : 5382 leaving 10 mm gap for thermal expansion.(i) Single socketed pipes. 110 mm diameter | 8 | RM | 231.65 | 335.3365 | 2682.6923
58 | MR | Providing and fixing PVC floor trap self cleansing design with or without vent arm complete including cutting and making good the walls and floors. Make:Supreme,Finolex,Prince etc.., | 2 | Each | 519 |  | 1038
|  | 110mm dia inlet 110mm dia outlet |  |  |  | 0 | 0 | 2
59 | 18.58.2.1 | Providing and fixing PTMT grating of approved quality and colour.:Rectangular type with openable circular lid.150 mm nominal size square 100 mm diameter of the inner hinged round grating | 3 | Each | 220.45 | 319.1234 | 957.3703
60 | LMR | Providing and fixing C.P. brass pillar cock (push type)approved quality conforming to IS standards and weighing not less than 690 gms.: 15 mm nominal bore for wash basins: Make:Jauqar, Hindware, Parryware, crome | 2 | Each | 2706 |  | 5412 | 3 | nos
61 | 26.1 | Providing and supplying aluminium extruded tubular and other aluminium sections as per the architectural drawings and approved shop drawings , the aluminium quality as per grade 6063 T5 or T6 as per BS 1474,including super durable powder coating of 60-80 microns conforming to AAMA 2604 of required colour and shade as approved by the Engineer-in-Charge. ( The item includes cost of material such as cleats, sleeves, screws etc. necessary for fabrication of extruded aluminium frame work. Nothing extra shall be paid on this account). | 65 | Kg | 338.25 | 489.6507 | 31827.2955
62 | 26.2 | Designing, fabricating, testing, protection, installing and fixing in positionsemi (grid) unitized system of structural glazing (with open joints) for linearas well as curvilinear portions of the building for all heights and all levels,including:a) Structural analysis & design and preparation of shop drawings for thespecified design loads conforming to IS 875 part III (the system mustpassed the proof test at 1.5 times design wind pressure without anyfailure), including functional design of the aluminum sections for fixing glazing panels of various thicknesses, aluminium cleats, sleeves and c) Providing and filling, two part pump filled, structural silicone sealant and one part weather silicone sealant compatible with the structuralsilicone sealant of required bite size in a clean and controlled factory /work shop environment , including double sided spacer tape, setting blocks and backer rod, all of approved grade, brand and manufacture,as per the approved sealant design, within and all around the perimeterd) Providing and fixing in position flashings of solid aluminium sheet mm thick and of sizes, shapes and profiles, as required as per the site conditions, to seal the gap between the building structure and all its interfaces with curtain glazing to make it watertighte) Making provision for drainage of moisture/ water that enters the curtainglazing system to make it watertight, by incorporating principles of required), making necessary holes of required sizes and of requirednumbers etc. complete. This item includes cost of all inputs ofsplice plates etc. gaskets, screws, toggles, nuts, bolts, clamps etc., structural and weather silicone sealants, flashings, fire stop (barrier)-cum-smoke seals, microwave cured EPDM gaskets for water tightness, pressure equalisation & drainage and protection against fire hazardincluding:b) Fabricating and supplying serrated M.S. hot dip galvanised / Aluminiumalloy of 6005 T5 brackets of required sizes, sections and profiles etc.to accommodate 3 Dimentional movement for achieving perfectverticality and fixing structural glazing system rigidly to theRCC/masonry/structural steel framework of building structure using stainless steel anchor fasteners/ bolts, nylon seperator to prevent bimetallic contacts with nuts and washers etc. of stainless steel grade 316, of the required capacity and in required numbers | 9.38 | Sqm | 2556.2 | 3700.3551 | 34709.331
|  | installation of glazed units, T&P, scaffolding and other incidental charges including wastages etc., enabling temporary structures and services, cranes or cradles etc. as described above and as specified. The item includes the cost of getting all the structural and functional design including shop drawings checked by a structural designer, dully approved by Engineer-in-charge. The item also includes the cost of all mock ups at site, cost of all samples of the individual components for testing in an approved laboratory, field tests on the assembled working structural glazing as specified, cleaning and protection till the handing over of the building for occupation. In the end, the Contractor shall provide a water tight structural glazing having all the performance characteristics etc. all complete as required, as per the Architectural drawings, as per item description, as specified, as per the approved shop drawings and as directed by the Engineerin-Charge. |  |  |  | 0 | 0
|  | Note:- 1. The cost of providing extruded aluminium frames, shadow boxes, extruded aluminium section capping for fixing in the grooves of the curtain glazing and vermin proof stainless steel wire mesh shall be paid for separately under relevant items under this subhead. However, for the purpose of payment, only the actual area of structural glazing (including width of grooves ) on the external face shall be measured in sqm. up to two decimal places. Note:-2. The following performance test are to be conducted on structural glazing system if area of structural glazing exceeds 2500 Sqm from the certified laboratories accreditated by NABL(National Accreditation Board for Testing and Calibration Laboratories), Department of Science & Technologies, India. Cost of testing is payable separately. The NIT approving authority will decide the necessity of testing on the basis of cost of the work, cost of the test and importance of the work. Performance Testing of Structural glazing system Tests to be conducted in the NBL Certified laboratories |  |  |  | 0 | 0
63 | LMR | Providing and fixing poly carbonate (multi wall 6mm or nearest size) sheet roofing of approved make and quality fixed with polymer coated J or L hooks, bolts and nuts of required diameter with necessary washers complete including the cost of M.S square tube 50x25mm 16 gauge fixed with MS flat 25x6mm including necessary nuts and bolts to support the roofing,painting witn two or more coatswaithsyntheticenamel paint over a priming coat of Zinchromate primer etc complete. | 6.22 | Sqm | 2785.59 |  | 17326.3698
64 | 10.2 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete: | 70 | Kg | 73.95 | 107.05 | 7493.5014
65 | LMR | WALL PANEL for acoustic treatment - -Supply and fixing of Keiler/equivalent make 6 mm Polyester Fiber panel, fixed on GI Channel filled with 48kg/ dencityx 50 mm thick rock wool backing with black fleece cloth of 120 GSM. | 64.955 | sqm | 5400 |  | 350757 |  |  | 2680735.038
66 | LMR | Supplying and fixing white board(3x1.50m) with necessary arrangements | 4.5 | sqm | 1500 |  | 6750
67 | LMR | Supply and installation of DCP type fire extinguisher of 6 kg. Capacity complete with initial charges and installation brackets complete with installation brackets with ISI mark IS:15638 | 1 | Each | 2800 |  | 2800
|  | TOTAL(PART-A) |  |  |  | 0 | 2171012.9672 | 217104.12 |  | 2171014.12
LMR ITEMS
1 |  | Surface mounted Indoor,decorative box type fitting, Retro LED cat ref. LTT8-20 with 20W LED Lamp having high efficiency PMMA diffuser giving soft glare free light of Crompton or Equi | 9 | Each | 3278 |  | 29502
2 |  | Recess down lighter DN194B LED15S of Philips/Equi with lamp | 8 | Each | 2904 |  | 23232
3 |  | Supply of Green square down lighter recessed BBS175 1xDLED of Philips or Equi with Lamp | 4 | Each | 1992 |  | 7968
4 |  | Supply of Recess mounted full glow RC170B LED 29S of Philips or Equi with lamp | 8 | Each | 4646 |  | 37168
5 |  | Supply & installation of LED Lamp Non Dimmable 7/9W B22 on existing angle batten | 2 | Each | 545 |  | 1090
6 |  | Supply of Linnet - LCL-10-CDL,Sleek LED mirror light,with high out put diffuser, 2 feet size of Crompton or Equi | 1 | Each | 2091 |  | 2091
7 |  | Supply of Indoor down lighter,recessed mounted LED down lights with the option for fixed/ adjustable and spot options. BBS312 1xDLED of Philips or Equi | 6 | Each | 2788 |  | 16728
8 |  | Supply & Installation of LED strip light for indoor with driver, Beetle cat ref. LST20RGB of crompton or equi of 5 meter length | 6 | set | 3336 |  | 20016
9 |  | Supply of ceiling fan 1050/1200 mm sweep,230V,1Ph, complete with double ball bearing, motor blades, down rods, canopy, capacitor etc complete as required 5 star rating (Crompton Riviera / Usha Maxx Air / Khaitan Newtec) | 8 | Each | 2180 |  | 17440
10 |  | Supply and installation of Decorative Wall fan 400 mm sweep, 230V.1Ph, complete with Openable mesh Cover ,string Operated etc as required. (Crompton WM Wind Flo / Usha Helix high speed / Khaitan Merlin Hi speed) | 6 | Each | 2698 |  | 16188
11 |  | Supply and fitting 250 mm sweep automatic shutter Sleek and stylish design type exhaust fan complete with louvers and cable from ceiling rose / connector to fan. (Usha Crisp Air / Crompton Crossair / Khaitan Vento). | 2 | Each | 1393 |  | 2786
12 |  | S/F PVC holder: Supplying and fixing PVC batten/ angle holder including connection etc. as required. | 2 | Each | 71 |  | 142
13 |  | Supply & fixing INFORMATION OUTLET WITH FACE PLATE (concealed in modular work station raceways /gypboard partitions/ walls-with modular back box), TERMINATION AND TESTING CAT6 A (AMP/PANDUIT/Systimax) | 10 | Each | 760 |  | 7600
14 |  | Supply of Alluminium cable. Supply of the following sizes of Alluminium armoured PVC insulated, XLPE Power cable of 1.1kV grade to site including transporting and stacking charges at work site.. |  |  |  |  | 0
a |  | 4 X 16 sq. mm | 30 | Metre | 315 |  | 9450
b |  | 4 X 10 sq. mm | 15 | Metre | 278 |  | 4170
15 |  | Supplying and drawing of UTP 4 pair CAT -6A LAN cable in existing surface/ recessed PVC conduit as required, AMP/Molex make | 300 | Metre | 77 |  | 23100
16 |  | S&F MCCB in cubicle Pannel: Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required. |  |  |  |  | 0
|  | 63 Amp, 16 KA TP MCCB | 1 | 1 | 6188 |  | 6188
DSR ITEMS
17 |  | Point wiring in PVC conduit, with Modular type switch: Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
a |  | Group B | 5 | Point | 585 | 846.846 | 4234.23
b |  | Group C | 32 | Point | 718 | 1039.3768 | 33260.0576
18 |  | Twin control point wiring in PVC conduit, with modular type switch: Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. | 2 | Point | 770 | 1114.652 | 2229.304 |  |  | 224859
19 |  | Power plug wiring in PVC conduit ( 2x4 sq mm ): Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 1 No 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | 50 | Metre | 162 | 234.5112 | 11725.56
20 |  | Circuit Sub main wiring in PVC Conduit: Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required |  |  |  | 0 | 0
| a | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | 60 | Metre | 106 | 153.4456 | 9206.736
| b | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 80 | Metre | 131 | 189.6356 | 15170.848
| c | 4 X 4 sq. mm + 2 X 4 sq. mm earth wire | 25 | Metre | 275 | 398.09 | 9952.25
| d | 4 X 6 sq. mm + 2 X 6 sq. mm earth wire | 25 | Metre | 389 | 563.1164 | 14077.91
|  | RE- WIRING IN PVC CONDUIT |  |  |  | 0 | 0
21 |  | Telephone wiring in existing conduit: Supplying and drawing following pair 0.5 sq mm FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. |  |  |  | 0 | 0
|  | 2 Pair | 50 | Metre | 18 | 26.0568 | 1302.84
|  | PVC CONDUIT, METAL BOXES |  | Metre |  | 0 | 0
22 |  | S/F PVC conduit: Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. |  |  |  | 0 | 0
| a | 20 mm | 100 | Metre | 146 | 211.3496 | 21134.96
| b | 25 mm | 250 | Metre | 152 | 220.0352 | 55008.8
| c | 40 mm | 20 | Metre | 110 | 159.236 | 3184.72
23 |  | S/F Modular type switch/ socket: Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. |  |  |  | 0 | 0
| a | Telephone socket outlet | 2 | Each | 95 | 137.522 | 275.044
24 |  | Supplying and fixing electronic fan regulator: Supplying and fixing stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | 8 | Each | 284 | 411.1184 | 3288.9472
25 |  | S/F Modular type blanking plates: Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | 12 | Each | 23 | 33.2948 | 399.5376
26 |  | S/F Modular boxes, base & cover plate: Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required. |  |  |  | 0 | 0
| a | 1 or 2 Module (75mmX75mm) | 20 | Each | 166 | 240.3016 | 4806.032
27 |  | S/F light plug point modular type accessaries: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). | 16 | Each | 303 | 438.6228 | 7017.9648
28 |  | S/F Power plug point with modular type switch: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 2 | Each | 395 | 571.802 | 1143.604
29 |  | S/F Ceiling rose: Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. | 15 | Each | 43 | 62.2468 | 933.702
30 |  | S/F call bell/buzzer: Supplying and fixing call bell/ buzzer suitable for single phase, 230 volts, complete as required. | 2 | Each | 61 | 88.3036 | 176.6072
31 |  | ITC Fluroscent/LED fitting directly on surface/celing: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | 35 | Each | 91 | 131.7316 | 4610.606
32 |  | ITC Fluroscent fitting with down rod: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc., including supplying and fixing ball and socket arrangement, 2 no. down rods of 20 mm dia X 1.6 mm thick steel conduit upto 30 cm length, painting and wiring the down rods and connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | 8 | Each | 233 | 337.2908 | 2698.3264
33 |  | S/F extra down rod: Providing and fixing extra conduit down rod of 20 mm dia, 2 X 10 cm length wiring with 2 X 1.5 sq. mm FR PVC insulated, copper conductor, single core cable including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | 16 | Each | 31 | 44.8756 | 718.0096
34 |  | ITC Ceiling fan: Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable etc. as required. | 8 | Each | 95 | 137.522 | 1100.176
35 |  | Extra down rod 15 mm dia 20 CM Length: Supplying and fixing extra conduit down rod of 20 cm length G.I. pipe 15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | 24 | Each | 27 | 39.0852 | 938.0448
36 |  | ITC Exhaust fan: Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. |  |  |  | 0 | 0
|  | Upto 450 mm sweep | 2 | Each | 204 | 295.3104 | 590.6208
37 |  | S/F SP MCB DB: Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) |  |  |  | 0 | 0
|  | 2 + 6/8 way, Double door | 2 | Each | 1041 | 1506.9516 | 3013.9032
38 |  | S/F Vertical Type Pre Wired TP MCB DB: Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required ,suitable for MCCB incomer.(But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.) |  |  |  | 0 | 0
| 2.9.5 | 4 way Double door | 1 | Each | 7901 | 11437.4876 | 11437.4876
39 |  | S/F 'C' series, MCB: Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | 0 | 0
a |  | Single pole | 8 | Each | 169 | 244.6444 | 1957.1552
40 |  | S/F S P MCB blanking plate: Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | 10 | Each | 7 | 10.1332 | 101.332
41 |  | S/F DP MCB isolator: Supplying and fixing following rating, double pole, 240 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  | 0 | 0
|  | 40 amps | 2 | Each | 218 | 315.5768 | 631.1536
42 |  | S/F SPN RCCB: Supplying and fixing following rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  | Each |  | 0 | 0
|  | 25 amps | 2 | Each | 1645 | 2381.302 | 4762.604
43 |  | S/F 20A SPN MCB industrial socket outlet: Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 2 | Each | 954 | 1381.0104 | 2762.0208
44 |  | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 1 | Each | 141 | 204.1116 | 204.1116
45 |  | G.I Earth Pipe Electrode With Salt & Charcoal: Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 2 | Each | 3926 | 5683.2776 | 11366.5552
46 |  | Providing and fixing 4.00mm dia copper wire on surface or in recess: Providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | 60 | metre | 86 | 124.4936 | 7469.616
47 |  | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. |  |  |  | 0 | 0
|  | Upto 35 sq. mm | 35 | metre | 606 | 877.2456 | 30703.596
48 |  | Supplying and making end termination with brass compression gland and aluminium lugs: Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. |  |  |  | 0 | 0
| 9.1.32 | 4 X 10 sq. mm (25mm) | 2 | Each | 193 | 279.3868 | 558.7736
| 9.1.33 | 4 X 16 sq. mm (28mm) | 2 | Each | 245 | 354.662 | 709.324
|  | TOTAL FOR PART-B |  |  |  |  | 509722.0708

## details (hidden)
DETAILED MTS FOR CIVIL WORKS OF CONFERENCE HALL N KAKKANADU FACTORY,COCHIN
Item no. | DSR | Item Description | Nos | L | B | H | Qty | Unit
1 | 15.2.2 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge.In cement mortar
|  | top parapet length | 2 | 13.06 | 0.12 | 0.75 | 2.3508
|  |  | 2 | 5.55 | 0.12 | 0.75 | 0.999
|  | Toilet dismantling | 2 | 5.6 | 0.115 | 2.4 | 3.0912
|  | Total |  |  |  |  | 6.441 | m3
|  | say |  |  |  |  | 10
2 | 15.3 | Demolishing R.C.C. work manually/ by mechanical means includingstacking of steel bars and disposal of unserviceable material within 50metres lead as per direction of Engineer - in- charge.
|  | existing shade | 1 | 3.36 | 0.1 | 0.75 | 0.252 | m3
|  | Total qty in M3 |  |  |  |  | 0.252 | m3
|  | Say |  |  |  |  | 1 | m3
3 | 15.5 | Extra for cutting reinforcement bars manually/ by mechanical means in R.C.C. or R.B. work (Payment shall be made on the cross sectional areaof R.C.C. or R.B. work) as per direction of Engineer -in -charge. | sqm |  |  |  | 30
4 | 15.23.1 | Dismantling tile work in floors, dadoing and roofs laid in cement mortar including stacking material within 50 metres lead.For thickness of tiles up to 25 mm
|  | toilet -1 | 2 | 1.1 |  | 2.1 | 4.62
|  |  | 2 | 1.4 |  | 2.1 | 5.88
|  | floor | 1 | 1.4 |  | 1.1 | 1.54
|  | toilet -2 | 2 | 1.1 |  | 2.1 | 4.62
|  |  | 2 | 1.4 |  | 2.1 | 5.88
|  | floor | 1 | 1.4 |  | 1.1 | 1.54
|  | Total qty in sqm |  |  |  |  | 24.08
|  | Total qty in Sqm |  |  |  |  | 25 | sqm
5 |  | Dismantling of Water closets/wash basin/flushing cistern etc. of all types (C.I./PVC/Vitrious China) including stacking of useful materials near the site and disposal of unserviceable materials within 50 metres lead. |  |  |  |  | 2 | Nos
6 | 15.6 | Disposal of building rubbish / malba / similar unserviceable, dismantled or waste materials by mechanical means including loading, transporting, unloading to approved municipal dumping ground or as approved by Engineer-in-charge, beyond 50 m initial lead, for all loads including all lifts involved.
|  | Total qty |  |  |  |  | 35.252
|  | Say |  |  |  |  | 40 | m3
7 | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30cm in depth. 1.5m in width as well as 10 sqm on plan) including disposal of excavated earth and lift upto 1.5m, disposed earth to be levelled and neatly dressed.:All kinds of soil
|  | Excavtion for footing | 1 | 1.5 | 1.5 | 1.5 | 3.375 | m3
8 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All works up to plinth level-.1:4:8 (1 Cement : 4 coarse sand : 8 graded stone aggregate 40 mm nominal size)
|  | Excavtion for footing | 1 | 1.2 | 1.2 | 0.1 | 0.144 | m3
|  | conference room | 1 | 10.14 | 5.55 | 0.1 | 5.6277 | sqm
|  |  | 1 | 1.7 | 3.15 | 0.1 | 0.5355 | sqm
|  |  | 1 | 2.33 | 3.13 | 0.1 | 0.72929
|  | Toilets-Floor | 1 | 1.1 | 1.4 | 0.1 | 0.154
|  |  | 1 | 1.1 | 1.4 | 0.1 | 0.154
|  | wash area | 1 | 2.32 | 1.47 | 0.1 | 0.34104
7.6855
|  | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All works up to plinth level-.1:4:8 (1 Cement : 4 coarse sand : 8 graded stone aggregate 40mm nominal size) |  |  |  |  | 0
| a | footing | 1 | 1.2 | 1.2 | 0.3 | 0.432
|  | pedastal | 1 | 0.45 | 0.45 | 0.45 | 0.091125
|  | Total qty in m3 |  |  |  |  | 0.52312
9 | 5.37 | Providing and laying in position ready mixed M-25 grade concrete for reinforced cement concrete work, using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , excluding the cost of centering, shuttering finishing and reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, improve workability without impairing strength and durability as per direction of the Engineer - in - charge. |  |  |  |  | 0.52312 | cum
| 5.37.2 | (Note :- Cement content considered in this item is @ 330 kg/cum. Excess/less cement used as per design mix is payable/recoverable separately).
| b | Columns
|  | DG side-GF | 1 | 0.3 | 0.6 | 4 | 0.72
|  | Columns-conference room -FF | 8 | 0.3 | 0.6 | 3.45 | 4.968
|  | DG side-FF | 1 | 0.3 | 0.6 | 3.45 | 0.621
| c | Slab
|  | Roof for Dg set-GF | 1 | 2.56 | 3.36 | 0.12 | 1.0322
|  | top slab of Dg set room | 1 | 2.56 | 3.36 | 0.12 | 1.0322
|  | Conference room | 1 | 5.56 | 14 | 0.12 | 9.3408
| g | Roof beam | 2 | 13.52 | 0.23 | 0.33 | 2.0523
|  |  | 4 | 5.55 | 0.23 | 0.33 | 1.685
| h | Ground floor roof beam | 1 | 3.33 | 0.23 | 0.33 | 0.25275
|  |  | 1 | 2.5 | 0.23 | 0.33 | 0.18975
|  |  | 1 | 3.33 | 0.23 | 0.33 | 0.25275
|  |  | 1 | 2.51 | 0.23 | 0.33 | 0.19051
|  | total qty in m3 |  |  |  |  | 22.3373 | m3
|  | say |  |  |  |  | 22.3373
Reinforced cement concrete work in beams, suspended floors, roofs having slope up to 15° landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases up to floor five level, excluding the cost of centering, shuttering, finishing and reinforcement, with 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size).
| d | Lintel | 1 | 1.98 | 0.23 | 0.15 | 0.06831
|  |  | 1 | 11.78 | 0.23 | 0.15 | 0.40641
|  |  | 1 | 3 | 0.23 | 0.15 | 0.1035
|  |  | 1 | 5 | 0.23 | 0.15 | 0.1725
| e | shade | 1 | 12.89 | 0.6 | 0.075 | 0.58005
|  |  | 1 | 5 | 0.6 | 0.075 | 0.225
| f | wash slab | 1 | 1.5 | 0.6 | 0.075 | 0.0675 | m3
1.6233
10 | 5.9 | Centering and shuttering including strutting, propping etc., and removal of form for,
10.a | 5.9.1 | Foundations, Footings, bases of columns,etc for mass concrete. | 1 | 4.8 |  | 0.3 | 1.44
|  |  | 1 | 1.8 |  | 0.45 | 0.81
|  | total qty in sqm |  |  |  |  | 2.25 | Sqm
10.b | 5.9.6 | Columns and Pillars, Piers, Abutments, Posts and Struts.
| a | Columns
|  | DG side-GF | 1 | 1.8 |  | 4.5 | 8.1
|  | Columns-conference room -FF | 8 | 1.8 |  | 3.45 | 49.68
|  | DG side-FF | 1 | 1.8 |  | 3.45 | 6.21
|  | Total for column shuttering |  |  |  |  | 63.99 | Sqm
|  | Say |  |  |  |  | 64 | Sqm
10.c | 5.9.3 | Suspended floors, roofs, landings, Balconies and access platform
| b | Slab
|  | Roof for Dg set-GF top | 1 | 2.56 | 3.36 |  | 8.6016
|  | side | 1 | 12.08 | 0.12 |  | 1.4496
|  | top slab of Dg set room | 1 | 2.56 | 3.36 |  | 8.6016
|  |  | 1 | 12.08 | 0.12 |  | 1.4496
|  | step- top | 1 | 1.2 | 1.7 |  | 2.04
|  |  | 1 | 5.8 | 0.12 |  | 0.696
|  | Toilet & Passage | 1 | 5.55 | 3.15 |  | 17.4825
|  | Conference room | 1 | 5.55 | 10.37 |  | 57.5535
|  |  | 1 | 31.84 | 0.12 |  | 3.8208
|  | wash slab | 1 | 1.5 | 0.6 |  | 0.9
|  |  | 1 | 1.5 | 0.12 |  | 0.18
|  | Total qty in m3 |  |  |  |  | 102.7752 | Sqm
|  | Say |  |  |  |  | 103 | Sqm
10.d | 5.9.5 | Lintel,beams,plinth beams,girders,bressumers and cantilevers
| c | Lintel | 1 | 2.2 | 0.38 |  | 0.836
|  |  | 2 | 13.52 | 0.38 |  | 10.2752
|  |  | 1 | 5.55 | 0.38 |  | 2.109
|  |  | 1 | 3.15 | 0.38 |  | 1.197
|  |  | 1 | 5.55 | 0.38 |  | 2.109
|  | Roof beam |  |  |  |  | 0
| g | Roof beam | 2 | 13.52 |  | 0.93 | 25.1472 |  | 27.04
|  |  | 5 | 5.55 |  | 0.93 | 25.8075 |  | 27.75
|  | Ground floor roof beam | 1 | 3.56 |  | 0.93 | 3.3108 |  | 3.56
|  |  | 1 | 2.56 |  | 0.93 | 2.3808 |  | 2.56
|  | Total qty in sqm |  |  |  |  | 73.1725 | Sqm | 60.91
|  | Say |  |  |  |  | 74
10.e | Weather shade, Chajjas, corbels etc., including edges
| e | shade | 1 | 14.27 |  | 0.75 | 10.7025
|  |  | 1 | 5.55 |  | 0.75 | 4.1625
|  | Total qty in sqm |  |  |  |  | 14.865 | Sqm
|  | Say |  |  |  |  | 15 | Sqm
11 | 5.22.A.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending,placing in position and binding all complete above plinth level. :Thermo-Mechanically Treated bars |  |  |  |  | 24.4836
|  | total |  |  |  |  | 2203.5283 | kg
|  | Say |  |  |  |  | 2203.5283 | kg
12 | 6.4.2 | Brick work with F.P.S bricks of class designation 5.0 in superstructure above plinth level up to floor v level in all shapes an sizes in: Cement mortar 1: 6 (1 cement :6 coarse sand)
|  | Out side wall-vertical wall | 2 | 13.52 | 0.23 | 3 | 18.6576
|  | Out side wall- Horizontal wall | 3 | 5.55 | 0.23 | 3 | 11.4885
|  | inside wall | 1 | 3.15 | 0.23 | 3 | 2.1735
|  | Front extention-Vertical wall | 1 | 3.36 | 0.23 | 3 | 2.3184
|  |  | 1 | 2.56 | 0.23 | 3 | 1.7664
deduction
|  | Doors-D1 | 2 | 1.2 | 0.23 | -2.25 | -1.242
|  | columns | 10 | 0.3 | 0.6 | -3 | -5.4
|  | windows-W | 2 | 1.8 | 0.23 | -1.5 | -1.242
|  | W1 | 2 | 1.5 | 0.23 | -1.5 | -1.035
|  | Doors-D2 | 1 | 1 | 0.23 | 2.25 | 0.5175
|  | ventilater | 2 | 0.6 | 0.23 | 0.45 | 0.1242
|  | beam | 1 | 60.91 | 0.23 | -0.223 | -3.1241
|  | Lintel | 1 | 2.2 | 0.23 | -0.15 | -0.0759
|  |  | 1 | 13.52 | 0.23 | -0.15 | -0.46644
|  |  | 1 | 3.15 | 0.23 | -0.15 | -0.10867
|  |  | 1 | 5.55 | 0.23 | -0.15 | -0.19148
|  | Total qty in m3 |  |  |  |  | 24.1605 | Cum
13 | 6.13.1 | Half brick masonry with F.P.S brick of class designation 7.5 in superstructure above plinth level up to floor V level : CM 1:3 (1 cement : 3 coarse sand)
|  | toilet walls | 2 | 1.4 |  | 3 | 8.4 | sqm
|  |  | 2 | 1.72 |  | 3 | 10.32
|  | deduction |  |  |  |  | 0
|  | doors-D3 | 2 | 0.8 |  | -2.1 | -3.36
|  | Parapet | 1 | 13.52 |  | 1 | 13.52
|  |  | 1 | 5.55 |  | 1 | 5.55
|  | Net qty |  |  |  |  | 28.88 | sqm
14 | 6.15 | Extra for providing and placing in position 2 Nos. 6mm dia M.S bars at every third course of half brick masonry (with FPS brick)
|  | Say |  |  |  |  | 28.88 | sqm
15 | 13.2.1 | 15mm cement plaster on the rough side of single or half brick wall of mix : 1 : 4 (1 cement : 4 fine sand) for external walls
|  | Out side wall-vertical wall | 1 | 13.52 |  | 3.45 | 46.644
|  |  | 1 | 13.52 |  | 0.45 | 6.084
|  | Out side wall- Horizontal wall | 2 | 5.55 |  | 3.45 | 38.295
|  | Front extention-Vertical wall | 1 | 3.36 |  | 4 | 4
|  |  | 1 | 2.56 |  | 4 | 10.24
|  | deduction |  |  |  |  | 0
|  | Doors-D1 | 2 | 1.2 |  | -2.25 | -5.4
|  | columns | 10 | 0.3 |  | -3 | -9
|  | windows-W | 2 | 1.8 |  | -1.5 | -5.4
|  | W1 | 1 | 1.5 |  | -1.5 | -2.25
|  | Doors-D2 | 1 | 1 |  | -1.5 | -1.5
|  | columns | 8 | 0.3 |  | -3.45 | -8.28
|  | Total qty in m3 |  |  |  |  | 73.433 | sqm
|  | Say |  |  |  |  | 74 | sqm
16 | 13.1.1 | 12mm cement plaster on the rough side of single or half brick wall of mix : 1 : 4 (1 cement : 4 fine sand) for internal walls, column and beams etc
|  | Out side wall-vertical wall | 2 | 13.52 |  | 3 | 81.12
|  | Out side wall- Horizontal wall | 2 | 5.55 |  | 3 | 33.3
|  |  | 2 | 5.55 |  | 3 | 33.3
|  | inside wall | 2 | 3.15 |  | 3 | 18.9
|  | Front extention-Vertical wall | 2 | 3.36 |  | 4 | 26.88
|  |  | 1 | 2.56 |  | 4 | 10.24
|  | column plastering | 10 | 1.8 |  | 3 | 54
beam plastering
| g | Roof beam | 2 | 13.52 |  | 1.13 | 30.5552
|  |  | 4 | 5.55 |  | 1.13 | 25.086
|  | Ground floor roof beam | 1 | 3.56 |  | 1.13 | 4.0228
|  |  | 1 | 2.56 |  | 1.13 | 2.8928
deductions
|  | Doors-D1 | 2 | 1.2 |  | -2.25 | -5.4
|  | Doors-D2 | 1 | 1 |  | -1.5 | -1.5
|  | columns | 8 | 0.3 |  | -3.45 | -8.28
|  | Net qty |  |  |  |  | 305.1168
17 | 13.16.1 | 6 mm cement plaster of mix : 1:3 (1 cement: 3 fine sand) for ceiling plastering
|  | Roof for Dg set-GF | 1 | 2.56 | 3.36 |  | 8.6016
|  | top slab of Dg set room | 1 | 2.56 | 3.36 |  | 8.6016
|  | Conference room | 1 | 13.52 | 5.55 |  | 75.036
|  | wash slab under side | 1 | 1.5 | 0.6 |  | 0.9
|  | total qty in sqm |  |  |  |  | 93.1392
18 | 13.8 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. |  |  |  |  | 398.256
19 | 13.60.1 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade –Two or more coats on new work.-internal walls | 0 |  |  |  | 398.256
20 | 13.48.1 | Finishing walls with Acrylic Smooth exterior paint of required shade : New work (Two or more coat applied @ 1.67 ltr/10 sqmover and including priming coat of exterior primer applied @ 2.20 kg/ 10 sqm) | 0 |  |  |  | 0
21 |  | Painting Steel work with Delux Multi surface paint to give an even shade.Two or more coat applied @ 0.90 ltr/10sqm over an over an under coat of primer applied @ 0.80ltr/10aqm of approved brand or manufacture.
|  | step painting-steel work | 4 | 1.7 |  | 0.3 | 2.04
|  |  | 5 | 1.7 |  | 0.15 | 1.275
[7 empty] | 3.315 | sqm
22 | 8.2.2.2 | Providing and fixing 18mm thick gang saw cut mirror polished premoulded and prepolished) machine cut for kitchen platforms, vanity counters, window sills , facias and similar locations of required size of approved shade, colour and texture laid over 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels. Granite of any colour and shade: Area of slab over 0.50 sqm.: Lowest retail price not less than Rs. 2500.00/m2( Granite to be selected by the Engineer in charge)
|  | area of slab | 1 | 1.5 | 0.6 |  | 0.9 | sqm
23 | 9.117.1 | Providing and fixing factory made UPVC door frame made of UPVC extruded section having an overall dimensions as below ( tolerance ± 1mm ), with wall thickness 2.0mm (± 0.2mm), corners of the door frame to be joined with galvanized brackets and stainless steel screws, joints mitered and plastic welded. The hinged side vertical of the frames reinforced by galvanized M.S. tube of size 19x19 mm and 1mm (± 0.1mm) wall thickness and 3 nos. Stainless steel hinged fixed to the frame complete as per manufacturers Specification and direction of engineering -in-change : Extruded section profile size 48x40 mm
|  |  | 2 | 3.36 |  |  | 6.72
24 | 9.118.1 | Providing and fixing existing door frames: 24 mm thick factory made PVC door shutters made of styles and rails of a UPVC hollow section of size 59x24 mm and wall thickness 2 mm (± 0.2mm) with in built edging on both sides. The styles and rails mitered and joint at the corners by means of M.S. galvanized / plastic brackets of size 75x220 mm having wall thickness 1.0 mm and stainless steel screws. The styles of the shutter reinforced by inserting galvanized M.S. tube of size 20x20 mm and 1mm (± 0.1mm) wall thickness. The lock rail made up of " H" section, a UPVC hollow section of size 100x24 mm and 2mm (± 0.2mm) wall thickness, fixed to the shutters styles by means of plastic/ galvanized M.S.'U' cleats. The shutter frame filled with a UPVC multi chambered single panel of size not less than 620mm, having over all thickness of 20mm and 1mm (± 0.1mm) wall thickness. The panes filled vertically and tie bar at two places by inserting horizontally 6mm galvanized M.S. rod and fastened with nuts and washers, complete as per manufacturer's specification and direction of Engineer- in - charge. (for W,C and bath room door shutter).
|  | door shutter | 2 | 0.8 |  | 2.1 | 3.36
25 | 11.41.2 | Providing and laying polished vitrified floor tile in different sizes (thickness to be specified by the manufacturer) with Acid and / or Alkali resistant tiles with water absorptions less than 0.08% and confirming to IS:15622 of approved make in all colours and shades, laid on 20mm thick cement mortor 1:4 (1 cement:4 Coard sand) including grouting the joints with white cement and matching pigments etc. complete. (Lowest retail price not less than Rs. 880/m2) : Size of Tiles 60 x 60 cm (Tiles to be selected by the Engineer in charge)
|  | conference room | 1 | 10.14 | 5.55 |  | 56.277 | sqm
|  |  | 1 | 1.7 | 3.15 |  | 5.355 | sqm
|  |  | 1 | 2.33 | 3.13 |  | 7.2929
|  | Total qty in sqm |  |  |  |  | 68.9249 | sqm
26 | 11.39 | Providing and laying rectified Glazed Ceramic floor tiles 300x300 mm or more (thickness to be specified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make in colours White, Ivory, Grey, Fume Red Brown, laid on 20mm thick cement mortar 1:4 (1 Cement : 4 Coarse sand) including grouting the joints with white cement and matching pigments etc., complete.
|  | Toilets-Floor | 1 | 1.1 |  | 1.4 | 1.54 | sqm
|  |  | 1 | 1.1 |  | 1.4 | 1.54
|  | wash area | 1 | 2.32 |  | 1.47 | 3.4104
|  | Total qty in sqm |  |  |  |  | 6.4904 | sqm
27 | 11.4 | Providing and fixing Ist quality ceramic glazed wall tiles of size 300x450mm conforming to IS : 15622 (thickness to be specified by the manufacturer ) of approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados over 12 mm thick bed of cement Mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm including pointing in white cement mixed with pigment of matching shade complete.
|  | Toilets-wall | 4 | 1.4 |  | 2.1 | 11.76 | sqm
|  |  | 2 | 0.2 |  | 2.1 | 0.84 | sqm
|  |  | 2 | 1.1 |  | 2.1 | 4.62 | sqm
|  | wash area | 1 | 2.32 |  | 2.1 | 4.872 | sqm
|  |  | 2 | 1.47 |  | 2.1 | 3.087 | sqm
dedudtions
|  |  | 2 | 0.45 |  | -0.6 | -0.54
|  |  | 1 | 1.5 |  | -0.1 | -0.15
24.489
|  | say |  |  |  |  | 25 | sqm
28 | 12.45 | Providing and fixing false ceiling at all height including providing and fixingof frame work made of special sections, power pressed from M.S. sheetsand galvanized with zinc coating of 120 gms/sqm (both side inclusive) asper IS : 277 and consisting of angle cleats of size 25 mm wide x 1.6 mmthick with flanges of 27 mm and 37mm, at 1200 mm centre to centre, oneflange fixed to the ceiling with dash fastener 12.5 mm dia x 50mm long with6mm dia bolts, other flange of cleat fixed to the angle hangers of 25x10x0.50mm of required length with nuts & bolts of required size and other end ofangle hanger fixed with intermediate G.I. channels 45x15x0.9 mm runningat the spacing of 1200 mm centre to centre, to which the ceiling section0.5 mm thick bottom wedge of 80 mm with tapered flanges of 26 mm eachhaving lips of 10.5 mm, at 450 mm centre to centre, shall be fixed in adirection perpendicular to G.I. intermediate channel with connecting clipsmade out of 2.64 mm dia x 230 mm long G.I. wire at every junction, includingfixing perimeter channels 0.5 mm thick 27 mm high having flanges of 20 mm and 30 mm long, the perimeter of ceiling fixed to wall/partition with the help of rawl plugs at 450 mm centre, with 25mm long dry wall screws @230 mm interval, including fixing of gypsum board to ceiling section andperimeter channel with the help of dry wall screws of size 3.5 x 25 mm at230 mm c/c, including jointing and finishing to a flush finish of tapered andsquare edges of the board with recomme-nded jointing compound , jointingtapes , finishing with jointing compound in 3 layers covering upto 150 mmon both sides of joint and two coats of primer suitable for board, all as permanufacturer’s specification and also including the cost of making openingsfor light fittings, grills, diffusers, cutouts made with frame of perimeterchannels suitably fixed, all complete as per drawings, specification anddirection of the Engineer in Charge but excluding the cost of painting with
|  | conference room |  | 9.91 |  | 4.86 | 48.1626 | sqm
29 |  | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) : For fixed portion: Powder coated aluminium (minimum thickness of powder coating 50 micron)
|  | entrance door | 2 | 1.2 |  | 2.1 | 5.04
|  | door to wash area | 1 | 0.9 |  | 2.1 | 1.89
|  | windows | 2 | 1.8 |  | 1.5 | 5.4
|  | ventiletrs | 2 | 0.6 |  | 0.45 | 0.54
|  | 9kg/sqm |  |  |  |  | 12.87
|  | Say |  |  |  |  | 115.83 | kg
30 |  | For shutters of doors, windows & ventilators including providing and fixing hinges/ pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately). Powder coated aluminium (minimum thickness of powder coating 50 micron)
|  | entrance door | 2 | 1.2 |  | 2.1 | 5.04
|  | door to wash area | 1 | 0.9 |  | 2.1 | 1.89
|  | windows | 2 | 1.8 |  | 1.5 | 5.4
|  |  | 1 | 1.5 |  | 1.5 | 2.25
|  | ventiletrs | 2 | 0.6 |  | 0.45 | 0.54
|  | 5kg/sqm |  |  |  |  | 15.12
|  | Say |  |  |  |  | 75.6 | kg
31 |  | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.5 mm thickness
|  | entrance door | 2 | 1.2 |  | 2.1 | 5.04
|  | door to wash area | 1 | 0.9 |  | 2.1 | 1.89
|  | windows | 2 | 1.8 |  | 1.5 | 5.4
|  |  | 1 | 1.5 |  | 1.5 | 2.25
|  | ventiletrs | 2 | 0.6 |  | 0.45 | 0.54
|  | total qty in sqm |  |  |  |  | 15.12 | sqm
|  | Say |  |  |  |  | 15.12 | sqm
32 | 21.8 | Filling the gap in between aluminium frame & adjacent RCC/Brick/Stone work by providing weather silicon sealant over backer rod of approved quality as per architectural drawings and direction of Enginner-in-charge complete. |  |  |  | 0 | 0
| 21.8.1 | Upto 5mm depth and 5mm width | 10 |  |  |  | 10
33 | 21.18 | Providing and fixing 12 mm thick frameless toughened glass door shutter of approved brand and manufacture, including providing and fixing top & bottom pivot & spring type fixing arrangement and making necessary holes etc. for fixing required door fitings, all complete as per direction of Engineer-in-charge ( Door handle, lock and stopper etc. to be paid separately) |  | 1.2 |  | 2.25 | 2.7
34 | MR | Providing and fixing arrangement and making necessary holes etc. for fixing required door fitings, all complete as per direction of Engineer-in-charge Door handle, lock and stopper etc. |  |  |  |  | 6
35 | 9.83 | Providing and fixing aluminium die cast body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 35 kg and door width upto 700 mm) with necessary accessories and screws etc. complete. |  |  |  |  | 2
36 | 9.97 | Providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade with necessary screws etc., complete. |  |  |  | 0 | 0
| 9.97.2 | 250 x 10mm |  |  |  |  | 8
| 9.97.4 | 150 x 10mm |  |  |  |  | 8
37 | 21.13 | Providing and fixing 100mm brass locks (best make of approved quality) for aluminum doors including necessary cutting and making good etc. complete |  |  |  |  | 8
38 | 21.12.2 | Providing and fixing aluminium tubular handle bar 32 mm outer dia, 3.0 mm thick & 2100 mm long with SS screws etc .complete as per direction of Engineer-in-Charge. Powder coated minimum thickness 50 micron aluminium tubular handle bar. |  |  |  |  | 8
39 | 9.101 | Providing and fixing aluminium hanging floor door stopper ISI marked anodised (anodic coating note less than grade AC 10 as per IS : 1868) transparent or dyed to required colour and shade with necessary screws etc., complete. |  |  |  | 0 | 0
| 9.101.1 | Single rubber stopper |  |  |  |  | 3
40 | 21.4 | Providing and fixing double action hydraulic floor spring of approved brand and manufacture IS : 6315 marked, for doors including cost of cutting floors as required, embedding in floors and cover plates with brass pivot and single piect M.S. sheet outer box with side plate etc., complete as per the direction of Engineer-in-charge. |  |  |  | 0 | 0
| 21.4.2 | With brass cover plate |  |  |  |  | 1
41 | 9.149 | Providing and fixing casement handle made of zinc alloyed (white powder coated) for uPVC casement window with necessary screws etc. complete. |  |  |  |  | 4
42 | 9.68.1 | Providing and fixing oxidised M.S. casement stays (straight peg type) with necessary screws etc. Complete-300 mm weighing not less than 200 gms |  |  |  |  | 8
43 |  | Providing and fixing wash basin (counter type) with CI / MS brackets, 15mm CP brass Pillar taps, 32mm CP brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever required.: White Vitreous China Wash basin size 630 x 450mm with a single 15mm C.P brass piller tap. Make:Hindware,Cera,Jaquar etc.., (Lowest retail price of basin not less than Rs. 3000/each and Pillar tap not less than Rs. 2000/each. Materials to be selected by the Engineer in charge)
[7 empty] | 2 | Nos
44 | 17.7.1 | Providing and fixing white vitreous china Wall Mounted type water closet (European type W.C.pan) with seat and lid, 3/6 litre low level white vitrous Dual Flushing cistern and C.P flush bend with fitting and C.I brackets, 40mm flush bend, overflow arrangement with specials of standard make and mosquito proof coupling of approved municipal design complete including painting of fittings and brackets, cutting and making good the walls and floors wherever required. Make:Hindware,Cera,Jaquar etc.., WC pan with ISI marked white solid plastic seat and lid (Lowest retail price not less than 10,000/each. Materials to be selected by the Engineer in charge)
[7 empty] | 2 | nos
45 |  | Providing and fixing C.P. brass long body bib cock (Sink cock)of approved quality conforming to IS standards and weighing not less than 690 gms. 15 mm nominal bore (Lowest retail price not less than 1800/each. Materials to be selected by the Engineer in charge) |  |  |  |  | 2 | nos
46 | 17.28.1.1 | Providing and fixing PVC Waste pipe for sink or wash basin including PVC waste fittings complete.:Semi rigid pipe 32mm dia |  |  |  |  | 2 | nos
47 | 17.34.1 | Providing and fixing Toilet paper holder . Make:Hindware,Cera,Jaquar etc..,:C.P Brass |  |  |  |  | 2 | nos
48 | 18.65 | Providing and fixing SS soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements. Weighing not less than 106 gms. |  |  |  |  | 3 | nos
49 | 17.31 | Providing and fixing 600 x 450mm bevelled edge mirror of superior glass (of approved quality) complete with 6mm thick hard board ground fixed to wooden cleats with C.P. brass screws and washers complete. |  |  |  |  | 1 | nos
50 | 17.73.2 | Providing and fixing SS towel rail complete with brackets fixed to wooden cleats with CP brass screws with concealed fitting arrangement of approved quality and colour. 600mm long towel rail with total length of 645mm, width 78mm and effective height of 88mm, weighing not less than 190gms. |  |  |  |  | 3 | nos
51 | LMR | Providing & fixing of CP Health faucet. Hand operated spray unit( Instand type)).Make:Jauqar, Hindware, Parryware, crome., (Lowest retail price not less than 1200/each. Materials to be selected by the Engineer in charge) |  |  |  |  | 2
52 | LMR | Providing and fixing PVC pipes for water supply arrangements including cost pipes, fittings, solvent cement,testing of pipes, labour charges etc complete : Concealed work including cutting chases and making good the wall etc
20mm nominal outer dia .Pipes. (10kg/cm2)
32mm nominal outer dia .Pipes. (10kg/cm2)
53 |  | Providing and fixing PVC soil, waste and vent pipe to IS : 13592 of SWR quality, including all fittings, like EG : Bends, Tees, Elbows, Collars, junction, inspection doors, cowls, offsets, access pipes, jointing with rubber ring / solvent cement by application of leak proof adhesive like FRP paste including cutting holes in walls and floors and making good. Make: Supreme, Finolex, Astral
50mm dia (6kg / sq.cm)
63mm dia (6kg / sq.cm)
75mm dia (6kg / sq.cm)
110mm dia (6 kg / sq.cm)
54 | 18.77 | Cutting holes upto 15 x 15 cm in R.C.C. floors and roofs for passing drain pipe etc. and repairing the hole after insertion of drain pipe etc. with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) including finishing complete.
55 | 12.41.2 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A including jointing with seal ring conforming to IS : 5382 leaving 10 mm gap for thermal expansion.(i) Single socketed pipes. 110 mm diameter
56 |  | Providing and fixing PVC floor trap self cleansing design with or without vent arm complete including cutting and making good the walls and floors. Make:Supreme,Finolex,Prince etc..,
| MR | 110mm dia inlet 110mm dia outlet |  |  |  |  | 2
57 | M.R | Providing and fixing CP grating of 6mm thick with rim including setting in floor with white cement mortar and making good the floor (Chilli make)
|  | 125mm dia |  |  |  |  | 3 | nos
58 |  | Providing and fixing C.P. brass pillar cock (push type)approved quality conforming to IS standards and weighing not less than 690 gms.: 15 mm nominal bore for wash basins: Make:Jauqar, Hindware, Parryware, crome |  |  |  |  | 2 | nos
59 | 26.1 | Providing and supplying aluminium extruded tubular and other aluminium sections as per the architectural drawings and approved shop drawings , the aluminium quality as per grade 6063 T5 or T6 as per BS 1474,including super durable powder coating of 60-80 microns conforming to AAMA 2604 of required colour and shade as approved by the Engineer-in-Charge. ( The item includes cost of material such as cleats, sleeves, screws etc. necessary for fabrication of extruded aluminium frame work. Nothing extra shall be paid on this account).
|  | step side | 1 | 1.7 | 2 | 3.4
|  | toilet side | 1 | 2.99 | 2 | 5.98
|  | 6.5Kg/sqm |  |  |  | 9.38
|  | Total weight |  |  |  | 60.97
|  | say |  |  |  | 65 | kg
60 | 26.2 | Designing, fabricating, testing, protection, installing and fixing in positionsemi (grid) unitized system of structural glazing (with open joints) for linearas well as curvilinear portions of the building for all heights and all levels,including:a) Structural analysis & design and preparation of shop drawings for thespecified design loads conforming to IS 875 part III (the system mustpassed the proof test at 1.5 times design wind pressure without anyfailure), including functional design of the aluminum sections for fixing glazing panels of various thicknesses, aluminium cleats, sleeves and c) Providing and filling, two part pump filled, structural silicone sealant and one part weather silicone sealant compatible with the structuralsilicone sealant of required bite size in a clean and controlled factory /work shop environment , including double sided spacer tape, setting blocks and backer rod, all of approved grade, brand and manufacture,as per the approved sealant design, within and all around the perimeterd) Providing and fixing in position flashings of solid aluminium sheet mm thick and of sizes, shapes and profiles, as required as per the site conditions, to seal the gap between the building structure and all its interfaces with curtain glazing to make it watertighte) Making provision for drainage of moisture/ water that enters the curtainglazing system to make it watertight, by incorporating principles of required), making necessary holes of required sizes and of requirednumbers etc. complete. This item includes cost of all inputs of splice plates etc. gaskets, screws, toggles, nuts, bolts, clamps etc., structural and weather silicone sealants, flashings, fire stop (barrier)- cum-smoke seals, microwave cured EPDM gaskets for water tightness, pressure equalisation & drainage and protection against fire hazardincluding:b) Fabricating and supplying serrated M.S. hot dip galvanised / Aluminiumalloy of 6005 T5 brackets of required sizes, sections and profiles etc.to accommodate 3 Dimentional movement for achieving perfectverticality and fixing structural glazing system rigidly to theRCC/masonry/structural steel framework of building structure using stainless steel anchor fasteners/ bolts, nylon seperator to prevent bimetallic contacts with nuts and washers etc. of stainless steel grade 316, of the required capacity and in required numbers
|  |  | 1 | 1.7 | 2 | 3.4
|  |  | 1 | 2.99 | 2 | 5.98
[6 empty] | 9.38 | sqm
|  | Say |  |  |  | 9.38 | sqm
61 |  | Providing and fixing poly carbonate (multi wall 6mm or nearest size) sheet roofing of approved make and quality fixed with polymer coated J or L hooks, bolts and nuts of required diameter with necessary washers complete including the cost of M.S square tube 50x25mm 16 gauge fixed with MS flat 25x6mm including necessary nuts and bolts to support the roofing,painting witn two or more coatswaithsyntheticenamel paint over a priming coat of Zinchromate primer etc complete.
|  |  | 1 | 1.12 |  | 2.99 | 3.3488
|  |  | 1 | 1.12 |  | 2.56 | 2.8672
|  | total qty in sqm |  |  |  |  | 6.216 | Sqm
62 |  | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete:
|  | 3"x16' square plate,thickness-1.6mm | 4 | 1.7 |  | 0.3 | 2.04
|  |  | 5 | 1.7 |  | 0.15 | 1.275
|  | total qty in sqm |  |  |  |  | 3.315
|  | Weight -20Kg/m2 |  |  |  |  | 66.3
|  | Say |  |  |  |  | 70 | Kg
63 |  | WALL PANEL for acoustic treatment - -Supply and fixing of Keiler/equivalent make 6 mm Polyester Fiber panel, fixed on GI Channel filled with 48kg/ dencityx 50 mm thick rock wool backing with black fleece cloth of 120 GSM. | 10.07 |  | 5.55 |  | 55.8885 | Sqm
|  |  | 4.82 |  | 2.5 | 2 | 24.1
|  |  | 10.155 |  | 2.5 | 2 | 50.775
74.875
|  | deduction | 2 |  | 1.8 | -1.5 | -5.4
|  |  | 1 |  | 1.2 | -2.1 | -2.52
66.955
|  | projector | 1 |  | -1 |  | -1
|  | TV | 1 |  | -1 |  | -1
64.955

## Plumbing-3 (hidden)
HLL LIFECARE LIMITED
CONSTRUCTION OF MULTISTORIED BUILDING AT THE CAMPUS OF CHO, POOJAPPURA , THIRUVANANTHAPURAM
INTERNAL PLUMBING AND SANITATION WORKS
Sl.No. | DSR | Description | Quantity | Unit | Rate | Amount
| Code No. |  |  |  | (Rs.) | (Rs.)
1 | M.R | Providing and fixing white vitreous china Wall Mounted type water closet (European type W.C.pan) with seat and lid, 3/6 litre low level white vitrous Dual Flushing cistern and C.P flush bend with fitting and C.I brackets, 40mm flush bend, overflow arrangement with specials of standard make and mosquito proof coupling of approved municipal design complete including painting of fittings and brackets, cutting and making good the walls and floors wherever required. Make:Hindware,Cera,Jaquar etc.., WC pan with ISI marked white solid plastic seat and lid (Lowest retail price not less than 10,000/each. Materials to be selected by the Engineer in charge) | 30 | Nos. | 13797.5 | 413925 | 413925
2 | LMR | Providing and fixing wash basin ( half pedestal single unit)) with CI / MS brackets, 15mm CP brass Pillar taps, 32mm CP brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever required.: White Vitreous China Wash basin size 630 x 450mm with a single 15mm C.P brass piller tap. Make:Hindware,Cera,Jaquar etc.., (Lowest retail price of basin not less than Rs. 4500/each and Pillar tap not less than Rs. 2000/each. Materials to be selected by the Engineer in charge) | 4 | Nos. | 8475 | 33900 | 33900 | 17.7.1
3 | LMR | Providing and fixing wash basin (counter type) with CI / MS brackets, 15mm CP brass Pillar taps, 32mm CP brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever required.: White Vitreous China Wash basin size 630 x 450mm with a single 15mm C.P brass piller tap. Make:Hindware,Cera,Jaquar etc.., (Lowest retail price of basin not less than Rs. 3000/each and Pillar tap not less than Rs. 2000/each. Materials to be selected by the Engineer in charge) | 31 | Nos. | 6732.75 | 208715.25 | 208715.25 | 17.7.1
4 | 17.10.1.1 | Providing and fixing Stainless Steel A ISI 304 (18/8) kitchen sink as per IS 13983 with C.I. brackets and stainless steel plug 40 mm including painting of fittings and brackets, cutting and making good the walls wherever required : Kitchen sink with drain board :510x1040 mm bowl depth 250mm. | 1 | Nos | 6975.4 | 6975.4
5 | LMR | Providing and fixing C.P. brass bib cock of approved quality conforming to IS:8931. Make:Hindware,Cera,Jaquar etc.., 15 mm nominal bore. (Lowest retail price not less than 1200/each. Materials to be selected by the Engineer in charge) | 60 | Nos. | 1425.35 | 85521 | 85521 |  | 18.49.1
6 | LMR | Providing and fixing C.P. brass long body bib cock (Sink cock)of approved quality conforming to IS standards and weighing not less than 690 gms. 15 mm nominal bore (Lowest retail price not less than 1800/each. Materials to be selected by the Engineer in charge) | 2 | Nos. | 2128.6 | 4257.2 | 4257.2 |  | 18.51.1
7 | 18.52.1 | Providing and fixing C.P. brass stop cock (concealed) of standard design and of approved make conforming to IS:8931: 15 mm nominal bore.Make:Hindware,Cera,Jaquar etc.. | 12 | Nos. | 618.7 | 7424.4
8 | 18.53.1 | Providing and fixing C.P. brass angle valve for basin mixer and geyser points of approved quality conforming to IS:8931 a) 15 mm nominal bore: 15mm nominal bore Make:Hindware,Cera,Jaquar etc.. | 100 | Nos. | 506.7 | 50670
9 | 17.69.1 | Providing and fixing CP Waste coupling for wash basin and sink of approved quality, colour and make. Waste coupling 31mm of 79mm length and 62mm breadth, weighing not less than 45 gms. Make:Hindware,Jaquar etc.., | 2 | Nos. | 99.3 | 198.6
10 | 17.28.1.1 | Providing and fixing PVC Waste pipe for sink or wash basin including PVC waste fittings complete.:Semi rigid pipe 32mm dia | 32 | Nos | 74.9 | 2396.8
11 | 17.70.2 | Providing and fixing PTMT Bottle Trap for Wash basin and sink.Bottle trap 38mm single piece moulded with height of 270mm, effective length of tail pipe 260mm from the centre of the waste coupling 77mm breadth with 25mm minimum water seal, weighing not less than 263gms. | 32 | Nos | 440.75 | 14104
12 | 18.65 | Providing and fixing SS soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements. Weighing not less than 106 gms. | 62 | Nos. | 152.7 | 9467.4
13 | 17.34.1 | Providing and fixing Toilet paper holder . Make:Hindware,Cera,Jaquar etc..,:C.P Brass | 30 | Nos. | 339.85 | 10195.5
14 | 17.31 | Providing and fixing 600 x 450mm bevelled edge mirror of superior glass (of approved quality) complete with 6mm thick hard board ground fixed to wooden cleats with C.P. brass screws and washers complete. | 18 | Nos. | 762.55 | 13725.9
15 | 17.73.2 | Providing and fixing SS towel rail complete with brackets fixed to wooden cleats with CP brass screws with concealed fitting arrangement of approved quality and colour. 600mm long towel rail with total length of 645mm, width 78mm and effective height of 88mm, weighing not less than 190gms. | 35 | Nos. | 448.4 | 15694
16 | MR | Providing & fixing of CP Health faucet. Hand operated spray unit (instand type).Make:Hindware,Cera,Jaquar etc.., (Lowest retail price not less than 1200/each. Materials to be selected by the Engineer in charge) | 30 | Set | 1577.3 | 47319 | 47319
17 | M.R. | Providing and fixing of over head shower set with shower flange 170 mm long, including shower head and shower arm conforming to I.S Specification of approved make as per directions including all lead and lift etc., complete. (Lowest retail price not less than 1500/each. Materials to be selected by the Engineer in charge) Make:Hindware,Cera,Jaquar etc.., | 12 | Nos. | 2212.65 | 26551.8 | 26551.8
18 | LMR | Providing and fixing of CP brass 15 mm dia, 2 in 1 exposed wall mixer cum spout for wall installation with lever control and necessary CP bend for shower connection, including cutting and making good the walls complete as per sample approved by the EIC. (Lowest retail price not less than 3500/each. Materials to be selected by the Engineer in charge) | 3 | Nos. | 5017.7 | 15053.1 | 15053.1
19 | 18.7 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for Hot and Cold water supply including all CPVC plain and brass threded fittings including fixing the pipe with clamps at 1.00m spacing. This includes jointing of pipes and fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer in caharge. Make:Supreme,Finolex,Prince etc..,
Internal Work - Exposed on wall
a) | 18.7.2 | 20mm nominal outer dia.Pipes | 100 | Mtr. | 182.15 | 18215
b) | 18.7.3 | 25mm nominal outer dia.Pipes | 100 | Mtr. | 222.9 | 22290
20 | 18.8 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for Hot and Cold water supply including all CPVC plain and brass threded fittings including fixing the pipe with clamps at 1.00m spacing. This includes jointing of pipes and fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer in caharge. Make:Supreme,Finolex,Prince etc..,
Concealed work including cutting chases and making good the wall etc.
a) | 18.8.2 | 20mm nominal outer dia.Pipes | 100 | Mtr. | 281.35 | 28135
b) | 18.8.3 | 25mm nominal outer dia.Pipes | 100 | Mtr. | 336.25 | 33625
21 | LMR | Providing and fixing PVC pipes for water supply arrangements including cost pipes, fittings, solvent cement,testing of pipes, labour charges etc complete : Exposed on wall
a) | LMR | 20mm dia. PVC pipe (12kg/cm2) | 150 | Mtr. | 201.4 | 30210 | 30210
b) | LMR | 25mm dia. PVC pipe (12kg/cm2) | 300 | Mtr. | 216.5 | 64950 | 64950
c) | LMR | 32mm dia. PVC pipe (10kg/cm2) | 100 | Mtr. | 242.55 | 24255 | 24255
d) | LMR | 50mm dia. PVC pipe (8kg/cm2) | 150 | Mtr. | 334.7 | 50205 | 50205
22 | LMR | Providing and fixing PVC pipes for water supply arrangements including cost pipes, fittings, solvent cement,testing of pipes, labour charges etc complete : Concealed work including cutting chases and making good the wall etc
a) | LMR | 20mm dia. PVC pipe (12kg/cm2) | 200 | Mtr. | 191.05 | 38210 | 38210
b) | LMR | 25mm dia. PVC pipe (12kg/cm2) | 150 | Mtr. | 211.35 | 31702.5 | 31702.5
c) | LMR | 32mm dia. PVC pipe (10kf/cm2) | 50 | Mtr. | 213.4 | 10670 | 10670
23 | 18.18 | Providing and fixing Ball Valve (brass) of approved quality, High or low pressure, with plastic floats complete. Make:Lehry,Supreme,Finolex,Prince etc..,
| 18.18.2 | 20mm dia nominal bore | 40 | Nos. | 407.4 | 16296
24 | 18.17 | Providing and fixing Gun metal gate valve with C.I. wheel of approved quality (screwed end). Make: Lehry,Supreme,Finolex,Prince etc..,
a) | 18.17.1 | 25 mm dia nominal bore | 5 | Nos. | 427.8 | 2139
b) | 18.17.2 | 32 mm dia nominal bore | 5 | Nos. | 500.35 | 2501.75
c) | 18.17.4 | 50 mm nominal bore | 3 | Nos. | 749.4 | 2248.2
25 | 18.77 | Cutting holes upto 15 x 15 cm in R.C.C. floors and roofs for passing drain pipe etc. and repairing the hole after insertion of drain pipe etc. with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) including finishing complete. | 40 | each | 176.3 | 7052
26 | 12.41.2 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A including jointing with seal ring conforming to IS : 5382 leaving 10 mm gap for thermal expansion.(i) Single socketed pipes. 110 mm diameter | 160 | mtr. | 218.6 | 34976
27 | 12.42 | Providing and fixing on wall face unplasticised - PVC moulded fittings/ accessories for unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A including jointing with seal ring conforming to IS : 5382 leaving 10 mm gap for thermal expansion.
a) | 12.42.1.2 | 110 mm Coupler | 40 | each | 133.55 | 5342
b) | 12.42.3.2 | 110x110x110 mm Single tee with door | 20 | each | 305.35 | 6107
c) | 12.42.5.2 | 110 mm bend | 20 | each | 160.25 | 3205
d) | 12.42.6.2 | 110 mm Shoe | 5 | each | 290.35 | 1451.75
28 | MR | Providing and fixing to the Inlet mouth of rain water pipe S.S grating 110mm diameter and weighing not less than 440 grams. | 5 | Nos | 162.05 | 810.25 | 810.25
29 | M.R. | Providing and fixing PVC soil, waste and vent pipe to IS : 13592 of SWR quality including all fittings, like : Bends, Tees, Elbows, Collars, junction, inspection doors, cowls, offsets, access pipes, jointing with rubber ring / solvent cement by application of leak proof adhesive like FRP paste including cutting holes in walls and floors and making good. Make:Supreme,Finolex,Prince etc..,
a) | M.R. | 50mm dia (6kg / sq.cm) | 200 | Mtr. | 212.9 | 42580 | 42580
b) | M.R. | 110mm dia (4 kg / sq.cm) | 200 | Mtr. | 487.25 | 97450 | 97450
c) | MR | 160mm dia (4kg/sq.m) | 100 | Mtr. | 664.25 | 66425 | 66425
30 | MR | Providing and fixing PVC pipes for external works including all specials and fittings, solvent cementearth work excavation for trenches, refilling and after laying pipes ect complete
a) | MR | 20mm dia PVC pipes, 12kg/cm2 for water supply connection from the existing line | 150 | Mtr. | 146.8 | 22020
b) | MR | 25mm dia PVC pipes, 12kg/cm2 for water supply connection from the existing line | 150 | Mtr. | 172.65 | 25897.5
30 | M.R. | Providing and fixing PVC floor trap self cleansing design with or without vent arm complete including cutting and making good the walls and floors. Make:Supreme,Finolex,Prince etc..,
a) | MR | 110mm dia inlet 110mm dia outlet | 45 | Nos | 521.5 | 23467.5 | 23467.5
31 | M.R | Providing and fixing CP grating of 6mm thick with rim including setting in floor with white cement mortar and making good the floor (Chilli make)
a) |  | 125mm dia | 45 | Nos. | 245.1 | 11029.5 | 11029.5
32 | 19.7 | Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement : 4 coarse sand ) with R.C.C. top slab with 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand : 8 graded stone aggregate 40mm nominal size), inside plastering 12mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) finished with a floating coat of neat cement complete as per standard design :
a) | 19.7.1.1 | Inside size 90x80 cm and 45 cm deep including C.I. cover with frame (light duty) 455x610 mm internal dimensions, total weight of cover and frame to be not less than 38 kg (weight of cover 23 kg and weight of frame 15 kg) : With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 6 | Nos. | 8062.7 | 48376.2
b) | 19.7.2 | Inside size 120x90 cm and 90 cm deep including C.I. cover with frame (medium duty) 500 mm internal diameter, total weight of cover and frame to be not less than 116 kg (weight of cover 58 kg and weight of frame 58 kg) :
| 19.7.2.1 | With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 2 | Nos. | 17592 | 35184
c) | 19.7.3 | Inside size 120x90 cm and 90 cm deep including C.I. cover with frame (heavy duty) 560 mm internal diameter, total weight of cover and frame to be not less than 208 kg (weight of cover 108 kg and weight of frame 100 kg) :
| 19.7.3.1 | With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 4 | Nos. | 22155.05 | 88620.2
33 | 19.8 | Extra for depth for manholes
a) | 19.8.1.1 | Size 90x80 cm: With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 5 | m | 5481.4 | 27407
b) | 19.8.2.1 | Size 120x90 cm: with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 10 | m | 6563 | 65630
34 | 19.4 | Providing and fixing square – mouth PVC. Gully trap grade “A” complete with CI grating brick masonry chamber with water tight tight CI cover with frame of 300 x 300mm size (inside) the weight of cover to be not less than 4.50 kg and frame to be not less than 2.70 kg as per standard design
a) | 19.4.2.1 | 150 x 100mm size P type with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 6 | each | 1546.95 | 9281.7
35 | 2.1 | Excavating trenches of required width for pipes, cables, etc including excavation for sockets, and dressing of sides, ramming of bottoms, depth upto 1.5 m including getting out the excavated soil, and then returning the soil as required, in layers not exceeding 20 cm in depth, including consolidating each deposited layer by ramming, watering, etc. and disposing of surplus excavated soil as directed, within a lead of 50 m :
| 2.10.1.2 | Pipes, cables etc. exceeding 80 mm dia. but not exceeding 300 mm dia. | 150 | Rmt | 192.75 | 28912.5
36 | 19.6 | Providing and laying non-pressure NP2 class (light duty) R.C.C. pipes with collars jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 fine sand) including testing of joints etc. complete :
| 19.6.2 | 150 mm dia. R.C.C. pipe | 150 | Mtrs | 340.35 | 51052.5
37 | 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank ISI : 12701 marked with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank | 30000 | Ltrs | 6.3 | 189000
38 | 3860 | Supplying, conveying and fdixing Heavy duty CI Mh cover and frame 560 mm internal diameter, total weight of cover and frame to be not less than 208 kg (weight of cover 108 kg and weight of frame 100 kg) : | 3 | Each | 9000 | 27000
|  | TOTAL COST |  |  | Rs. | 2260023 | 1327207.1
|  | Deduct MR Items Amount |  | A | Rs. | 1327207.1
|  | Total Cost of DSR item |  | B | Rs. | 932815.9
|  | Add cost index 38% |  |  |  | 354470
|  | Total |  |  |  | 2614493
Senior Quantity Surveyor

## Gen.Abstract-1 (hidden)
HLL LIFECARE LIMITED
CONSTRUCTION OF MULTISTORIED BUILDING AT THE CAMPUS OF CHO, POOJAPPURA , THIRUVANANTHAPURAM
GENERAL ABSTRACT
Sl. No. | Description | Amount
I | Civil Works
i | Construction of building | #REF!
ii | Plumbing works | 2614493
II | Electrical works | 9692643
III | Air Conditioning | 6512355
IV | Fire protection | 5152428
V | Elevators | 5520000
VI | HT Electrification | 11000000
| Total | #REF!
| Add3% for Contingency | #REF!
| Total (A) | #REF!
| Add 5% for price escalation | #REF!
| Add3% for Structural vetting and project implementation | #REF!
| Amount for rounding | 38428
| Grand Total | #REF!
Rupees Eighteen Crores Thirty four lakhs only
Senior Quantity Surveyor

## Contents (hidden)
HLL LIFECARE LIMITED
CONSTRUCTION OF MULTISTORIED BUILDING AT THE CAMPUS OF CHO, POOJAPPURA, THIRUVANANTHAPURAM
CONTENTS
1 | Estimatge report
2 | General Abstract | 1
3 | Abstract of Estimate ( Civil) | 2 to 19
4 | Plumbing | 20 to 27
5 | Electrical Abstract | 28 to 28
6 | Electrical Estimate | 29 to 42
7 | Air Conditioning | 43 to 49
8 | Fire Protection | 50 to 62
9 | Elevators | 63 to 64
8 | Detailed Estimate (civil) | 65 to 159
9 | Drawings

## Electrical Abst-4 (hidden)
CONSTRUCTION OF INSTITUTIONAL BUILDING FOR NIIST AT THIRUVANANTHAPURAM | HLL LIFECARE LIMITED
CONSTRUCTION OF MULTISTORIED BUILDING AT THE CAMPUS OF CHO, POOJAPPURA , THIRUVANANTHAPURAM
ELECTRICAL ESTIMATE FOR PHASE I CONSTRUCTION
| SL. No | DESCRIPTION | AMOUNT IN Rs.
| A | POINT WIRING | 2757309
| B | DISTRIBUTION BOARD | 390782
| C | CABLE LAYING, TERMINATION AND CABLE TRAY | 663386
| D | EARTHING & LIGHTNING PROTECTION | 169261
|  | Total Amount in Rs (DSR Items) | 3980738
|  | Adding cost index (38%) | 1512680.44
|  | Total Amount in Rs including cost index (DSR Items) | 5493418
| E | LT CABLE | 672300
| F | LIGHT FIXTURES | 2416750
| G | TELEPHONE SYSTEM | 260250
| H | MISCELLANEOUS | 849925
|  | Total Amount in Rs (LMR Items) | 4199225
|  | Grand Total Amount in Rs (LMR + DSR) | 9692643

## Ele. Est-5. (hidden)
HLL LIFECARE LIMITED
CONSTRUCTION OF MULTISTORIED BUILDING AT THE CAMPUS OF CHO, POOJAPPURA , THIRUVANANTHAPURAM
ELECTRICAL ESTIMATE FOR PHASE I CONSTRUCTION
Item no. | Item Description | Unit | Qty | Rate in Rs | Amount in Rs
|  |  |  | (Rs.) | (Rs.)
A | POINT WIRING
1 | Wiring for light point / fan point / exhaust fan point / call bell point with 1.5 sq.mm FR PVC insulated copper conductor single core cable in surface/recessed PVC conduit with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sqmm, FR PVC insulated copper conductor single core cable etc. as required.
| Group C | Point | 510 | 727 | 370770
2 | Wiring for twin control light point with 1.5sq.mm FR PVC insulated copper conductor singlecore cable in surface/ recessed PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sqmm FR PVC insulated coppper conductor single core cable etc as required | Point | 20 | 782 | 15640
3 | Wiring for circuit/submain wiring along with earth wire with the following sizes of FR PVC insulated copper conductor, single core cable in surface/recessed PVC conduit as required.
3.1 | 2 x 1.5sq.mm + 1 x 1.5sq.mm earth wire | m | 1430 | 116 | 165880
3.2 | 2 x 2.5sq.mm + 1 x 2.5sq.mm earth wire | m | 4099.8889 | 140 | 573984
3.3 | 2 x 4sq.mm +1 x 4sq.mm earth wire | m | 1960 | 171 | 335160
3.4 | 2 x 6 sqmm + 1 x 6 sqmm earth wire | m | 200 | 216 | 43200
4 | Supplying and drawing following pair 0.5 sq mm FR PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required.
4.1 | 2 pair | m | 3360 | 17 | 57120
4.2 | 4 pair | m | 2240 | 26 | 58240
5 | Supplying and drawing co-axial TV cable RG-6 grade, 0.7 mm solid copper conductor PE insulated, shielded with fine tinned copper braid and protected with PVC sheath in the existing surface/ recessed steel/ PVC conduit as required. | m | 175 | 23 | 4025
6 | Supplying and fixing of following sizes of PVC conduit along with the accessories in surface/ recess including cutting the wall and making good the same in case of recessed conduit as required.
6.1 | 20 mm | m | 4000 | 64 | 256000
6.2 | 25 mm | m | 7225 | 72 | 520200
6.3 | 40 mm | m | 100 | 117 | 11700
6.4 | 50 mm | m | 100 | 152 | 15200
7 | Supplying and fixing of following sizes (nominal size) on surface or in recesss with suitable size of phenolic laminated sheet cover in front including painting etc as required.
7.1 | 200mm x 300 mm x 60 mm deep | Each | 5 | 275 | 1375
7.2 | 250mm x 300mm x 100 mm deep | Each | 10 | 341 | 3410
8 | Supply and fixing following modular socket on the existing modular plate & switch box including connections but excluding modular plate etc as required.
8.1 | Telephone outlet | Each | 160 | 92 | 14720
8.2 | TV antenna outlet | Each | 5 | 94 | 470
9 | Supplying and fixing stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | Each | 20 | 362 | 7240
10 | Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | Each | 110 | 23 | 2530
11 | Supply and fixing following size / module, GI / PVC box along with modular base & cover plate for modular switches in recess etc as required.
11.1 | 1 or 2 module | Each | 185 | 159 | 29415
12 | Supplying and fixing suitable size GI / PVC box with modular plate and cover in front on surface or in recess including providing and fixing 1 no. 3 pin 6 amps modular socket outlet and 6 amps modular switch, connection, painting etc. as required | Each | 250 | 320 | 80000
13 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess including providing and fixing 6 pin 16 & 6 amps modular socket outlet and 16 amps modular switch, connection etc. as required | Each | 110 | 411 | 45210
14 | Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. | Each | 55 | 42 | 2310
15 | Installation, testing and commissioning of prewired, fluorescent fittings / compact flourescent fitting / of all types, complete with all accessories and tube etc. directly on ceiling /wall, including connections with 1.5 sq.mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | Each | 165 | 82 | 13530
16 | Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable etc. as required. | Each | 20 | 87 | 1740
17 | Supplying and fixing extra down rod of 10 cm length G.I. pipe ,15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | Each | 50 | 21 | 1050
18 | Installation of exhaust fan upto 450mm dia sweep in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. | Each | 30 | 189 | 5670
19 | Supplying and drawing of UTP 4 pair CAT 6 LAN cable in the existing surface / recessed steel / PVC conduit as required. | m | 3920 | 31 | 121520
| TOTAL OF POINT WIRING |  |  |  | 2757309
B | DISTRIBUTION BOARD
20 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board / DB including drilling holes in cubicle panel, making connections, etc. as required.
20.1 | 100A 16kA TP MCCB | Each | 2 | 3032 | 6064
20.2 | 125A 16kA TP MCCB | Each | 5 | 4233 | 21165
21 | Supplying and fixing following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, with provision of 100 / 125 amps TP 16 KA MCCB as incomer, interconnection between incomer MCCB and bus bars (but without MCB's/ MCCB) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.)
21.1 | 4 way TP | Each | 2 | 5260 | 10520
21.2 | 8 way TP | Each | 5 | 6703 | 33515
22 | Supplying and fixing following way prewired SP&N MCB distribution board of steel sheet for 240 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required. (But without MCB/ RCCB/ Isolator)
22.1 | 8 way, Double door | Nos | 2 | 2844 | 5688
22.2 | 12 way, Double door | Nos | 1 | 3432 | 3432
23 | Supplying and fixing following way prewired TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required.(But without MCB/ RCCB/ Isolator)
23.1 | 4 way, Double door | Each | 4 | 6997 | 27988
23.2 | 6 way, Double door | Each | 6 | 9034 | 54204
23.3 | 8 way, Double door | Each | 4 | 9899 | 39596
24 | Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required (But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.)
24.1 | 6 way Double door | Each | 3 | 9708 | 29124
24.2 | 8 way Double door | Each | 3 | 10584 | 31752
25 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
25.1 | Single pole | Each | 200 | 146 | 29200
25.2 | Double pole | Each | 3 | 412 | 1236
25.3 | Triple pole | Each | 34 | 610 | 20740
25.4 | Triple pole and neutral | Each | 14 | 784 | 10976
26 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | Each | 150 | 6 | 900
27 | Supplying and fixing following rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
27.1 | 25 amps | Each | 2 | 1427 | 2854
27.2 | 40 amps | Each | 1 | 1510 | 1510
28 | Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
28.1 | 25 amps | Each | 4 | 1819 | 7276
28.2 | 40 amps | Each | 10 | 1845 | 18450
28.3 | 63 amps | Each | 6 | 2128 | 12768
29 | Supplying and fixing DP sheet steel enclosure on surface/ recess along with 25/32amps 240 volts "C" curve DP MCB complete with connections, testing and commissioning etc. as required. | Each | 8 | 629 | 5032
30 | Supplying and fixing FP sheet steel enclosure on surface/ recess along with 16/25/32amps 415 volts "C" curve TP MCB complete with connections, testing and commissioning etc. as required. | Each | 10 | 850 | 8500
31 | Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top along with 20 amps `C' series, SP, MCB in sheet steel enclosure on surface or in recess, with chained metal cover for the socket outlet and complete with connections testing and commissioning etc, as required. | Each | 5 | 796 | 3980
32 | Supplying and fixing 30 amps, 415volts, TPN industrial type, socket outlet, with 4 pole and earth, metal enclosed plug top along with 30amps `C' series, TPN, MCB in sheet steel enclosure on surface or in recess, with chained metal cover for the socket outlet and complete with connections testing and commissioning etc, as required. | Each | 2 | 2156 | 4312
| TOTAL OF DISTRIBUTION BOARD |  |  |  | 390782
C | CABLE LAYING, TERMINATION AND CABLE TRAY
33 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
33.1 | Upto 35 sq. mm | m | 140 | 181 | 25340
33.2 | Above 35 sq. mm and upto 95 sq. mm | m | 50 | 188 | 9400
33.3 | Above 185 sq. mm and upto 400 sq. mm | m | 150 | 215 | 32250
34 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
34.1 | Upto 35 sq. mm | m | 40 | 15 | 600
34.2 | Above 35 sq. mm and upto 95 sq. mm | m | 10 | 23 | 230
34.3 | Above 185 sq. mm and upto 400 sq. mm | m | 10 | 53 | 530
35 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
35.1 | Upto 35 sq. mm (clamped with 1mm thick saddle) | m | 80 | 22 | 1760
35.2 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | m | 40 | 67 | 2680
35.3 | Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | m | 10 | 107 | 1070
36 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
36.1 | Upto 35 sq. mm (clamped with 1mm thick saddle) | m | 1000 | 19 | 19000
36.2 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | m | 375 | 44 | 16500
36.3 | Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | m | 30 | 84 | 2520
37 | Supplying and making cable route marker with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) of size 60 cm X 60 cm at the bottom and 50 cm X 50 cm at the top with a thickness of 10cm including inscription duly engraved as required. | each | 50 | 283 | 14150
38 | Supplying and making end termination with brass compression gland and aluminium / copper lugs including gland earthing for following size of PVC insulated and PVC sheathed / XLPE aluminium / copper conductor cable of 1.1 KV grade as required.
38.1 | 3.5 C x 150 sq.mm | Each | 6 | 501 | 3006
38.2 | 3.5 C x 120 sq.mm | Each | 18 | 417 | 7506
38.3 | 3.5 C x 35 sq.mm | Each | 6 | 245 | 1470
38.4 | 3.5 C x 25 sq.mm | Each | 6 | 210 | 1260
38.5 | 4 x 16 sqmm | Each | 18 | 208 | 3744
38.6 | 4 x 10 Sq.mm | Each | 20 | 163 | 3260
38.7 | 4 x 6 sqmm | Each | 20 | 163 | 3260
38.8 | 3 C x 4 Sqmm Cu cable | Each | 8 | 125 | 1000
38.9 | 3 C x 2.5 Sqmm Cu cable | Each | 6 | 125 | 750
39 | Supplying and installing following size of perforated GI cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with GI suspenders, fixed to wall, including bolts & nuts, horizontal & vertical bends, reducers, tees, cross members & all other accessories as required.
39.1 | 300 mm width x 62.5 mm depth x 2.0 mm thickness | m | 400 | 841 | 336400
39.2 | 150 mm width x 50 mm depth x 1.6mm thickness | m | 100 | 523 | 52300
40 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc as required
40.1 | 50 mm dia | m | 100 | 388 | 38800
40.2 | 100 mm dia | m | 100 | 846 | 84600
| TOTAL FOR CABLE LAYING, TERMINATION & CABLE TRAY |  |  |  | 663386
D | EARTHING & LIGHTNING PROTECTION
41 | Earthing with GI earth pipe 4.5 m long, 40mm dia including accessories, and providing masonry enclosure with cover plate having locking arrnagement and watering pipe etc. with charcoal or coke and salt complete as required. | Set | 8 | 3753 | 30024
42 | Providing and fixing 25 mm x 5 mm GI strip on surface or in recess for earth connections etc. as required. | m | 600 | 133 | 79800
43 | Supply and providing 8 SWG dia copper wire on surface or in recess for earth connection | m | 100 | 94 | 9400
44 | Providing and fixing 8 SWG dia G.I. wire on surface or in recess for loop earthing as required. | m | 100 | 34 | 3400
45 | Providing and fixing of lightning protection finial, made of 25mm dia 300mm long, copper tube, having single prong at top, with 85mm dia 3mm thick copper base plate including holes etc complete as required. | Each | 3 | 741 | 2223
46 | Providing and fixing GI tape 20 mm x 3 mm thick on parapet or surface of wall for lightning conductor complete as required (horizontal run) | m | 150 | 64 | 9600
47 | Providing and fixing GI tape 20 mm x 3 mm thick on parapet or surface of wall for lightning conductor complete as required (vertical run) | m | 200 | 91 | 18200
48 | Providing and fixing testing joint, made of 20 mm x 3 mm thick GI strip, 125 mm long, with 4 nos of GI bolts, nuts, chuck nuts and spring washers etc complete as required. | Each | 6 | 69 | 414
49 | Providing and laying G.I. tape 32 mm X 6 mm from earth electrode directly in ground as required. | m | 120 | 135 | 16200
| TOTAL FOR EARTHING & LTG. PROTECTION |  |  |  | 169261
E | LT CABLE
50 | Supply of the following size 1.1kV grade XLPE insulated PVC sheathed, armoured Aluminium conductor power cable confirming to IS 7098 (part 1) ammended upto date.
50.1 | 3.5 C x 150 sq.mm | m | 80 | 1245 | 99600
50.2 | 3.5 C x 120 sq.mm | m | 250 | 1050 | 262500
50.3 | 3.5 C x 35 sq.mm | m | 100 | 390 | 39000
50.4 | 3.5 C x 25 sq.mm | m | 150 | 315 | 47250
50.5 | 4 x 16 sqmm | m | 200 | 250 | 50000
50.6 | 4 x 10 Sq.mm | m | 240 | 225 | 54000
50.7 | 4 x 6 sqmm | m | 250 | 175 | 43750
51 | Supply of the following size 1.1kV grade XLPE insulated PVC sheathed, armoured Copper conductor power cable confirming to IS 1554 ammended upto date.
51.1 | 3 C x 4 Sqmm Cu cable | m | 150 | 320 | 48000
51.2 | 3 C x 2.5 Sqmm Cu cable | m | 120 | 235 | 28200
| TOTAL OF LT CABLES |  |  |  | 672300
F | LIGHT FIXTURES
52 | Supply of surface mounted LED downlight fixture 18W, with all accessories like driver, connector etc complete. (GE GDS018.40S1 / Equi) | Nos | 20 | 7450 | 149000
53 | Supply of surface mounted LED downlight fixture 24W, with all accessories like driver, connector etc complete. (GE GDS024.40S0 / Equi) | Nos | 6 | 8575 | 51450
54 | Supply and installation of recess mounted LED downlight fixture 18W, with all accessories like driver, connector etc complete. (GE GDR018.40S1 / Crompton LCDH-20-CDL/Equi) | No | 135 | 7600 | 1026000
55 | Supply and installation of recess mounted adjustable type LED light fixture 15W, with all accessories like driver, connector, etc complete. (Philips BBS311 IxDLED -5000 WH / Equi). | No | 40 | 4500 | 180000
56 | Supply of 28 W T5 surface mounted fluorescent luminarire CRCA sheet steel box type fitting with electronic ballast (THD less than 10%) with 28W T5 lamp with all accessories complete. (Philips TMS 122M IxTL5-28W EBT / GE GET CI 1x28 C/s HF / Crompton T5JB1328EB) | No | 80 | 1100 | 88000
57 | Supply and installation of recess mounted 4x14W light fixture, complete with all accessories like electronic ballast (THD less than 10%) , 14W lamps etc complete with suitable length chain, anchor fastner, hook etc for the proper installation. (TBS 869 4xTL5-14W EBP D8 / GE SOC 414 / Crompton T5CQS11414EBB). | No | 95 | 6300 | 598500
58 | Supply of 18W surface mounted fluorescent luminarire CRCA sheet steel box type fitting with electronic ballast (THD less than 10%) with 18W lamp with all accessories complete. (Philips TMS 520/118 / GE LMS 14 DN / Crompton T5JB13114EB) | No | 65 | 550 | 35750
59 | Supply & installation of surface mounted suspended type LED downlight fixture 12W, with all accessories like driver, connector, suspension mechanism etc complete. (GE GDP012.40L1 / Equi) | Nos. | 5 | 5600 | 28000
60 | Supply and installation of Decorative Wall fan 400 mm sweep, 230V.1Ph, complete with Openable mesh Cover ,string Operated etc as required. (Crompton WM Wind Flo / Usha Helix high speed / Khaitan Merlin Hi speed) | No | 5 | 2650 | 13250
61 | Supply of ceiling fan 1200 mm sweep,230V,1Ph, complete with double ball bearing, motor blades, down rods, canopy, capacitor etc complete as required. (Crompton Riviera / Usha Maxx Air / Khaitan Newtec) | No | 20 | 2000 | 40000
62 | Supply of 300 mm dia medium duty Industrial type exhaust fan complete with louvers and cable from ceiling rose / connector to fan. (Usha Turbo Hi speed / Crompton Driffair / Khaitan Euro Metal). | No | 3 | 1600 | 4800
63 | Supply of 250mm sweep, 1250 rpm, louvered ventilating fan suitable for single phase 230 volt, 50Hz AC supply complete with motor, capacitor, louvers/shutters and all accessories as required complete. (Make : Usha Crisp Air / Crompton Crossair / Khaitan Vento) | Nos | 30 | 1400 | 42000
64 | Supply and installation of IP 65, outdoor LED street light with high pressure die cast aluminium housing, polycarbonate cover, electronic driver etc as required. The light fitting shall be mounted on suitable height pole (max 3mtr height), with suitable arm bracket, pole base, PVC / poly carbonate loop in loop out box, with all necessary accessories as required. The cost of the civil foundation shall be measured along with civil items The light fitting shall be suitabily installed with all required accessories to poles. The item shall include 3C x 1.5 sqmm PVC insulated copper unarmoured cable for connecting between the luminiare and the loop in loop out box. (Similar to Philips BRP020 1x10 LED). | Nos | 20 | 8000 | 160000
| TOTAL OF LIGHT FITTINGS |  |  |  | 2416750
G | TELEPHONE SYSTEM
65 | Supplying and fixing Network modular type socket outlet (RJ-45) in 1/2 module GI modular box with modular plate including connections etc. as required. | No | 145 | 450 | 65250
66 | Supply,laying & termination of telephone wires / cables as per DOT specification, with solid annealed Cu conductor of 0.5mm thick, High Density Polyethylene insulated, twisted pair, unarmoured, with outer sheath of low density polyetylene.
66.1 | 10 pair | m | 200 | 48 | 9600
66.2 | 40 pair | m | 50 | 86 | 4300
66.3 | 50 pair | m | 120 | 155 | 18600
66.4 | 200 pair | m | 200 | 650 | 130000
67 | Supply and Installation of following pair MDF box, back mount frame and original krone connectors with all accessories.
67.1 | 10 pair | Each | 4 | 1250 | 5000
67.2 | 40 pair | Each | 3 | 3500 | 10500
67.3 | 50 pair | Each | 1 | 5000 | 5000
67.4 | 200 pair | Each | 1 | 12000 | 12000
| TOTAL OF TELEPHONE SYSTEM |  |  |  | 260250
H | MISCELLANEOUS
68 | Dismantling and re-installation in new location, the existing 200kVA DG set including its canopy and all accessories like control panel, exhaust pipe, fuel tank and its piping, AMF panel, power and control cables including termination, earth strip, earth pit etc. The testing and commissioing of the DG set has to be done and made operational to the existing system complete as required. | Set | 1 | 150000 | 150000
69 | Dismantling and re-installation in new location, the existing 125kVA DG set including its canopy and all accessories like control panel, exhaust pipe, fuel tank and its piping, power and control cables including termination, earth strip, earth pit etc. The testing and commissioing of the DG set has to be done and made operational to the existing system complete as required. | Set | 1 | 125000 | 125000
70 | Supply & installation of exhaust gas piping of suitable diameter as per manufactures standard welded black MS, B class pipe confirming to IS:3589 cut to required lengths and installed with necessary bends, supports and clamps, anti- vibration mountings, insulation of exhaust system with mineral wool / Rockwool, 50mm thick wire mesh & aluminum cladding etc. | m | 50 | 3500 | 175000
71 | Cladding of existing exhaust pipe with mineral wool / Rockwool, 50mm thick wire mesh & aluminum cladding etc. | m | 40 | 1500 | 60000
72 | Dismantling the existing underground / surface mounted cables of following sizes and storing in the place as per the direction of Engineer-in-charge. The cables has to be dismantled without any damage complete as required.
72.1 | Upto 35sqmm | m | 200 | 250 | 50000
72.2 | Above 35sqmm to 95sqmm | m | 60 | 260 | 15600
72.3 | Above 95sqmm to 185sqmm | m | 250 | 270 | 67500
73 | Supplying and fixing suitable size modular plate and cover in front on surface or in recess including providing and fixing 3 nos 3 pin 6 amps modular socket outlet and one no. 6 amps modular switch, connection etc. as required | Point | 145 | 745 | 108025
74 | Supplying and fixing of following rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
74.1 | 40A TPN C curve MCB | Each | 8 | 2000 | 16000
74.2 | 63A TPN C curve MCB | Each | 16 | 2100 | 33600
74.3 | 63A DP C curve MCB | Each | 2 | 1000 | 2000
74.4 | 40A DP C curve MCB | Each | 2 | 1100 | 2200
75 | Supplying and fixing TP sheet steel enclosure on surface/ recess along with 63 amps 415 volts "C" curve FP MCB complete with connections, testing and commissioning etc. as required. | Each | 10 | 3000 | 30000
76 | Preparation of drawings and documents for submissioin to Electrical Inspectorate duly sealed and signed for the total scope of work done. The drawings and documents shall be submitted to client / contractor who is liasoning with statutory bodies for power connection. . | Job | 1 | 15000 | 15000
| TOTAL COST OF MISCELLANEOUS |  |  |  | 849925

## AC-6 (hidden)
HLL LIFECARE LIMITED
CONSTRUCTION OF MULTISTORIED BUILDING AT THE CAMPUS OF CHO, POOJAPPURA , THIRUVANANTHAPURAM
Airconditioning Works - Bill of Quantities
Item |  |  | Unit | Qty | Rate | Amount
No. |  | Description of items |  |  | (Rs.) | (Rs.)
PART A |  | MACHINERY
1 |  | Supply, installation, testing and commissioning (SITC) of 17 TR capacity aircooled Ductable split air conditioner with multiple hermetically sealed scroll compressor, Ceiling Suspended Indoor Units (IDU) and all standard fittings, IDU SS drain pan, as per specifications complete with suitable capacity drive motor, air cooled condenser with all accessories, electronic microprocessor pendant controller with digital display, first charge R 22 refrigerant gas, vibration isolator pads ODU MS stand and saftey devices like thermal protector, pressure relief valve, over load relays single phase preventor, power cabling between units and from nearest isolator, high-low pressure cut out, suitable for three phase 440V supply. | No | 4 | 367080 | 1468320 | 68
2 |  | Supply, installation, testing and commissioning of suitable hard drawn copper refrigerant piping for 17TR machine with 13 mm nitrile rubber insulation interconnecting the condensing unit to evaporating unit for packaged units as per site condition. (Multi compressor units piping will be measured unit meter as 1m of multiple pipes between units as required | RM | 60 | 2070 | 124200
3 |  | Supply, installation, testing and commissioning Ceiling Suspended Cassette type room Air-conditioner 3 TR capacity unit three phase 415V, compact cooling coil, electronic expansion valve, suction air grill, in built drain pump coated with silver ions to prevent slime, mould and bacterial growth, air filter with anti-mould and anti bacterial treatment & decorative panel. Out door unit with highly energy efficient Compressor with copper coils, first charge refrigarant gas and with MS stand. Unit to be capable of maintaining 22±1° C indoor condition with cordless remote with various features like 3 speed, auto manual selection etc also. Unit capable of 30 meter maximum interunit piping length and 15 maximum installation level difference. Decorative panel to be part of supply of units. | No | 7 | 109250 | 764750 | 18
4 |  | Supply, installation, testing and commissioning of High Wall mounted Split Air Conditioner of following capacity consisting of high wall mounted type room unit (fan coil) with cordless remote control and one number outdoor condensing unit comprising of enegy efficient suitable rotary compressor for operation on single phase, 230 V, 50Hz supply, with 5 years warrenty with copper coils, fixing the outdoor unit on a raised platform as per manufacturers recommendation and fixing of room (fan coil) unit on wall, incl 5m distance refrigerant copper piping with 13mm nitrile rubber insulation, providing and making interconnection between room & condenser as per site conditions, comprising of 1" dia drain PVC pipe with insulation 2m, canvas connections, full electrical & control cabling from power plug near indoor unit and to outdoor unit, first charge refrigarant gas, suitable stabilizer etc ODU MS Stand complete as required.
4.1 |  | 2 TR 4 star rated as per BEE | No | 6 | 79235 | 475410 | 12 | 12
4.2 |  | 1.5 TR 5 star rated as per BEE | No | 15 | 55775 | 836625 | 22.5 | 31.5
4.3 |  | 1 TR 5 star rated as per BEE | No | 4 | 44850 | 179400 | 4
5 |  | Supply & installation Copper Refrigerant piping suitable for Split & Cassette units, duly insulated with closed cell elastomeric nitrile rubber insulation, class-o, covered with two layers of shield coating, complete with elbows, T joints, sleeves etc., with GSS slotted rail supporting arrangement and GI clamp for individual pipes. | RM | 290.4 | 1150 | 333960
6 |  | Supply, Laying and Fixing of suitable rated grade PVC sheathed, armoured Aluminium conductor cable conforming to IS 7098 (Part 1) amended upto date with brass compression glands on surface/ cable tray/ wall etc as required from the Indoor to outdoor units of all ductable units for control wiring. | RM | 53 | 260 | 13780
7 |  | Supply, Laying and Fixing of suitable rated grade XLPE insulated, PVC sheathed, armoured Aluminium conductor cable conforming to IS 7098 (Part 1) amended upto date with brass compression glands on surface/ cable tray/ wall etc as required from the Indoor to outdoor units of all Cassette units for control wiring. | RM | 132 | 220 | 29040
8 |  | Supply, installation, testing and commissioning PVC drain pipe of 25mm dia ISI marked, connecting the drain lines from the indoor units to floor sump, with 9mm nitrile rubber insulation as per specification | RM | 120 | 230 | 27600
|  | TOTAL FOR PART A |  |  |  | 4253085
PART B |  | AIR DISTRIBUTION
9 |  | Supply, installation, balancing and commissioning of factory fabricated GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
9.1 | DSR 2013 | 20 G | SQM | 48.4 | 1287.54 | 62316.936 | DSR 2013
9.2 | DSR 2013 | 22 G | SQM | 106 | 913.56 | 96837.36 | DSR 2013
9.3 | DSR 2013 | 24 G | SQM | 608 | 805.92 | 489999.36 | DSR 2013
10 |  | SITC of External thermal insulation on supply air ducts using min 12mm thick nitrile rubber class "O" closed cell type with antimicrobial protection as per specifications. | SQM | 713 | 1014 | 722982
11 |  | Supply, installation, testing and commissioning of Acoustic duct lining using 10mm nitrile rubber insulation open cell type inside the ducts, with necessary adhesive, fixtures at the outlets of all indoor units upto 4m distance from fan outlet as per spec provided. | SQM | 54 | 1475 | 79650
12 |  | Supply, installation and comissioning of underdeck insulation with 20 mm thick closed cell elastomeric Nitrile Rubber density of 40kg/m3 on ceiling with necessary adhesive, fixtures 600x600mm GI wire netting, supports etc. | SQM | 198 | 1191 | 235818
13 |  | Supply, fabrication, installation, testing of flexible connections made out of fire resistant flexible double canvas sleeve. | Set | 4 | 1655 | 6620
14 | DSR 2013 | Supplying & fixing of powder coated extruded aluminium Continuos Grills with louvers but without volume control dampers complete as required. | SQM | 12 | 5163.96 | 61967.52 | DSR 2013
15 | DSR 2013 | Supplying, fixing testing commissioning of supply air diffusers of powder coated aluminium with aluminium volume control dampers with anti smudge ring & removable core. | SQM | 16 | 11647.2 | 186355.2 | DSR 2013
16 | DSR 2013 | Supplying, fixing testing commissioning of Return air diffusers of powder coated aluminium without volume control dampers with anti smudge ring & removable core | SQM | 16 | 7756.98 | 124111.68 | DSR 2013
17 |  | Supplying, Fixing,testing and commissioning of fire dampers in supply air duct/main branch and return air path as and where required of required sizes i/c control wiring,the damper shall be motorized and spring return so as to close the damper in the event of power failure automatically and open the same in case of power being restored. The spring return action shall be inbuilt mechanism and not externally mounted. The damper shall also be closed in the event of fire signal complete as required and as per specifications.
17.1 | DSR 2013 | Fire damper | SQM | 5.2125 | 9472.32 | 49374.468 | DSR 2013
17.2 | DSR 2013 | Actuator | No | 4 | 8993.46 | 35973.84 | DSR 2013
18 | DSR 2013 | Supply, installation, testing and commissioning of GI volume control duct damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc, as per specifications. | SQM | 4 | 6448.74 | 25794.96 | DSR 2013
19 |  | SITC of Fresh air GI louvers of size 300x300 mm with wire mesh and birds screen for IDUs/AHUs and with damper as per specifications. | SQM | 4 | 3285 | 13140
20 |  | Supply, installation, testing and comissioning of Inline Centrifugal duct fan with dynamically balanced impeller of 500cfm capacity, min 10 mm static , complete with GI box, with single phase direct driven motor with class B, IP44 protection with an internal automatic safety thermal overload protection, dynamically balanced impeller of following capacity, with an operating sound level of less than 55dB at 3 m distance. | No | 4 | 17082 | 68328
|  | TOTAL FOR PART B |  |  |  | 2259270
|  | GRAND TOTAL |  |  |  | 6512355
Rupees Sixty Five Lakhs Tweleve Thousand Three Hundred and Fifty Five Only

## Fire-7 (hidden)
HLL LIFECARE LIMITED
CONSTRUCTION OF MULTISTORIED BUILDING AT THE CAMPUS OF CHO, POOJAPPURA , THIRUVANANTHAPURAM
FIRE PROTECTION SYSTEM
Sl. No. | Description of item | Unit | Qty | Rate | Amount
1 | HYDRANT/SPRINKLER SYSTEM
1.1 | Supply, installation, testing and commissioning of Diesel Engine driven main fire pump suitable for automatic operation and consisting of following: complete in all respect as required. (a) End suction, top discharge, back pull out centrifugal pump of cast iron body and bronze impeller with stainless steel shaft, mechanical seal to ensure a minimum pressure of 3.5 kg/sq.cm.at highest and farthest outlet at specified flow of 2850 lpm at 80 m. head conforming to IS 1520 | [5 empty] | 13680
| (b) Suitable HP, 1500 RPM water cooled with radiator, diesel engine conforming to relevant BS & IS standard complete with auto starting mechanism, 12 volts/24 Volts electric starting equipment, Diesel Tank , exhaust pipe extended up to 1 m. outside pump house duly insulated with 50 mm. thick glass wool with 1.0 mm. thick aluminium sheet cladding, residential silencer, instruments and protection as per specification, stop solenoid for auto stop in the event of fault with audio indications, painted with posts office red colour etc. as required. (c) M.s.fabricated common base plate coupling, coupling guard, (d) Suitable cement concrete foundation duly plastered with anti vibration pads and foundation bolts etc. as required. | set | 1 | 816142 | 816142 |  | 37.2752
`
1.2 | Supply, installation, testing and commissioning of Electric driven main fire pump suitable for automatic operation and consisting of following: complete in all respect as require. (a) Centrifugal, end suction pump top discharge back pull out made of cast iron body & bronze impeller with stainless steel shaft, mechanical seal to ensure a minimum pressure of 3.5 kg/sq.cm. at highest and farthest outlet at specified flow of 2850 lpm at 80m,. head conforming to IS 1520.
| (b) Suitable HP SO cage induction motor, TEFC, synchronous speed 2900 RPM, suitable for operation on 415 volts, 3 phase 50 Hz. AC with IP 55 protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS- 325. (c) M.S. fabricated Common base plate, coupling, coupling guard, vibration eliminator, suitable rcc foundation and foundation bolts etc. as required. | set | 2 | 332074 | 664148
1.3 | Supply, Installation, testing and commissioning of electric driven pressurisation(Jockey) pump suitable for automatic operation and consisting of following: complete in all respect as required. (a) End suction, top discharge, back pull out centrifugal pump of cast iron body and bronze impeller with stainless steel shaft, mechanical seal and flow of 180 lpm at 80 m. head conforming to IS : 1520.
| (b) Suitable HP SQ cage induction motor TEFC type suitable for operation of 415 volts, 3 phase 50 Hz. AC with IP 55 class of protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS : 325, and also with a delay timer of max 30 sec to avoid frequent starts. © M.S. fabricated Common base plate, coupling, coupling guard, vibration eliminator, foundation bolts etc. as required. (d) Suitable cement concrete foundation duly plastered with anti vibration pads etc. as required. | set | 1 | 125858 | 125858
1.4 | Main Fire Pump Panel
Supply, Installation, Testing & Commissioning of Fire Pump Panel, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP42, free standing, floor mounting, dust and vermin proof, powder coated, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system, including internal wiring with suitable size wires, rotary handle, spreader etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification.
INCOMER
| 1 No. 250A, FP, SDFU with suitable rating HRC fuse / Copper link for capacity of 250A. |  |  |  |  | 9715
BUSBARS
1 Set of 300 Amp TPN busbars of high conductivity electrolytic quality Aluminium alloy.
INSTRUMENTS
| 1 No Three phase Digital voltmeter, Acc. Class 1 |  |  |  |  | 2000
| 1 No Three phase Digital ammeter, Acc. Class 1 |  |  |  |  | 2000
| 1 Set of phase indicating lamps, LED type, RYB. |  |  |  |  | 300
| 1 Set of ON, OFF indicating lamps, LED type. |  |  |  |  | 200
| 1 Set of 2A 10kA C curve SP control MCB. |  |  |  |  | 600
| 1 Set of 250/5A, Class 1.0, 10VA, Cast Resin CT for metering. |  |  |  |  | 2000
OUTGOING
Main Electrical Fire Pump
| 2 Nos. 125A, FP, SDFU with suitable rating HRC fuse / Copper link for capacity of 125A. |  |  |  |  | 19430
| 2 Nos Fully automatic Star/Delta starter of suitable rating for 415V, 50Hz, 3 phase main electrical fire pump (approx. one pump 75HP). The starter shall have ON, OFF push button, ON, OFF indication lamp, complete with all accessories and internal wiring required for automatic and manual operation. |  |  |  |  | 88780
Jockey & Terrace Pump
| 2 Nos. 32A, FP, SDFU with suitable rating HRC fuse / Copper link for capacity of 32A. . |  |  |  |  | 3060
| 1 No Fully automatic DOL starter of suitable rating for 415V, 50Hz, 3 phase Jockey pump (approx. 7.5HP). The starter shall have ON, OFF push button, ON, OFF, Trip LED indication lamp, thermal over load relay, single phase preventor, complete with all accessories and internal wiring required for automatic and manual operation. |  |  |  |  | 9275
Spare
| 2 Nos. 32A, FP, SDFU with suitable rating HRC fuse / Copper link for capacity of 63A. . |  |  |  |  | 3060
| Necessary control cabling between the feeders of Fire pump, jockey pump, sprinkler pump, booster pump shall be done and all required accessories shall be provided for the automatic operation of the Fire pump as per statutory requirement.. |  |  |  |  | 50000
| Diesel Engine Control |  |  |  |  | 254348.7545
Diesel engine control consisting of:
1 No. 16A DP C curve control MCB, 16A On/off control switch.
Auto / manual selector switch, 3 attempt starting device, push button etc.
All required timers, relays, fuses and accessories for automatic operation of diesel engine.
Indication lamp for high water temperature, engine fail to start, engine On indication, high/low lube oil pressure.
Necessary control wiring for start / stop solinoid, line / oil pressure switch, temperature switch etc.
Battery Charger suitable for 12 V / 24 V DC with boost and trickle selector switch, 0 -15 V / 0 - 30 V DC volt meter, 0 - 20 A DC Ammeter.
6 panel annunciation window for fault indication with hooter, accept & reset push button.
| The system shall include all accessories to control the operation of sprinkler pump, main electric pump, diesel pump, jockey pump, booster pump in auto sequence as per the specification. | Set | 1 | 255000 | 255000
1.5 | a) Supplying, Installation, testing and commissioning of electric driven pump (terrace pump) sets suitable for automatic operation and consisting electrical control panel with DOL Starter and accessories of the following complete in all respect as required
Pump rated for 900lpm, 35m head Monobloc type, C.I body volute type coupled with suitable HP SQ cage induction motor,sychoronous speed 2900rpm, suitable for operation on 415V, 3phase 50Hz, AC with IP 55 class of protection for enclosure, horizontal foot mounted type with class F insulation,
M.S. fabricated common base plate, coupling, coupling guard, foundation bolts etc. as required.
| Suitable cement concrete foundation duly plastered with anti vibration pads. | set | 1 | 48623 | 48623
1.6 | Supply, installation, testing and commissioning of pressure gauge 0-200 PSI ( 0 - 14 Kg ) range, 3/8" BSP bottom entry, 4" dial weather proof with stainless steel internals, siphon tube amd ball valve including fittings, etc. complete as required | no | 5 | 1921 | 9605
1.7 | Supply, installation, testing and commissioning of industrial type pressure switch having 1/4" BSP(F) connection IP:32 enclosure protection, phosphor bronze bellows as sensing element, SDPT contact system, switch rating 6A Inductive/lOA resistive 380 V AC, 0.2A Inductive/10A resistive 250V DC suit with ball valve etc. complete as required. | no | 4 | 2195 | 8780
1.8 | Supplying and fixing air vessel ade of 250 mm dia 8 mm thick MS sheet, 1200 mm. In height with air release valve on top and flanged connection to riser, drain arrangement with 25 mm dia Gun metal wheel valve, with required accessories, pressure gauge and painting with synthetic enamel paint of approved shade as required. | set | 1 | 20581 | 20581
1.9 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589 and 1239 including drop forged fittings like elbows, tees flanges, tapers, nuts bolts, gaskets etc.., fixing the pipe on the wall/ceiling with suitable clamps and painting with primer and two or more coats of synthetic enamel paint of required shade complete as required.
1.9.1 | 150 mm dia | m | 74.8 | 1827 | 136659.6
1.9.2 | 100 mm dia | m | 34 | 1218 | 41412
1.9.3 | 80 mm dia | m | 16.8 | 862 | 14481.6
1.9.4 | 65 mm dia | m | 57 | 719 | 40983
1.9.5 | 40 mm dia | m | 239.4 | 395 | 94563
1.9.6 | 25 mm dia | m | 321.3 | 271 | 87072.3
1.1 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589 / 1239 including drop forged fittings like elbows, tees flanges, tapers, nuts bolts, gaskets etc. in ground including excavation & providing cement concrete blocks as supports, anticorrosive wrapping coating min 2mm thick as per IS10221, refilling the trench with compaction etc. of following sizes complete as required.
1.10.1 | 150 mm dia | m | 220 | 2030 | 446600
1.10.2 | 80 mm dia | m | 9 | 1039 | 9351
1.11 | Supplying, fixing, testing & commissioning of dual plate non-return valve of following sizes confirming to IS : 5312 complete with rubber gasket, GI bolts, nuts, washers etc. as required.
1.11.1 | 150 mm dia | no | 4 | 7195 | 28780
1.11.2 | 65 mm dia | no | 1 | 2151 | 2151
1.12 | Supplying, fixing, testing & commissioning of foot valve complete with bolts, nuts, washers and rubber gaskets etc. conforming to IS:4038 (ISI marked) of sizes:
1.12.1 | 150 mm dia | no | 3 | 8578 | 25734
1.12.2 | 65 mm dia | no | 1 | 3569 | 3569
1.13 | Supplying and fixing, testing & commissioning of double flanged sluice valve of rating PN 1.6 with non rising spindle, with hand wheel for AG applications, CI body complete with nuts, bolts, washers, gaskets, conforming to IS 14846 of following sizes as required.
1.13.1 | 150 mm dia | no | 8 | 30992 | 247936
1.13.2 | 100 mm dia | no | 1 | 18808 | 18808
1.13.3 | 65 mm dia | no | 2 | 11850 | 23700
1.14 | Supplying and fixing, testing & commissioning of double flanged butterfly valve of rating PN 1.6, Wafer Design Butterfly Valves confirm as per IS 13095. MoC Body Cast Iron, disc ductile Iron to IS 1865 & nylon coated, EPDM seal & O ring, Stem Material: SS-410 Hand Lever upto 150mm, flange connection following sizes as required
1.14.1 | 150 mm dia | no | 2 | 7806 | 15612
1.14.2 | 100 mm dia | no | 1 | 4438 | 4438
1.14.3 | 80 mm dia | no | 3 | 2754 | 8262
1.14.4 | 65 mm dia | no | 8 | 2333 | 18664
1.15 | Supplying, fixing, testing & commissioning Ball Valve Regular bore type with Nickel plated Brass body with female thread IS:9890 / EN ISO 17292 / (BS 5351), hand lever operated
1.15.1 | 25 mm dia | no | 4 | 2033 | 8132
1.16 | Supply, installation, testing and commissioning of gun metal fire hydrant valve, single headed oblique type 63 mm instantaneous outlets with female socket for hose connection and inlet side with flange suitable for 100 mm pipe flange, valve conforming to 1S:5290 complete with blank cap chain, etc | no | 14 | 6759 | 94626
1.17 | Supplying and fixing First-aid Hose Reel with MS construction spray painted in Post office Red, conforming to IS 884 with up to date amendments, complete with the following as required. (a) 30 m. long 20 mm (nominal internal dia water hose Thermoplastic (Textile reinforced) Type-2 as per IS: 12585 (b) 20 mm (nominal internal ) dia gun metal globe valve & nozzle. (c) Drum and brackets for fixing the equipments on wall. (d) Connections from riser with 40 mm dia stop valve (gun metal) & M.S. Pipe | set | 9 | 7844 | 70596
1.18 | Supplying and fixing 63 mm dia, 15 mtr. Long RRL hose pipe with 63 mm dia Male and Female Gun metal couplings duly binded with GI wire, rivets etc. conforming to IS 636 (type-A) as required. | no | 26 | 4942 | 128492
1.19 | Supplying & fixing 63 mm dia Gun metal branch pipe with 20 mm (nominal internal diameter) size Gun Metal nozzle conforming to IS 903, suitable for instantaneous connection to inter-connect hose pipe coupling as required. | no | 13 | 2337 | 30381
1.2 | Supply, installation, testing and commissioning of hose boxes wall/pedestal type of size 750 x 250 x 600 mm made out of 16 SWG MS sheet steel with front side glass, locking arrangement and painted with approved colour completed as required and as per specifications. | no | 13 | 6583 | 85579
1.21 | Supply, installation, testing and commissioning of Fire brigade collective breaching with 4 nos. of (twin Siamese) 150 mm flanged out let connection and built in check valves complete as required. | set | 1 | 9128 | 9128
1.22 | Supply, and fixing of Air release valve all riser pipes as per specification | set | 2 | 1372 | 2744
1.23 | Supply, and fixing of priming tank 500liters made of suitable thick MS painted and with all connections and valves as per specification | set | 1 | 12000 | 12000
1.24 | SITC of Sprinkler Alarm Valve with water motor gong, test valves, drain valves complete with all accessories, set of pressure gauges, supports, etc of following sizes.
1.24.1 | 100 mm | no | 1 | 44591 | 44591
1.25 | Supplying and fixing Orifice Plate made of 6 mm thick, stainless steel with orifice of required size in between flange & landing valve of external and internal hydrant to reduce pressure to working pressure of 3.5 Kg / cm2 complete as per specifications as required. | no | 8 | 676 | 5408
1.26 | Supply, installation, testing, and commissioning of sprinkler bulbs pendeant type having a temperature rating of 68 degree centigrade | no | 258 | 398 | 102684
1.27 | Supplying, fixing, testing & commissioning of Sprinkler Flexible Hose 1000 mm in length, Unbraided, UL Listed along with all necessary accessories like Nipple threaded , Reducing Nipple threaded, Large Bracket with Bolt, Small Bracket with Bolt, Meter Square Bar etc complete as per spec. | no | 192 | 1380 | 264960
| TOTAL FIRE HYDRANT/SPRINKLER SYSTEM |  |  |  | 4076835
2 | PORTABLE FIRE EXTINGUISHERS
2.1 | Supply and fixing of Stored Pressure Water CO2 type Fire Extinguisher, 9Liters capacity Fire Extinguishers pressurised by Nitrogen Gas fitted with brass valve, plastic syphon tube and discharge hose with Nozzle and Pressure Gauge to indicate pressure inside. Extinguisher is Phosphated and Epoxy powder coated internally and externally as per IS: 5 Shade No. 538 complete with wall brackets. The Extinguisher is manufactured as per IS 15683 -2006 bearing ISI Mark | no | 18 | 1962.1219 | 35318.1951
2.2 | Supply & fixing of of CO2 type Fire Extinguisher made from brand new seamless steel cylinder, as per IS: 7285 and CCE approval, fitted with Discharge hose and horn and Wheel type valve with initial Charge as per IS: 15683-2006 specification, bearing ISI Mark | no | 10 | 6802.0228 | 68020.2276
| TOTAL FOR FIRE EXTINGUISHERS |  |  |  | 103339
3 | FIRE ALARM SYSTEM (ADDRESSABLE)
3.1 | Supply, installation, testing and commissioning of Addressable type Manual Call Point (push to call type) complete with push button, enclosed in box with provision for cable or conduit coupling. The unit to be painted fire red outside, white inside and written 'In case of fire press to call'. | no | 17 | 3151 | 53567
3.2 | Supply, installation, testing and commissioning of Hooter cum Speaker at different locations complete with all fixing accessories, 120dB etc. under false ceiling, roof, wall, etc, with a time delay of max 30sec, interconnecting lo loop cable complete as required. | no | 17 | 4064 | 69088
3.3 | Supply, Installation, Testing & Commissioning of 16 bit intelligent Addressable Fire Alarm Panel with 3 loops ( each loop accessing at least 120 detectors ) including battery backup. The panel shall be microprocessor based with its own micro controller, memory, communication module and fire device loop
interface cards for intelligent initiating and indicating devices and should also be networkable in peer-to-peer basis with other Addressable Fire Alarm Panels. The Panel shall be able to give pin point location of all Fire/Fault conditions of addressable units via the address codes for each unit. The Panel shall also be able to automatically switch off all Control Switches when ever any Alarm is triggered.
The panel shall have 54 Ah SMF Battery, Keypad operation, L C D unit to indicate Fire / Fault Signal of individual unit, in built printer to log all incoming data etc complete in all respects. operation of speakers. Panel shall have :
The Panel shall also have Logic hardware and software built into it for initiating specific AHU tripping, time delay operation of hooter and others as follows :
(a) programming software for the system
(b) automatic system test activates
(c) detector sensitivity adjustments
(d) alarm verification
(e) Alpha/numerical display
(f) provision to connect to PCs and external printers
| (g) Support modbus and bacnet protocol. | no | 1 | 142827 | 142827
3.4 | Supply, installation, testing and commissioning of Analogue Addressable type Optical Smoke Detector (photoelectric type) complete with all accessories like base. base box, etc. to be installed under/above false ceiling, roof and concealed space, etc. interconnecting to loop cable complete as required. | no | 128 | 2206 | 282368
3.5 | Supply, installation, testing and commissioning of Analogue Addressable type Heat Detector (photoelectric type, Fixed cum-rate of rise type) with range unto 60 deg C complete with all fixing accessories like base, base box, etc. to be installed under/above false ceiling, roof and concealed space, etc. interconnecting to loop cable complete as required. | no | 48 | 2122 | 101856
3.6 | Supply, installation, testing and commissioning of addressable Loop Isolators to protect one area or a number of devices with complete set to be installed under/above false ceiling, roof, concealed space, wall, etc. interconnecting to loop cable complete as required. | no | 7 | 2442 | 17094
3.7 | Supply, installation, testing, and commissioning of Response Indicators | no | 36 | 95 | 3420
3.8 | Supply and laying of 2x 1.5sq.mm copper armoured FRLS cable ISI marked with proper clamping, supports and terminations. | m | 2127 | 142 | 302034
| TOTAL FOR FIRE DETECTION SYSTEM |  |  |  | 972254
| GRAND TOTAL FOR FIRE PROTECTION SYSTEM |  |  |  | 5152428
Rupees Fifty One Lakhs Fifty Two Thousand Four Hundred and Twenty Eight Only

## Elevator-8 (hidden)
HLL LIFECARE LIMITED
CONSTRUCTION OF MULTISTORIED BUILDING AT THE CAMPUS OF CHO, POOJAPPURA, THIRUVANANTHAPURAM
SITC OF LIFTS
| SITC OF ELEVATOR | Unit | Qty | Rate |  |  | Amount
1 | Supply, installation, testing & commissioning of electric traction type elevator of following capacity and type suitable for operation on 415 V, 3 phase, 50 Hz AC supply, having AC variable voltage and variable frequency type traction control, machine roomless type, speed of 1.00 Mtr/sec, electromagnetic brake system, simple operations, operating control panel with luminous buttons, overload warning indicator, battery operated alarm bell, LED type light fixtures and emergency light, intercom suitable for hook up to EPABX, infrared ray sensing door protection for full height, reverse phase relay on controller, fireman’s switch at ground floor, digital car positions indicator in car and at all positions indicator in car and at all floors with Up/DOWN direction, all signal fixtures in stainless steel faceplates, light fixtures, ventilation fan, etc complete with all accessories including automatic rescue device in the event of power failure etc., as required. | [6 empty] | 1500000
a) | The Elevator traction motor placed top of the hoistway, Machine Room less, and shall be of gearless type with travel height of 26.mtrs. (suitable for lift well size 2100mm (D)X 1900m(W)) complete as per technical specification, duplex full collective operation with/without attendant. Car/Hoistway Entrance protected by SS mirror finish and center opening width min 800mm x 2000mm height. Complete with channels, necessary scaffolding, electrical panel, logic control panel and shaft lighting etc required for the erection of the elevators. Capacity Minimum 680 Kgs (10 passengers Minimum) passenger elevator, 8 stops & 8 openings with min car size of 1300mm wide x1350mm deep x 2200mm height Inside dimensions and entrance at front side on all the serving floors, provided with SS etched finish panel on all three sides, SS mirror finish ceiling, door & hand rail on rear side & granite flooring complete as per specifications. | No | 2 | 2760000 | 4200000 | 4645344 | 5520000
TOTAL FOR SITC OF ELEVATOR | [6 empty] | 5520000
Rupees Fifty Five Lakhs and Twenty Thousand Only
| Gross area per floor |  | 464
| Net usable area per floor |  | 371.2
| No of landing incl GF |  | 8
Assuming population density 9.5m2 per person
| Probable population |  | 273.5158 |  |  |  | 480000
| RTT for 10P 1.5m/s |  | 150 |  |  |  | 38640
| Time |  | 75 |  |  |  | 12.4224
14.6244