## ELE ESTI
Construction of OP & IP Block at THQH Nedumgolam, Kollam District ELECTRICAL ESTIMATE
Sl. No. |  | Description of item | Unit | Qty | Rate Rs(in figures&words) | Amount in Rs
PART B - ELECTRICAL WORKS
1 | 1.1 | Wiring for light point/exhaust fan point/fan point /call bell point with 1.5 sq:mm FRLS PVC insulated copper conductor single core cable cable in surface/ recessed PVC conduit, with modular switch, modular plate, suitable size G.I. box and earthing the point with 1.5 sq:mm FRLS PVC insulated copper conductor single core cable etc as required.
a) | 1.10.3 | Group C | Point | 325
2 | 1.11 | Wiring for twin control light point with 1.5 sq:mm FRLS PVC insulated copper conductor single core cable in surface/recessed medium class PVC conduit, 2 way modular type switch, modular plate, suitable GI box and earthing the point with 1.5 sq mm. FRLS PVC insulated copper conductor single core cable etc as required. | Point | 3
3 | 1.12 | Wiring for light/ power plug with 2x4 sq.mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC coduit along with 1 No 4 sq mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | Rm | 300
4 | 1.14 | Wiring for circuit sub main wiring alongwith earthwire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed PVC conduit as required.
a) | 1.14.1 | 2x1.5 sq mm +1x1.5 sq. mm earth wire | Rm | 2500
b) | 1.14.2 | 2x2.5 sq mm +1x 2. 5 sq.mm earth wire | Rm | 800
c) | 1.14.9 | 4x6 sq mm + 2x6 sq mm earth wire. | Rm | 200
d) | 1.14.10 | 4x10 sq mm + 2x10 sq mm earth wire. | Rm | 200
5 | 1.18 | Supplying and drawing following pair, 0.5 sq mm FRLS PVC insulated copper conductor, un armoured telephone cable in the existing surface/recessed steel/ PVC conduit.
a) | 1.18.2 | 2 Pair | Rm | 400
6 | 1.19 | Supplying and drawing co - axial TV cable RG-6 grade, 0.7 mm solid copper conductor PE insulated, shielded with fine tinned copper braid and protected with PVC sheath in the existing surface/recessed steel/ PVC conduit as required. | Rm | 100
7 | 1.21 | Supplying and fixing of following sizes of medium class PVC conduit along with accessaries in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
a) | 1.21.1 | 20 mm | Rm | 800
b) | 1.21.2 | 25 mm | Rm | 50
8 | 1.22 | Supplying and fixing metal box of following sizes ( Nominal size ) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
a) | 1.22.13 | 200 mmx 300 mmx 60mm deep | Each | 5
9 | 1.24 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc as required.
a) | 1.24.6 | Telephone socket outlet | Each | 30
b) | 1.24.7 | TV antena socket outlet | Each | 2
10 | 1.25 | Supplying and fixing stepped type electronic fan regulator on the existing modular plate and switch box excluding modular plate but including connections etc as required. | Each | 75
11 | 1.26 | Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | Each | 50
12 | 1.27 | Supplying and fixing following size/ modules,GI box along with modular base, cover plate for modular switches in recess etc as required.
a) | 1.27.1 | 1 or 2 module( 75 mmx75 mm) | Each | 110
13 | 1.31 | Supplying and fixing suitable size G. I box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc as required. | Each | 140
14 | 1.32 | Supplying and fixing suitable size G. I box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 15/16& 5/6 amps modular socket outlet and 15/16 amps modular switch, connection,painting etc as required. | Each | 20
15 | 1.33 | Supplying and fixing 3 pin , 5 amps ceiling rose on the existing junction box / wooden block including connection etc as required. | Each | 80
16 | 1.38 | Supplying and fixing call bell / buzer suitable for D.C / A.C single phase, 230 volts, complete as required. | Each | 15
17 | 1.41 | Installation testing and commissioning of pre- wired, fluroscent fitting / compact fluroscent fitting of all types, complete with all accessories and tube etc. directly on ceiling / wall, including connection with 1.5 sq mm FRLS PVC insulated,copper conductor, single core cable and earthing etc as required. | Each | 155
18 | 1.44 | Installation ,testing and commissioning of ceiling fan, including wiring the down rods of standard length { Up to 30 Cm } with 1.5 sq mm FR PVC insulated, copper conductor, single core cable etc as reqjired. | Each | 75
19 | 1.47 | Supplying and fixing extra down rod of 10 Cm length G. I pipe, 15 mm dia, heavy guage including painting etc. as required ( Note: More than 5 Cm length shall be rounded to the nearest 10 Cm and 5 Cm or less shall be ignored) | Each | 150
20 | 1.50.1 | Installation of exhaust fan up to 450 mm sweep in the existing opening, including, making the hole to suit the size of the above fan, making good the damage, connection, testing , commissioning etc as required. | Each | 10
21 | 2.8 | Supplying and fixing following way, three pole and neutral, sheet steel,MCB distributon board consumer unit, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, detachable gland plate, inter connections, phosphatized and powder painted including earthing etc as required.(But with out MCB/RCCB/Isolator)
a) | 2.8.5 | 4 way, Double door | Each | 2
b) | 2.8.6 | 6 way, Double door | Each | 2
22 | 2.9 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's (but without MCB's and incomer ) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.)
a) | 2.9.5 | 4 way, Double door | Each | 2
23 | 2.1 | Supplying and fixing 5 amps to 32 amps rating, 240 Volts ' C ' series, miniature circuit breaker suitable for inductive load of the following poles in the existing MCB DB complete with connections, testing and commissioning etc as required.
a) | 2.10.1 | Single pole | Each | 50
b) | 2.10.5 | Tripple pole and neutral | Each | 2
24 | 2.11 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc as required. | Each | 20
25 | 2.15 | Supplying and fixing following rating,four pole,415 volts, residual current circuit breaker { RCCB }, having a sensitivity current up to 300 milli amperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a) | 2.15.1 | 25 amps | Each | 2
b) | 2.15.2 | 40 amps | Each | 2
26 | 2.13 | Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a) | 2.13.1 | 40 amps | Each | 2
b) | 2.13.2 | 63 amps | Each | 2
27 | 4.1 | Supplying and installing following size of perforated GI cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with GI suspenders including bolts & nuts, suspenders, bends, tees etc as required.
a) | 4.1.4 | 300 mm width X 50 mm depth X 1.6 mm thickness | Rm | 40
28 | 2.18 | Supplying and fixing 20 amps, 240 Volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top along with 20 amps 'C' series, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket outlet and complete with connections, testing and commissioning etc. as required. | Each | 5
29 | 5.4 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | Set | 2
30 | 5.9 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | Rm | 40
31 | 5.15 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | Rm | 60
32 | 5.17 | Providing and fixing 4 mm dia copper wire on surface or in recess for loop earthing as required. | Rm | 40
33 | 7.1 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
a) | 7.1.3 | Above 95 sq. mm and upto 185 sq. mm | Rm | 170
34 | 7.5 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/HUME/METAL pipe as required.
a) | 7.5.3 | Above 95 sq. mm and upto 185 sq. mm | Rm | 10
35 | 7.7 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
a) | 7.7.1 | Upto 35 sq. mm (clamped with 1mm thick saddle) | Rm | 190
b) | 7.7.2 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | Rm | 100
c) | 7.7.3 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | Rm | 20
36 | 9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
a) | 9.1.32 | 4 X 10 sq. mm | Each | 6
b) | 9.1.33 | 4 X 16 sq. mm | Each | 6
c) | 9.1.21 | 3½ X 35 sq. mm | Each | 6
d) | 9.1.24 | 3½ X 95 sq. mm | Each | 2
37 | 14.13.3 | Providing, laying & fixing 100mm dia GI pipe (medium class) in ground complete with GI fittngs including trenching (75cm) deep and refilling etc as required. | Rm | 10
38 | LMR | Supply of 1x28 watts surface mounted luminaire, CRCA powder coated housing, aluminium reflector, pre-wired complete with all accessories like electronic ballast, 28W T5 lamp etc complete as required. (Philips TMS 122 M IxTL5-28W EBE / GE GET CI 1x28 C/S HF / Crompton T5RSF28EB). | Each | 90
39 | LMR | Supply of 1x28 watts fluroscent tube fitting sleek with decorative end cap, powder coated CRCA steel channel complete with all electrical accessories like electronic ballast, lamp holder, 28W T5 lamp etc complete as required. (Philips TMS 540 HF / GE LMS 28 N N / Crompton T5GP28EBS9). | Each | 10
40 | LMR | Supply of 1x28 watts surface mounted mirror optic luminaire, powder coated CRCA housing, complete with all accessories like electronic ballast, 28W T5 lamp etc complete as required.(Philips TCS150 IxTL5 -28W MI EBT / GE GETC 1x28 MOS HF / Crompton T5CS128EB). | Each | 55
41 | LMR | Supplying and fixing 1x28W Decorative compact street light luminaire with sheet steel aluminium housing, UV stabilized acrylic cover, aluminium reflector, lamp etc complete with all mounting accessories as required. The item shall also include suitable size lamp bracket fabricated out of B class G.I pipe to suit the lamp fitting with its clamping accessories, painting etc as required. (Philips HGS120 1xTL5-28W EBE / GE NA214NG V2 / Crompton T5SFE28EB ) | Each | 10
42 | LMR | Supply of ceiling fan 1200 mm sweep, double ball bearing, approved colour and quality with original down rod, suspension shackle, canopy etc with out regulator complete with all accessories as required. (Usha Sonata Max or equivalent) | Each | 75
43 | LMR | Supply of medium duty exhaust fan 300 mm sweep, metal blades of approved colour, for single phase 230 volt, 50Hz AC supply complete with motor, capacitor, metal grill cover and all accessories as required complete. (Usha Turbo Hi speed or equivalent) | Each | 10
44 | LMR | Supply and installation of 400 mm sweep, wall fan, swinging type with speed control, necessary adapter, of approved colour, for single phase 230 volt, 50Hz AC supply complete with motor, capacitor all accessories as required complete. (Usha Max Air or equivalent) | Each | 5
45 | LMR | Supply & fixing PVC straight / Angle batten holder with ISI marking including connection etc complete with all accessories as required. | Each | 20
46 | LMR | Supply and fixing ISI marked Compact Fluroscent Lamp (CFL), 15 watts of approved quality. | Each | 20
47 | LMR | Supply and fixing Polished aluminium reflector on the PVC straight / angle batten holder etc complete as required. | Each | 20
48 | LMR | Supply of the following size 1.1kV grade XLPE insulated PVC sheathed, armoured Aluminium conductor power cable confirming to IS 7098 (part 1) ammended upto date.
a) |  | 4 x 10 Sq mm | Rm | 60
b) |  | 4 x 16 Sq mm | Rm | 90
c) |  | 3.5 x 35 Sq mm | Rm | 40
d) |  | 3.5 x 95 Sq mm | Rm | 60
49 | LMR | Supplying and fixing following rating, 415 Volts, "C" curve, miniature circuit breaker suitable for power loads of following poles in the existing MCB DB complete with connections, testing and commissioning etc as required.
a |  | 40A TP MCB | Each | 2
b |  | 63A TP MCB | Each | 2
50 | LMR | Supply & fixing modular type computer outlet (RJ-45) with modular base and cover plate, GI box complete with all accessories, connection etc. complete as required. | Each | 5
51 | LMR | Supply and laying CAT 6 cable in the exisitng surface / recessed steel / PVC conduit as required. | Rm | 80
52 | LMR | Supply and Installation of 10 pair MDF box, back mount frame and original krone connectors with all accessories. | Each | 2
53 | LMR | Supply, Installation, Testing & Commissioning of LT floor panel, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP42, free standing, floor mounting, dust and vermin proof, powder coated, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system, including internal wiring with suitable size wires, rotary handle, spreaders, 3mm thick gland plate, hinged type door with neoprene gasket etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification.
Incomer
1 no. 160A, FP, AC23, 415V, 50Hz switch disconnector Fuse unit complete with handle assembly and door interlock and suitable rating HRC fuse.
Busbar
1 Set of 200 TPN busbars of high conductivity electrolytic quality Aluminium alloy.
1 Set of 25 x 3 mm copper busbars of high conductivity electrolytic quality shall be provided throught out the panel for its earthing.
Instruments
1 No 3 phase Digital Multi function meter to read V, A, F, Acc class 1.
1 Set of phase indicating lamps, LED type, RYB.
1 Set of 2A 10kA C curve SP control MCB
1 Set of 100/5A, Class 1.0, 10VA, Cast Resin CT
Outgoing
5 nos. 63A, TPN, C curve, MCB.
|  | 3 nos. 40A, TPN, C curve, MCB. | Each | 1
54 | LMR | Supply, Installation, Testing & Commissioning of Three phase meter box, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP54, wall / floor mounting, dust and vermin proof, powder coated, outdoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system including internal wiring with suitable size wires, rotary handle, spreaders, 3mm thick gland plate, hinged type door with neoprene gasket etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification.
Space provision for accomodating 3 phase CT operated energy meter from KSEB with all connections, glass view panel, control MCB, lockable compartment etc.
3 nos. Suitable ratio CT (as per KSEB) with Acc. Class 0.5, 10VA in locakable compartment.
3 nos 200A rewireable type baklite fuse unit with 1 no. Neutral link.
1 no. 200A, FP, AC23A, 415V, 50Hz switch disconnector fuse unit with Din type HRC fuse of suitable rating (as per KSEB) in separate cubical.
|  | The meter board shall have 250 Amp TPN busbars of high conductivity electrolytic quality Aluminium alloy, earth bus of required size, 4P terminal connectors, control wiring with all reqiuired accessories complete. | Each | 1
55 | LMR | Supplying and laying 10 SWG copper wire on surface / recess / groundloop earthing, including soldering connection / termination with Cu thimble etc as required | Rm | 150
56 | LMR | Preparation, submission of drawings and applications for the installation and service connection to KSEB and obtaining Power allocation, sanction and energising of the installation, road cutting permission, including obtaining sanction from the authorities complete Including providing necessary assistance to the client for obtaining sanctions. | Job | 1
57 | LMR | Supply and providing 6 mm thick & 1 m wide electrical grade chequered type rubber mat to withstand 3.3 KV dielectric strength conforming to IS 5429/ 1969. | Rm | 5
58 | LMR | Supply and providing First Aid Chart duly framed and placed in a conspicuous location for clear vision. | Each | 2
Air Conditioning Works
59 |  | Supply, installation, testing and commissioning of High Wall mounted Split Air Conditioner of 2TR capacity consisting of high wall mounted type room unit (fan coil) with cordless remote control and one number outdoor condensing unit comprising of enegy efficient suitable rotary compressor for operation on single phase, 230 V, 50Hz supply, fixing the outdoor unit on a raised platform as per manufacturers recommendation and fixing of room (fan coil) unit on wall, upto 10 m distance refrigerant copper piping with 13mm nitrile rubber insulation, providing and making interconnection between room & condenser as per site conditions, comprising of 1" dia drain PVC pipe with insulation 10m, canvas connections, full electrical cabling from power plug near indoor unit and to outdoor unit, vibration isolators, first charge refrigarant gas, min 4star rated as per BEE suitable stabilizer etc complete as required. Make: Carrier /Hitachi/Panasonic/LG/Samsung/ Blue star / Voltas | Set | 1 |  |  | #VALUE!
60 |  | Supply and laying of electrical cabling for 2 TR split unit (between indoor & outdoor unit) | Rm | 50
61 |  | Supply laying and fixing of additional length suitable dia copper refrigerant piping between indoor and out door unit for 2TR machine with suitable dia nitrile rubber insulation. | Rm | 10
TOAL PART B - ELECTRICAL WORKS
GRAND TOTAL - PART A + PART B