## ele works
BILL OF QUANTITIES
Electrical works (Internal & Compound lighting)
Sl: No: | Code No | Description of item | Unit | Qty | Rate in figures (Rs.) | Rate in words (Rs.) | Amount (Rs.)
1 | 1.10 | Point wiring in PVC conduit, with Modular type switch: Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
a | 1.10.2 | Group B | Point | 200
b | 1.10.3 | Group C | Point | 580
2 | 1.11 | Twin control point wiring in PVC conduit, with modular type switch: Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. | Point | 40
3 | 1.12 | Power plug wiring in PVC conduit ( 2x4 sq mm ): Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 1 No 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | Metre | 3720
4 | 1.13 | Power plug wiring in PVC conduit ( 4x4 sq mm ): Wiring for light/ power plug with 4X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 2 Nos 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | Metre | 600
5 | 1.14 | Circuit Sub main wiring in PVC Conduit: Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required
a | 1.14.1 | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | Metre | 5400
b | 1.14.2 | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | Metre | 6700
c | 1.14.9 | 4 X 6 sq. mm + 2 X 6 sq. mm earth wire | Metre | 450
6 | 1.17 | Wiring in existing conduit; Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
a | 1.17.1 | 1 x 1.5 sq. mm | Metre | 650
7 | 1.18 | Telephone wiring in existing conduit: Supplying and drawing following pair 0.5 sq mm FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required.
a | 1.18.2 | 2 Pair | Metre | 1800
b | 1.18.3 | 4 Pair | Metre | 1250
8 | 1.19 | T. V cable in existing conduit: Supplying and drawing co-axial TV cable RG-6 grade, 0.7 mm solid copper conductor PE insulated, shielded with fine tinned copper braid and protected with PVC sheath in the existing surface/ recessed steel/ PVC conduit as required. | Metre | 250
PVC CONDUIT, METAL BOXES
9 | 1.21 | S/F PVC conduit: Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
a | 1.21.1 | 20 mm | Metre | 2750
b | 1.21.2 | 25 mm | Metre | 3500
c | 1.21.3 | 32 mm | Metre | 1800
d | 1.21.4 | 40 mm | Metre | 600
e | 1.21.5 | 50 mm | Metre | 400
10 | 1.22 | S/F Metal boxes: Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
a | 1.22.4 | 150 mm X 150 mm X 60 mm deep | Each | 4
b | 1.22.7 | 200 mm X 150 mm X 60 mm deep | Each | 4
c | 1.22.11 | 200 mm X 150 mm X 100 mm deep | Each | 6
d | 1.22.14 | 200 mm X 300 mm X 100 mm deep | Each | 6
11 | 1.24 | S/F Modular type switch/ socket: Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
a | 1.24.1 | 5/6 amps switch | Each | 50
c | 1.24.4 | 3 pin 5/6 amp socket outlet | Each | 100
d | 1.24.6 | Telephone socket outlet | Each | 52
e | 1.24.7 | TV antenna socket outlet | Each | 3
f | 1.24.8 | Bell push | Each | 4
12 | 1.25 | Supplying and fixing electronic fan regulator: Supplying and fixing stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | Each | 120
13 | 1.26 | S/F Modular type blanking plates: Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | Each | 360
14 | 1.27 | S/F Modular boxes, base & cover plate: Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.
a | 1.27.1 | 1 or 2 Module (75mmX75mm) | Each | 250
b | 1.27.5 | 8 Module (125mmX125mm) | Each | 50
c | 1.27.6 | 12 Module (200mmX150mm) | Each | 10
15 | 1.31 | S/F light plug point modular type accessaries: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). | Each | 200
16 | 1.32 | S/F Power plug point with modular type switch: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | Each | 50
17 | 1.33 | S/F Ceiling rose: Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. | Each | 680
18 | 1.38 | S/F call bell/buzzer: Supplying and fixing call bell/ buzzer suitable for single phase, 230 volts, complete as required. | Each | 4
19 | 1.41 | ITC Fluroscent / LED fitting directly on surface/ceiling: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | Each | 350
20 | 1.42 | ITC Fluroscent/LED fitting with down rod: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc., including supplying and fixing ball and socket arrangement, 2 no. down rods of 20 mm dia X 1.6 mm thick steel conduit upto 30 cm length, painting and wiring the down rods and connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | Each | 650
21 | 1.43 | S/F extra down rod: Providing and fixing extra conduit down rod of 20 mm dia, 2 X 10 cm length wiring with 2 X 1.5 sq. mm FR PVC insulated, copper conductor, single core cable including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | Each | 3250
22 | 1.44 | ITC Ceiling fan: Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable etc. as required. | Each | 120
23 | 1.48 | Extra down rod 15 mm dia 20 CM Length: Supplying and fixing extra conduit down rod of 20 cm length G.I. pipe 15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | Each | 600
24 | 1.50 | ITC Exhaust fan: Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required.
| 1.50.1 | Upto 450 mm sweep | Each | 105
25 | 2.2 | S&F MCCB in cubicle Pannel: Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required.
a | 2.2.1 | 100 Amp, 16 KA TP MCCB | Each | 8
b | 2.2.2 | 125 Amp, 16 KA TP MCCB | Each | 6
26 | 2.3 | S/F SP MCB DB: Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
| 2.3.6 | 2 + 6/8 way, Double door | Each | 8
27 | 2.4 | S/F TP MCB DB: Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
a | 2.4.4 | 4 way (4 + 12), Double door | Each | 18
b | 2.4.5 | 6 way (4 + 18), Double door | Each | 12
29 | 2.9 | S/F Vertical Type Pre Wired TP MCB DB: Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required ,suitable for MCCB incomer.(But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.)
a | 2.9.5 | 4 way Double door | Each | 4
b | 2.9.6 | 6 way Double door | Each | 4
c | 2.9.7 | 8 way Double door | Each | 6
30 | 2.10 | S/F 'C' series, MCB: Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 2.10.1 | Single pole | Each | 270
b | 2.10.4 | Triple pole | Each | 28
31 | 2.11 | S/F S P MCB blanking plate: Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | Each | 145
32 | 2.12 | S/F DP MCB isolator: Supplying and fixing following rating, double pole, 240 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
| 2.12.1 | 40 amps | Each | 6
33 | 2.13 | S/F FP MCB Isolator: Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 2.13.1 | 40 amps | Each | 28
b | 2.13.2 | 63 amps | Each | 4
34 | 2.14 | S/F SPN RCCB: Supplying and fixing following rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
| 2.14.1 | 25 amps | Each | 6
35 | 2.15 | S/F TPN RCCB: Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 2.15.1 | 25 amps | Each | 16
b | 2.15.2 | 40 amps | Each | 12
c | 2.15.3 | 63 amps | Each | 4
36 | 2.18 | S/F 20A SPN MCB industrial socket outlet: Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | Each | 4
37 | 2.19 | S/F 20A TPN MCB industrial socket: Supplying and fixing 20 amps, 415 volts, TPN industrial type, socket outlet, with 4 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, TPMCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | Each | 6
38 | 2.20 | S/F 30A TPN MCB industrial socket: Supplying and fixing 30 amps, 415 volts, TPN industrial type, socket outlet, with 4 pole and earth, metal enclosed plug top alongwith 30 amps "C" curve, TPMCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | Each | 6
39 | 2.21 | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | Each | 14
40 | 4.1 | Supplying and installing of perforated pre-painted M.S. cable trays: Supplying and installing following size of perforated pre-painted M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
a | 4.1.2 | 150 mm width X 50 mm depth X 1.6 mm thickness | Metre | 160
b | 4.1.4 | 300 mm width X 50 mm depth X 1.6 mm thickness | Metre | 80
41 | 5.2 | G.I Earth Pipe Electrode With Salt & Charcoal: Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | Set | 4
42 | 5.4 | G.I.Earth plate Electrode with Salt & Charcoal: Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | Set | 6
43 | 5.6 | Copper.Earth plate Electrode With Salt& Charcoal: Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | Set | 2
44 | 5.7 | Supplying and laying 6 SWG G.I. wire in ground: Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including connection/ termination with GI thimble etc. as required. | Metre | 650
45 | 5.16 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess: Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | Metre | 250
46 | 5.19 | Providing and fixing 4.00mm dia copper wire on surface or in recess: Providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/ submain wiring/ cable as required. | Metre | 300
47 | 6.1 | Providing and fixing of lightning conductor finial, made of 25 mm dia 300 mm long, copper tube, having single prong at top, with 85 mm dia 3 mm thick copper base plate including holes etc. complete as required. | Each | 4
48 | 6.3 | Fixing of lightning conductor finial (single prong) with base plate including holes etc. complete as required. | Each | 4
49 | 6.4 | Jointing copper / G.I. tape (with another copper/ G I tape, base of the finial or any other metallic object) by riveting / nut bolting/ sweating and soldering etc as required. | Each | 4
50 | 6.7 | Providing and fixing G.I. tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required.(For horizontal run) | Metre | 250
51 | 6.8 | Providing and fixing G.I. tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required.(For vertical run) | Metre | 100
52 | 6.12 | Providing and fixing testing joint, made of 20 mm X 3 mm thick G.I. strip, 125 mm long, with 4 nos. of G.I. bolts, nuts, chuck nuts and spring washers etc. complete as required. | Each | 4
53 | 6.14 | Providing and laying G.I. tape 32 mm X 6 mm from earth electrode directly in ground as required. | Metre | 40
54 | 7.1 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
a | 7.1.1 | Upto 35 sq. mm | Metre | 500
b | 7.1.2 | Above 35 sq. mm and upto 95 sq. mm | Metre | 50
55 | 7.4 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation, sand cushioning, protective covering and refilling the trench etc as required.
a | 7.4.1 | Upto 35 sq. mm Metre | Mtr | 60
b | 7.4.2 | Above 35 sq. mm and upto 95 sq. mm | Mtr | 50
56 | 7.7 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
a | 7.7.1 | Upto 35 sq. mm (clamped with 1mm thick saddle) | Metre | 30
b | 7.7.2 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | Metre | 60
57 | 9.1 | Supplying and making end termination with brass compression gland and aluminium lugs: Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
a | 9.1.1 | 2x 6 &10 sq mm (19mm) | Each | 90
b | 9.1.21 | 3½ X 35 sq. mm (32mm) | Each | 4
c | 9.1.23 | 3½ X 70 sq. mm (38mm) | Each | 16
d | 9.1.24 | 3½ X 95 sq. mm (45mm) | Each | 12
e | 9.1.32 | 4 X 10 sq. mm (25mm) | Each | 36
f | 9.1.33 | 4 X 16 sq. mm (28mm) | Each | 24
58 | 14.13 | Providing, laying and fixing following dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc as required
a | 14.13.1 | 50 mm dia | metre | 50
b | 14.13.3 | 100 mm dia | metre | 30
Total SR
LMR Items
59 |  | Point wiring in PVC conduit, with Modular type switch, Group control Wiring for light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required for controling two or three lights by single swirch. | Each | 260
60 |  | Supplying and drawing of UTP 4 pair CAT -6A LAN cable in existing surface/ recessed PVC conduit as required, AMP/Molex make | Metre | 3850
61 |  | Supply & installation of modular type Cat 6A information outlet with modular plate & switch box including connection etc as required,AMP/Molex make | Each | 77
62 |  | Telephone wiring in existing conduit: Supplying and drawing following pair 0.5 sq mm FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required.
a |  | 20 Pair | Metre | 150
b |  | 50 Pair | Metre | 60
63 |  | Supply & installation of following pair krone module in suitable size MDF box with all accessories.
a |  | 20 pair | Each | 3
b |  | 50 pair | Each | 1
c |  | 100 pair | Each | 1
64 |  | S/F PVC holder: Supplying and fixing PVC batten/ angle holder including connection etc. as required. | Each | 106
65 |  | S/F DP MCB Isolator with Enclosure: Supplying and fixing DP sheet steel enclosure on surface/ recess along with 25/32amps 240 volts "C" curve DP MCB complete with connections, testing and commissioning etc. as required. | each | 6
66 |  | S/F TP MCB Isolator with Enclosure: Supplying and fixing TP sheet steel enclosure on surface/ recess along with 16/25/32amps 415 volts "C" curve TP MCB complete with connections, testing and commissioning etc. as required. | each | 15
67 |  | Providing and fixing 25 mm X 3mm copper strip on surface or in recess: Providing and fixing 25 mm X 3 mm copper strip on surface or in recess for connections etc. as required. | Metre | 60
68 |  | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
a |  | Upto 35 sq. mm (clamped with 1mm thick saddle) | Metre | 30
b |  | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | Metre | 650
69 |  | Supply of Surface mounted Indoor Industrial Battens Green perform BN208C LED40/CDL L1200 FR + LEDtube 1200mm 18W840 T8 AP I with Mounting Accessories of Philips or Equi | Each | 40
70 |  | Supply of Surface mounted Indoor Industrial Tube, TMC 501 P 2xT-LED with mounting rail for TLED lamps + LED tube 1200mm with Mounting Accessories of Philips or Wipro & Crompton | Each | 440
71 |  | Supply of Surface mounted Endura LED Bulkhead WT 202W LED of Philips/Equi + LED Non Dimmable 5W B22 | Each | 125
72 |  | Supply of Surface mounted High bay green BY400V LED72S CW of Philips with lamp | Each | 10
73 |  | Supply of Recess down lighter DN194B LED15S of Philips/Equi with lamp | Each | 100
74 |  | Supply of Green square down lighter recessed BBS175 1xDLED of Philips or Equi with Lamp | Each | 50
75 |  | Recess mounted full glow RC380B LED 30,glare free of Philips or Equi with lamp | Each | 10
76 |  | Supply of Recess mounted full glow RC170B LED 29S of Philips or Equi with lamp | Each | 25
77 |  | Supplying and fixing Decorative compact out door building light luminaire , Green line BRP409LED CW of Philips or Equi with LED lamp, housing, wiring with 2x1.5 sq mm PVC insulated copper wire with suitable earthing using 1x1.5 sq mm copper wire, lamp bracket fabricated out of suitable Size G.I pipe first quality, to suit the lamp fitting complete testing and commissioning etc as required | Each | 15
78 |  | Supply & installation of LED Lamp Non Dimmable 7/9W B22 on existing angle batten | Each | 106
79 |  | Supply of Linnet - LCL-10-CDL,Sleek LED mirror light,with high out put diffuser, 2 feet size of Crompton or Equi | Each | 15
80 |  | Supply of Indoor down lighter,recessed mounted LED down lights with the option for fixed/ adjustable and spot options. BBS312 1xDLED of Philips or Equi | Each | 20
81 |  | Supply of out door Liara,inverted pyramid tripod type LED bollard with soft 360 light,IP-65 protection,corrosion resistant cat No.LBLS1-10-CDL of Crompton or Equi Philips/Bajaj for compound wall | Each | 35
82 |  | Supply of out door Maple, decorative post top for 360 indirect light,IP-65,impact & corrosion resistant cat No. LPTO-40-CDL/M, 40W LED of Cropmton or equi Philips/Bajaj for gate lighting | Each | 4
83 |  | Supply and installation of IP 65, outdoor LED street light with high pressure die cast aluminium housing, electronic driver etc as required. The light fitting shall be mounted on suitable height pole (max 7.0mtr height), tapered octogonal pole in three distinct sections having thickness 3.25mm to 4.50mm, foundation bolt, base plate, all required accesories etc. The pole shall be hot dip galvanised type, with suitable(1.5mtr: max) brackets, shall be produced as single - armed and equipped in end-piece to secure lanterns. PVC / poly carbonate loop in loop out box, with SP MCB, necessary accessories as required. The cost of the civil foundation shall be measured along with civil items The light fitting shall be suitabily installed with all required accessories to poles. The item shall include 3C x 1.5 sqmm PVC insulated copper unarmoured cable for connecting between the luminiare and the loop in loop out box. (Similar to Green line BRP409LED CW of Philips or Equi with LED lamp). | Each | 34
84 |  | Supply and installation of IP 65, outdoor LED street light with high pressure die cast aluminium housing, electronic driver etc as required. The light fitting shall be mounted on suitable height pole (max 7.0mtr height), tapered octogonal pole in three distinct sections having thickness 3.25mm to 4.50mm, foundation bolt, base plate, all required accesories etc. The pole shall be hot dip galvanised type, with suitable(1.5mtr: max) brackets, shall be produced as double - armed and equipped in end-piece to secure lanterns. PVC / poly carbonate loop in loop out box, with SP MCB, necessary accessories as required. The cost of the civil foundation shall be measured along with civil items The light fitting shall be suitabily installed with all required accessories to poles. The item shall include 3C x 1.5 sqmm PVC insulated copper unarmoured cable for connecting between the luminiare and the loop in loop out box. (Similar to Green line BRP409LED CW of Philips or Equi with LED lamp). | Each | 12
85 |  | Supply and installation of IP 65, outdoor LED street light with high pressure die cast aluminium housing, electronic driver etc as required. The light fitting shall be mounted on suitable height pole (max 7.0mtr height), tapered octogonal pole in three distinct sections having thickness 3.25mm to 4.50mm, foundation bolt, base plate, all required accesories etc. The pole shall be hot dip galvanised type, with suitable(1.5mtr: max) brackets, shall be produced as four - armed and equipped in end-piece to secure lanterns. PVC / poly carbonate loop in loop out box, with SP MCB, necessary accessories as required. The cost of the civil foundation shall be measured along with civil items The light fitting shall be suitabily installed with all required accessories to poles. The item shall include 3C x 1.5 sqmm PVC insulated copper unarmoured cable for connecting between the luminiare and the loop in loop out box. (Similar to Green line BRP409LED CW of Philips or Equi with LED lamp). | Each | 2
86 |  | Supply of ceiling fan 1050/1200 mm sweep,230V,1Ph, complete with double ball bearing, motor blades, down rods, canopy, capacitor etc complete as required 5 star rating (Crompton Riviera / Usha Maxx Air / Khaitan Newtec) | Each | 120
87 |  | Supply and installation of Decorative Wall fan 400 mm sweep, 230V.1Ph, complete with Openable mesh Cover ,string Operated etc as required. (Crompton WM Wind Flo / Usha Helix high speed/ Khaitan Merlin Hi speed) | Each | 80
88 |  | Supply and fitting 250 mm sweep automatic shutter Sleek and stylish design type exhaust fan complete with louvers and cable from ceiling rose / connector to fan. (Usha Crisp Air / Crompton Crossair / Khaitan Vento). | Each | 40
89 |  | Supply and fitting 450 mm sweep heavy duty Industrial type exhaust fan complete with louvers and cable from ceiling rose / connector to fan. (Usha Turbo Hi speed / Crompton Driffair / Khaitan Euro Metal). | Each | 65
90 |  | Supply of Turbo force Industrial type , Pedestral Air circulators 600mm sweep ,with metalic blades of Almonard/Crompton | Each | 40
91 |  | Supply of the following size 1.1kV grade XLPE insulated PVC sheathed, armoured Aluminium conductor power cable confirming to IS 7098 (part 1) ammended upto date.
a |  | 3½ X 95 sq. mm | Metre | 360
b |  | 3½ X 70 sq. mm | Metre | 480
c |  | 3½ X 35 sq. mm | Metre | 60
d |  | 4 X 16 sq. mm | Metre | 420
e |  | 4 X 10 sq. mm | Metre | 450
f |  | 2 x 10 Sqmm | Metre | 180
g |  | 2 x 6 Sqmm | Metre | 600
92 |  | S/F 'C' series, MCB: Supplying and fixing following rating, 415 volts, "C" curve, miniature circuit breaker suitable for inductive load of three pole (TP) in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a |  | 63 Amps | Each | 6
b |  | 40Amps | Each | 4
93 |  | Supplying and fixing U-PVC Trunking Type Cable Management System for Power, Data, Communication Cables/wires complete with Cover Plates, End Caps, Internal & External angles, Cable Retainers, cable Dividers,Tees, accessories etc as required. The same shall be suitable for fixing 6A, 16A Sockets, switches, RJ45, RJ-11 with its modular box & front plate etc. The CMS shall conform to BS:4678/ BS:4662 & corresponding BIS.
|  | Size 105 x 50 mm with separation partition & Plastic clip | Mtr | 60
94 |  | Supply & installation of following modular type switches & sockets in the exisitng DLP trunking with all required accessories like modular box, front plate etc as required.
a |  | 6A socket with switch | Each | 22
b |  | 6/16A socket with switch | Each | 11
c |  | RJ45 data outlet | Each | 12
d |  | RJ11 telephone outlet | Each | 6
95 |  | Preparation of drawings and documents for submissioin to Electrical Inspectorate duly sealed and signed for the total scope of work done. The drawings and documents shall be submitted to client / contractor who is liasoning with statutory bodies for power connection. | LS | 1
Total LMR
Grand Total Electrical (Internal & Compound)