## Summary
CONSTRUCTION OF ANALYTICAL LAB AT KFB, BELGAUM
SUMMARY SHEET
S.NO | Item description | TOTAL AMOUNT
1 | Civil Works
2 | Plumbing Works
3 | Electrical Works
Total
Service tax component to be paid by the bidder
Service tax component to be directly paid by HITES in case the bidder is a Proprietary/ partnership firm
GRAND TOTAL
[INCLUDING 100% SERVICE TAX (a +b)]

## Civil
ANALYTICAL LAB AT KFB, BELGAUM
CIVIL WORKS
Sl.NO | DSR ITEM NO | DESCRIPTION OF WORK | UNIT | QUANTITY | RATE IN FIGURES (Rs.) | RATE IN WORDS (RS.) | AMOUNT (Rs.)
1 | 2.31 | Clearing jungle including uprooting of rank vegetation, grass, brush wood, trees and saplings of girth upto 30 cm measured at a height of 1 m above ground level and removal of rubbish upto a distance of 50 m outside the periphery of the area cleared. | 100sqm | 2000 |  |  | 0
2 | 2.33 | Felling trees of the girth (measured at a height of 1 m above ground level), including cutting of trunks and branches, removing the roots and stacking of serviceable material and disposal of unserviceable material.
2.1 | 2.33.1 | Beyond 30 cm girth upto and including 60 cm girth | Nos | 28 |  |  | 0
2.2 | 2.33.2 | Beyond 60 cm girth upto and including 120 cm girth | Nos | 17 |  |  | 0
3 (a) | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator) /manual means over areas (exceeding 30cm in depth. 1.5 m in width as well as 10 sqm on plan) including disposal of excavated earth, lead upto 50m and lift upto 1.5m, disposed earth to be levelled and neatly dressed. All kinds of soil. | Cum | 680 |  |  | 0
3 (b) | 2.6.1 +2.26.1 | Earth work in excavation by mechanical means (Hydraulic excavator) /manual means over areas (exceeding 30cm in depth. 1.5 m in width as well as 10 sqm on plan) including disposal of excavated earth, lead upto 50m and lift from 1.5m to 3.0m disposed earth to be levelled and neatly dressed. | cum | 30 |  |  | 0
4 | 2.8.1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan) including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All kinds of soil. | cum | 25 |  |  | 0
5 | 2.25 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. | Cum | 710 |  |  | 0
6 | 1.1.2.8 | Conveying and disposing off the excess excavated earth from the site including loading, unloading, hire charges of lorry etc. complete | Cum | 35 |  |  | 0
7 | LMR | Supplying and filling in plinth with Msand under floors, including watering, ramming, consolidating and dressing complete | Cum | 55 |  |  | 0
8 | 2.34.1 | Supplying chemical emulsion in sealed containers including delivery as specified Chlorpyriphos/ Lindane emulsifiable concentrate of 20% | Litre | 290 |  |  | 0
9 | 2.35.3.1 | Treatment of soil under existing floors using chemical emulsion @ one litre per hole, 300 mm apart including drilling 12 mm diameter holes and plugging with cement mortar 1 :2 (1 cement : 2 Coarse sand) to match the existing floor : With Chlorpyriphos/Lindane E.C. 20% with 1% concentration | Sqm | 515 |  |  | 0
10 | 4.1.5 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:3:6 (1 Cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size). | Cum | 98 |  |  | 0
11 | 4.1 | Providing and laying damp-proof course 40 mm thick with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 12.5 mm nominal size). | Sqm | 30 |  |  | 0
12 | 4.13 | Applying a coat of residual petroleum bitumen of grade of VG-10 of approved quality using 1.7 kg per square metre on damp proof course after cleaning the surface with brushes and finally with a piece of cloth lightly soaked in kerosene oil. | Sqm | 30 |  |  | 0
13 | 5.33 | Providing and laying in position machine batched and machine mixed design mix M-25 grade cement concrete for reinforced cement concrete work, using cement content as per approved design mix, including pumping of concrete to site of laying but excluding the cost of centering, shuttering, finishing and reinforcement, including admixtures in recommended proportions as per IS: 9103 to accelerate, retard setting of concrete, improve workability without impairing strength and durability as per direction of Engineer-in-charge. (Note :- Cement content considered in this item is @ 330 kg/cum. Excess/less cement used as per design mix is payable/recoverable separately).
13 (a) | 5.33.1 | All works upto plinth level | Cum | 180 |  |  | 0
13 (b) | 5.33.2 | All works above plinth level upto floor V level | Cum | 180 |  |  | 0
14 | 5.35 | Add for using extra cement in the items of design mix over and above the specified cement content therein | Quintal | 180 |  |  | 0
15 | 5.2.3 | Reinforced cement concrete work in walls (any thickness), including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc. up to floor five level excluding cost of centering, shuttering, finishing and reinforcement : 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size). | Cum | 8 |  |  | 0
16 | 5.9 | Centering and shuttering including strutting, propping etc. and removal of form for :
16 (a) | 5.9.1 | Foundations, footings, bases of columns, etc. for mass concrete | Sqm | 200 |  |  | 0
16 (b) | 5.9.3 | Suspended floors, roofs, landings, balconies and access platform | Sqm | 610 |  |  | 0
16 (c) | 5.9.5 | Lintel beams, Plinth beams, girders, bressumers and catilevers. | Sqm | 760 |  |  | 0
16 (d) | 5.9.6 | Columns, pillars, piers, abutments, posts, and struts. | Sqm | 275 |  |  | 0
16 (e) | 5.9.7 | Stairs, (excluding landings) except spiral-staircases | Sqm | 40 |  |  | 0
16 (f) | 5.9.16.1 | Edges of slabs and breaks in floors and walls.Under 20 cm wide | Metre | 170 |  |  | 0
16 (g) | 5.9.19 | Weather shade, Chajjas, corbels etc., including edges. | Sqm | 30 |  |  | 0
17 | 5.22.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete upto plinth level Thermo-Mechanically Treated bars. | Kg | 47840 |  |  | 0
18 | 6.1.2 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundation and plinth in: Cement mortar 1:6 (1 cement : 6 coarse sand) | Cum | 35 |  |  | 0
19 | 6.4.2 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in : Cement mortar 1:6 (1 cement : 6 coarse sand) | Cum | 120 |  |  | 0
20 | 6.12.2 | Half brick masonry with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundations and plinth in.cement mortar 1:4 (1 cement : 4 coarse sand) | Sqm | 285 |  |  | 0
21 | 6.15 | Extra for providing and placing in position 2 Nos. 6mm dia. M.S. bars at every third course of half brick masonry. | Sqm | 285 |  |  | 0
22 | LMR | Supply and Installation of Modular sandwiched walls of 100 mm thickness with both sides G.I. Powder coated of 60-80 microns froming smooth surface finish with PUFF as infill with density of 45Kg/m3 & 0.8mm Thick hot dipped GI Sheet with zinc coating of 120gsm, necessary stifner to be given as per manufacturer's standard and as per sample approved, including built in risers with perforated return air grilles & provision for installing G4 synthetic washable filters in riser, electrical conduiting and cut-outs for sockets, switches, Magnehelic Guage Box and complete in all respect including, supports, sealants, etc. The filler insulation material shall be PUF (In case the vendors specification are different - vendor should specify the details). Also ref to technical specification in the tender | Sqm | 170 |  |  | 0
23 | LMR | Supply and Installation of Clean room doors with not less than 46mm thick door leaf and frames equal to 100 mm thickness with properly leveled replaceable view panel/glass. Both side Epoxy Powder coated (60-80 microns) 0.8mm thick G.I sheets(hot dipped with zinc coating of 120 gsm)with PUF as infill of density not less than 40+/-2 Kg/m3 .The door panel should meet the Euro classes minimum reaction to fire B-s3,d0 or Class'O'.
Door to be provided with necessary stiffners complete with, not less than 1.2 mm thick epoxy powder coated GI sheet or with anodized aluminium door frames totally flushed with the wall panels, door bottom drop seal/ hinges with lifting arrangement ,SS304 Butt hinges with ball bearings, Double glazed view panel (450x600/150x150 mm) with 6mm toughened (with 4 sided beveled and smooth edges,with moisture traps using silica gel between panes), SS 304 door closure/s suitable to work against a differential air pressure of not less than 25 pascals & be able to lock at 900 / Normal (as specified),Both side SS304 'D' handle(18ø Dia and 254 mm length), Both side 1.2 mm thick SS kick plate (wherever specified), SS Lock & key (wherever specified) and.
Provision for door interlocking system etc. (In case the vendors specification are different - vendor to provide details). Do refer to the technical specification provided in the tender
23.1 |  | Door (D) - Double Leaf | Nos | 1 |  |  | 0
23.2 |  | Door (D1) - Single Leaf | Nos | 8 |  |  | 0
23.3 |  | Door (D2) - Double Leaf | Nos | 12 |  |  | 0
24 | LMR | Clean room doors with view panels made from both sides SS 304 Panel with Matt Finish with PUFF as infill with density of 45Kg/m3 & 0.8mm Thick hot dipped GI Sheet with zinc coating of 120gsm, necessary stifner to be given complete with door bottom drop seal, clean room bearing hinges and door closure suitable for clean room as per manufacturer's standard and as per sample approved. Price to include cost of Mortice dead bolt both side key operation cylinder locks, SS 'D' handles, View panel and any other hardware complete required. Size (W x H) in mm. (Refer dimension and specification to above door item). Also ref to technical specification in the tender
24.1 |  | Door (D1) - Single Leaf (Change Room) | Nos | 4 |  |  | 0
25 | LMR | Factory finished cutouts in wall panels for fixing of electrical/Communication sockets/Module boxes/ Magnehelic guages and any other etc. | Sqm | 5 |  |  | 0
26 | 9.147 | Providing and fixing uPVC Factory made, white colour casement/sliding window and door made of extruded profiles. Profiles of frames and sash will be mitered cut and fusion welded at all corners including drilling of holes for fixing hardware and drinage of water etc, making arrangement for fixing of hardware, EPDM gasket, 1.2 ± 0.2mm thick galvanised steel profile to be inserted in required profile, frame will be fixed to the wall with 8 mm x 100mm long fasteners, all complete as per direction of Engineer-in-Charge. (Glazing, hardware hinges and fitting etc. to be paid seperately.) Note: Each member of window to be measured seperately with clear length.
26 (a) | 9.147.2 | Casement Window (with friction hinge & outward opening) Casement Frame (67 mm x 62 mm) | Metre | 100 |  |  | 0
26 (b) | 9.147.2.2 | Casement Window Sash/Mullion (67 mm x 75 mm) (style, rail and intermediate section) | Metre | 220 |  |  | 0
26 (c) | 9.147.2.3 | Casement Glazing Bead (35 mm x 18 mm) | Metre | 180 |  |  | 0
27 | 9.148.3 | Providing and fixing stainless steel (SS - 304 grade) friction hinges to the side/top hung uPVC windows, of approved quality with necessary stainless steel screws etc. as per direction of Engineer-in-Charge. 300 x 19 x 1.9 mm | Each | 45 |  |  | 0
28 | 9.149 | Providing and fixing casement handle made of zinc alloyed (white powder coated) of uPVC casement windows with necessary screws etc. complete | Each | 45 |  |  | 0
29 | 9.48.2 | Providing and fixing M.S. grills of required pattern in frames of windows etc. with M.S. flats, square or round bars etc. including priming coat with approved steel primer all complete. Fixed to openings /wooden frames with rawl plugs screws etc. | Kg | 800 |  |  | 0
30 | 10.17 | Providing and fixing M.S. fan clamp type I or II of 16 mm dia M.S. bar bent to shape with hooked ends in R.C.C. slabs, beams during laying including painting the exposed portion of loop, all as per standard design complete. | Each | 25 |  |  | 0
31 | 10.28 | Providing and fixing stainless steel (Grade 304) railing made of Hollow tubes, channels, plates etc. including welding, grinding, buffing, polishing and making curvature (wherever required) and fitting the same with necessary stainless steel nuts and bolts complete i/c fixing the railing with necessary accessories & stainless steel dash fasteners , stainless steel bolts etc., of required size, on the top of the floor or the side of waist slab with suitable arrangement as per approval of Engineer-in-charge. ( for payment purpose only weight of stainless steel members shall be considered excluding fixing accessories such as nuts, bolts, fasteners etc.) | Kg | 295 |  |  | 0
32 | 11.41.2 | Providing and laying vitrified floor tiles in different sizes (thickness to be specified by the manufacturer) with water absorption's less than 0.08% and conforming to IS : 15622 of approved make in all colours and shades, laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand) including grouting the joints with white cement and matching pigments etc., complete.Size of Tile 600x600 mm: (Lowest retail price not less than Rs. 900/m2) | Sqm | 540 |  |  | 0
33 | 11.46.2 | Providing and laying Vitrified tiles in different sizes (thickness to be specified by manufacturer) with water absorption less than 0.08 % and conforming to I.S. 15622, of approved make in all colours & shade in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.Size of Tile 600x600 mm: | Sqm | 80 |  |  | 0
34 | 8.2.2.2 | Providing and fixing 18mm thick gang saw cut mirror polished premoulded and prepolished) machine cut for kitchen platforms, vanity counters, window sills , facias and similar locations of required size of approved shade, colour and texture laid over 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels. Granite of any colour and shade: Area of slab over 0.50 sqm.: Lowest retail price not less than Rs. 2500.00/m2( Granite to be selected by the Engineer in charge) | Sqm | 145 |  |  | 0
35 | 12.52.2 | Providing and fixing tiled false ceiling of approved materials of size 595x595 mm in true horizontal level suspended on inter locking metal grid of hot dipped galvanized steel sections ( galvanized @ 120 gsm/sqm, both side inclusive) consisting of main "T" runner with suitably spaced joints to get required length and of size 24x38mm made from 0.30mm thick (minimum) sheet, spaced at 1200mm center to center and cross "T" of size 24x25mm made of 0.30mm thick (minimum) sheet, 1200mm long spaced between main "T" at 600mm center to center to form a grid of 1200x600 mm and secondary cross "T" of length 600mm and size 24x25mm made of 0.30 mm thick (minimum) sheet to be interlocked at middle of the 1200x600mm panel to form grids of 600x600mm and wall angle of size 24x24x0.3 mm |  |  |  |  | 0
|  | and laying false ceiling tiles of approved texture in the grid including, wherever, required, cutting/making, opening for services like diffusers, grills, light fittings, fixtures, smoke detectors etc. Main "T" runners to be suspended from ceiling using GI slotted cleats of size 27 x 37 x 25 x1.6 x mm fixed to ceiling with 12.5 mm dia and 50 mm long dash fasteners, 4mm GI adjustable rods with galvanised butterfly level clips of size 85 x 30 x 0.8 mm spaced at 1200mm center to center along main T, bottom exposed width of 24 mm of all T-sections shall be pre-painted with polyester paint, all complete at all heights as per specifications drawings and as directed by Engineer-in-charge. |  |  |  |  | 0
|  | GI Metal Ceiling Lay in perforated Tegular edge global white color tiles of size 595x595 mm and 0.5 mm thick with 8 mm drop; made of GI sheet having galvanizing of 100 gms/sqm (both sides inclusive) and 20% perforation area with 1.8 mm dia holes and having NRC (Noise Reduction Coefficient ) of 0.5, electro statically polyester powder coated of thickness 60 microns (minimum), including factory painted after bending and perforation, and backed with a black Glass fiber acoustical fleece. | Sqm | 555 |  |  | 0
36 | 4.2.3 | Cement concrete 1:2:4 (1 Cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) to the top of roof slab up to floor V level | cum | 40 |  |  | 0
37 | 13.1.1 | 12 mm cement plaster of mix 1:4 (1 cement: 4 fine sand) for inside walls | Sqm | 1660 |  |  | 0
38 | 13.2.1 | 15 mm cement plaster on the rough side of single or half brick wall of mix :1:4 (1 cement: 4 fine sand) for outside walls | Sqm | 810 |  |  | 0
39 | 13.16.1 | 6 mm cement plaster of mix : 1:3 (1 cement: 3 fine sand) for under side of roof slab | Sqm | 675 |  |  | 0
40 | 13.9.1 + 13.21 | Cement plaster 1:3 (1 cement: 3 coarse sand) finished with a floating coat of neat cement.12 mm cement plaster including providing and mixing water proofing material in cement plaster work in proportion recommended by the manufacturers. to the top surface of sunshade | Sqm | 590 |  |  | 0
41 | 13.8 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. | Sqm | 2335 |  |  | 0
42 | 13.43.1 | Applying one coat of water thinnable cement primer of approved brand and manufacture on wall surface : | Sqm | 2335 |  |  | 0
43 | 13.47.1 | Finishing walls with Premium Acrylic Smooth exterior paint with Silicone additives of required shade New work (Two or more coats applied @ 1.43 ltr/ 10 sqm. over and including priming coat of exterior primer applied @ 2.20 kg/ 10 sqm). | Sqm | 820 |  |  | 0
44 | 13.60.1 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade: Two or more coats on new work. | Sqm | 2335 |  |  | 0
45 | 13.61.1 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade :Two or more coats on new work. | Sqm | 35 |  |  | 0
46 | 16.68 | Providing and laying 60mm thick factory made cement concrete interlocking paver block of M -30 grade made by block making machine with strong vibratory compaction, of approved size, design & shape, laid in required colour and pattern over and including 50mm thick compacted bed of fine sand, filling the joints with fine sand etc. all complete as per the direction of Engineer-in-charge. | Sqm | 235 |  |  | 0
|  | Total Amount |  |  |  |  | 0

## Plumbing
ANALYTICAL LAB AT KFB, BELGAUM
PLUMBING WORKS
Sl.NO | DSR ITEM NO | DESCRIPTION OF WORK | UNIT | QUANTITY | RATE IN FIGURES (Rs.) | RATE IN WORDS (RS.) | AMOUNT (Rs.)
1 | 17.7.1 | P/F wash basin with all fittings White vitreous china Wash basin 630x450mm with a pair of 15mm CP brass pillar taps | Nos | 1 |  |  | 0
2 | 17.11.2 | Providing and fixing white vitreous china laboratory sink with C.I. brackets, C.P. brass chain with rubber plug, 40 mm C.P brass waste and 40mm C.P. brass trap with necessary C.P. brass unions complete, including painting of fittings and brackets, cutting and making good the wall wherever required :
|  | Size 600x450x200 mm | Nos | 9 |  |  | 0
3 |  | providing and fixing PVC Soil, waste and vent pipe to IS: 13592 of SWR quality 4kg/sq.cm pressure rated upto 110mm dia and 6kg/sq.cm pressure rated agriculture series above 100mm, including all fittings, like EG: Bends, Tees, Elbows, Collars, junction, inspection doors, cowls, offsets, access pipes, jointing with rubber rin g/ solvent cement by application of leak proof adhesive like FRP including cutting holes in walss and floors and making good
3.1 | LMR | 100 mm | Rm | 70 |  |  | 0
3.2 | LMR | 75 mm | Rm | 12 |  |  | 0
4 | LMR | Providing and fixing PVC 'P' or 'S' floor trap self cleansing design with or without vent arm complete including cutting and making good the walls and floors.. | Nos | 11 |  |  | 0
5 | LMR | Providing and fixing unplasticised P.V.C. connection pipe with PTMT Nuts, collar and bush of approved quality and colour.
|  | 15 mm nominal bore with 30 cm length | Nos | 1 |  |  | 0
6 | 17.7 | Providing and fixing PTMT Bottle Trap for Wash basin and sink.
6.1 | 17.7.2 | Bottle trap 38 mm single piece moulded with height of 270 mm, effective length of tail pipe 260 mm from the centre of the waste coupling, 77 mm breadth with 25 mm minimum water seal, weighing not less than 263 gms | Nos | 10 |  |  | 0
7 | 17.71 | Providing and fixing PTMT liquid soap container 109 mm wide, 125 mm high and 112 mm distance from wall of standard shape with bracket of the same materials with snap fittings of approved quality and colour, weighing not less than 105 gms. | Nos | 10 |  |  | 0
8 | 17.73.2 | Providing and fixing PTMT towel rail complete with brackets fixed to wooden cleats with CP brass screws with concealed fitting arrangement of approved quality and colour.
|  | 600 mm long towel rail with total length of 645 mm, width 78 mm and effective height of 88mm, weighing not less than 190 gms | Nos | 10 |  |  | 0
9 | 18.7 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer-in-Charge. Internal work - Exposed on wall
9.1 | 18.7.3 | 25 mm nominal outer dia pipes | Rm | 70 |  |  | 0
9.2 | 18.7.4 | 32 mm nominal outer dia pipes | Rm | 10 |  |  | 0
10 | 18.51.1 | Providing and fixing C.P. brass long body bib cock of approved quality conforming to IS standards and weighing not less than 690 gms.
|  | 15 mm nominal bore | Nos | 9 |  |  | 0
11 | 18.5.3.1 | Providing and fixing C.P. brass angle valve for basin mixer and geyser points of approved quality conforming to IS:8931
|  | 15 mm nominal bore | Nos | 1 |  |  | 0
12 | 18.17.1 | P/F gun metal gate valve with C.I. wheel (screwed end) : 25 mm nominal bore
|  | 25 mm nominal bore | Nos | 2 |  |  | 0
|  | GRAND TOTAL |  |  |  |  | 0

## Electrical
ANALYTICAL LAB AT KFB, BELGAUM
ELECTRICAL WORKS
Sl.NO | DSR ITEM NO | DESCRIPTION OF WORK | UNIT | QUANTITY | RATE IN FIGURES (Rs.) | RATE IN WORDS (RS.) | AMOUNT (Rs.)
DSR 2014 ITEMS
1 | 1.1 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc. as required.
1a | 1.10.1 | Group A | Point | 91 |  |  | 0
1b | 1.10.2 | Group B | Point | 10 |  |  | 0
1c | 1.10.3 | Group C | Point | 10 |  |  | 0
2 | 1.11 | Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate,suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc. as required. | Point | 4 |  |  | 0
3 | 1.12 | Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 1 No 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | Metre | 872 |  |  | 0
4 | 1.13 | Wiring for light/ power plug with 4X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 2 Nos 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | Metre | 194 |  |  | 0
5 | 1.14 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required
5a | 1.14.2 | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | Metre | 1001 |  |  | 0
5b | 1.14.4 | 2 X 6 sq. mm + 1 X 6 sq. mm earth wire | Metre | 525 |  |  | 0
5c | 1.14.9 | 4 X 6 sq. mm + 2 X 6 sq. mm earth wire | Metre | 194 |  |  | 0
5d | 1.14.10 | 4 X 10 sq. mm + 2 X 10 sq. mm earth wire | Metre | 80 |  |  | 0
5e | 1.14.11 | 4 X 16 sq. mm + 2 X 16 sq. mm earth wire | Metre | 80 |  |  | 0
6 | 1.18 | Supplying and drawing following pair 0.5 mm dia FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. | [5 empty] | `
6a | 1.18.3 | 4 Pair | Metre | 585 |  |  | 0
7 | 1.19 | Supplying and drawing co-axial TV cable RG-6 grade, 0.7 mm solid copper conductor PE insulated, shielded with fine tinned copper braid and protected with PVC sheath in the existing surface/ recessed steel/ PVC conduit as required. | Metre | 15 |  |  | 0
8 | 1.20 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required. |  |  |  |  | 0
8a | 1.20.1 | 20 mm | Metre | 100 |  |  | 0
9 | 1.21 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
9a | 1.21.1 | 20 mm | Metre | 600 |  |  | 0
10 | 1.24 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
10a | 1.24.6 | Telephone socket outlet | Each | 22 |  |  | 0
10b | 1.24.7 | TV antenna socket outlet | Each | 1 |  |  | 0
11 | 1.25 | Supplying and fixing stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | Each | 5 |  |  | 0
12 | 1.28 | Supplying and fixing following Modular base & cover plate on existing modular metal boxes etc. as required.
12a | 1.28.1 | 1 or 2 Module | Each | 23 |  |  | 0
13 | 1.31 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). | Each | 110 |  |  | 0
14 | 1.32 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | Each | 46 |  |  | 0
15 | 1.5 | Supplying and drawing of UTO & Pair CAT 6 LAN Cable in the existing surface / recessed steel/ PVC conduit as required. | Each | 585 |  |  | 0
16 | 2.2 | Providing and fixing following rating and breaking capacity and pole MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connection etc as required.
16a | 2.2.1 | 100Amp.16KA , TPMCCB | Each | 2 |  |  | 0
17 | 2.5 | Suppling and fixing of following amps surface/recess mounting, vertical type, 415 Volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's (But Without MCB's and Incomer) as required. Note: Vertical type MCB DB is normally used where 3 phase outlets were required.
17a | 2.5.4 | 4 Way (4+12), Double door | Each | 2 |  |  | 0
18 | 2.8 | Supplying and fixing following way prewired TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FRLS PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. As required.(But without MCB/ RCCB/ Isolator)
18a | 2.8.8 | 12 way (4 + 36), Double door | Each | 4 |  |  | 0
19 | 2.10 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
19a | 2.10.1 | Single pole | Each | 108 |  |  | 0
19b | 2.10.2 | Single pole and neutral | Each | 15 |  |  | 0
19c | 2.10.3 | Double pole | Each | 15 |  |  | 0
19d | 2.10.4 | Triple pole | Each | 15 |  |  | 0
19e | 2.10.5 | Triple pole and neutral | Each | 15 |  |  | 0
20 | 2.13 | Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
20a | 2.13.1 | 40 amps | Each | 2 |  |  | 0
20b | 2.13.2 | 63 amps | Each | 1 |  |  | 0
21 | 2.15 | Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
21a | 2.15.2 | 40 amps | Each | 2 |  |  | 0
21b | 2.15.3 | 63 amps | Each | 1 |  |  | 0
22 | 2.17 | Supplying and fixing TP sheet steel enclosure on surface/ recess along with 16/25/32amps 415 volts "C" curve TP MCB complete with connections, testing and commissioning etc. as required. | Each | 20 |  |  | 0
23 | 2.18 | Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | Each | 20 |  |  | 0
24 | 2.19 | Supplying and fixing 20 amps, 415 volts, TPN industrial type, socket outlet, with 4 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, TPMCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | Each | 20 |  |  | 0
25 | 2.20 | Supplying and fixing 30 amps, 415 volts, TPN industrial type, socket outlet, with 4 pole and earth, metal enclosed plug top alongwith 30 amps "C" curve, TPMCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | Each | 20 |  |  | 0
EARTHING:
26 | 5.2 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | Each | 2 |  |  | 0
27 | 5.4 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | Set | 2 |  |  | 0
28 | 5.6 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | Set | 1 |  |  | 0
29 | 5.8 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm) | Metre | 50 |  |  | 0
30 | 5.9 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | Metre | 50 |  |  | 0
31 | 5.11 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe on earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | Metre | 60 |  |  | 0
32 | 5.14 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | Metre | 80 |  |  | 0
33 | 5.15 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | Metre | 80 |  |  | 0
34 | 5.16 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | Metre | 50 |  |  | 0
35 | 5.20 | Providing and fixing earth bus of 50 mm X 5 mm copper strip on surface for connections etc. as required. | Metre | 25 |  |  | 0
LIGHTNING CONDUCTOR
36 | 6.1 | Providing and fixing of lightning conductor finial, made of 25 mm dia 300 mm long, copper tube, having single prong at top, with 85 mm dia 3 mm thick copper base plate including holes etc. complete as required. | Each | 1 |  |  | 0
37 | 6.7 | Providing and fixing G.I. tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required. (For horizontal run) | Metre | 40 |  |  | 0
38 | 6.8 | Providing and fixing G.I. tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required. (For vertical run) | Metre | 15 |  |  | 0
MV CABLE JOINTING & END TERMINATION
39 | 9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
39a |  | 3½ X 25 sq. mm (28mm) | Each | 2 |  |  | 0
40 | 9.2 | Supplying and making outdoor end termination with cast resin compound including aluminium lugs and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
40a |  | 3½ X 25 sq. mm | Each | 2 |  |  | 0
|  | Total of DSR 2014 Items |  |  |  |  | 0
| A | LMR ITEMS:
LT PANELS
41 | LMR | Supply, Installation, Testing and Commissioning compartmentalised, cubicle panel, fabricated out of 2mm thick sheet steel, free standing totally enclosed, dust and vermin proof, suitable for 3PH 415 Volts, with incoming and outgoings, meters, connections, interconnections with suitable size cables, complete with terminating arrangements with lugs, painting, earthing etc, with cable chamber, bus bar chamber etc. Cable Termination for feeders shall be as specified in Single Line Diagram. Wherever Metering other than Indicating Lamps is specified the cost fo metering shall include 3 nos wire wound,Cast Resin CTs of Cl 1.0, 15 VA of feeder rating A / 1 or 5 A even if not specified. All ACBs shall have RYB LED,ON/Off,Trip LED Indicating Lamps. All Outgoing MCCBs above 100 A rating shall have Micro Processor based variable overload and Short Circuit Protection, Spreaders and Terminal Shrouds,Rotary Handles. Below 100A MCCB can be with Fixed Thermal overload and magnetic shortcircuit setting.
41a |  | FLOOR PANEL
Incomer
1 No 200 Amps TPN MCCB
Busbar
1 set of 150 A TPN Aluminium Bus Bar
Outgoings
|  | 6 nos 63 Amps TPN MCB | Nos | 1 |  |  | 0
CABLING
42 | LMR | Supply, testing and commissioning of following sizes of XLPE Insulated, cores laid up, PVC tape/Extruded Inner sheathed,galvanised steel strip armoured, Extruded PVC Type ST2 Sheathed, Aluminium conductor 1.1 kv grade cable as per IS 7098(Part 1) 1988 on wall/ceiling/ cable tray / masonry duct/pipes with suitable MS Clamps wherever required as per specification. |  |  |  |  | 0
|  | 1.1 KV 3 1/2 Core 25 sq.mm | Metre | 100 |  |  | 0
LOW CURRENT WIRING
43 | LMR | Supplying and fixing of 50 pair tag block enclosed in an MS box and mounted on the wall. | Nos | 1 |  |  | 0
44 | LMR | Supplying and laying 50 pair 0.5 Sq.mm. PVC insulated armoured telephone cables. | Metre | 100 |  |  | 0
NETWORKING SYSTEM
45 | LMR | Supplying and fixing following modular switch/ socket on the modular plate & metal box including connections as required. |  |  |  |  | 0
45a | LMR | I/o for Cate 6 E with phase plate base box | Each | 22 |  |  | 0
46 | LMR | Supplying and fixing of 24 Port Network switch with all accessories etc. complete. | Each | 1 |  |  | 0
47 | LMR | Supplying and fixing of 4 U Rack suitable for fixing 24 Port Network switch with all accessories etc. complete. | Each | 1 |  |  | 0
48 | LMR | Supplying and fixing of Network LIU with all accessories etc. complete. | Each | 2 |  |  | 0
49 | LMR | Supplying and fixing of SFU for Network LIU with all accessories etc. complete. | Each | 2 |  |  | 0
50 | LMR | Supplying and fixing of SFU adapter wire with jack at 2 ends with all accessories etc. complete. | Each | 2 |  |  | 0
51 | LMR | Supplying and laying of single mode OFC cable inclusive of splicing and all accessories complete etc. | Metre | 100 |  |  | 0
INTERNAL LIGHTING FIXTURES & FANS
Supplying, installation, testing and commissioning of the following luminaries on surface / wall/ false ceiling with Necessary accessories for illumination. the cost shall include fixtures, luminarie, fixing accessories, required support structures, terminationetc. complete.
52 | LMR | 1x28W, indoor surface mountable fluorescent CRCA sheet steel power coated body light fixture, 28W T5 lamp, electronic HPF ballast, lamp holder, prewired complete with all necessary accessories suitable for operation on 230V, 50Hz AC supply as required | Nos | 8 |  |  | 0
53 | LMR | Supply of 1200 mm sweep min three star rated ceiling fan complete with motor, double ball bearing, blades, canopy, 30 cm down rod and without speed regulator suitable for 230 V 50 HZ, AC supply confirms to IS 374/1979 as required complete. | Nos | 5 |  |  | 0
54 | LMR | Supply of 300mm sweep exhaust fan, metal blades with safety guard suitable for single phase 230 volt, 50Hz AC supply complete with motor, capacitor and all accessories as required complete. | Nos | 2 |  |  | 0
55 | LMR | Supply, installation of 2 x 2 feet square type LED light fitting with luminaire similar to bajaj 'DOMINTO' Sleek suspended / recess mounting LED 2x2 luminaire at office space | Nos | 71 |  |  | 0
56 | LMR | Supply, installation Garnet 7W White Round LED light fitting with luminaire similar to WIPRO Garnet 7W White Round LED at office space | Nos | 15 |  |  | 0
57 | LMR | Supply and fixing of Flexi LED strip in the decorative false ceiling approximately 5 mtr roll inclusinve of connections and all accessories etc. complete 5W/mtr, IP20, 5mtr roll (IP20 driver included) | Nos | 4 |  |  | 0
MISCELLANEOUS WORKS
58 | LMR | Supplying and fixing of cupper strip of size 50mm width thickness 0.5mm( for antistatic earthing in all thelabs )in floor, surface and furnitures etc complete with all accessories inclusive of fixing and pasting | Kg | 68.05 |  |  | 0
59 | LMR | Supply & providing first aid chart duly framed and fixed in proper manner in MV panel room / Generator room/Electrical room | Set | 1 |  |  | 0
60 | LMR | Supply & providing Co2 5Kg (Dry chemical ) Fire extinguisher with necessary mounting bracket and fixed neatly in MV panel room / Generator | Nos | 15 |  |  | 0
61 | LMR | Supply & laying ISI marked electrical grade chequered type rubber mat of size 2m x 1m x 6 mm suitable for 415V power supply. | Nos | 1 |  |  | 0
|  | Total of LMR Items (A) |  |  |  |  | 0
| B | SMOKE DETECTION AND FIRE ALARM SYSTEM
PORTABLE CHEMICAL FIRE EXTINGUISHER
62 | LMR | Supply, Installation & Testing of GE / Morley/Honey well make addressable Photoelectric type Smoke detector for below/abovefalse ceiling with base plate. | Nos | 20 |  |  | 0
63 | LMR | Supply, Installation & Testing of GE / Morley/honeywell make addressable photoelectric type Heat detector with base plate | Nos | 5 |  |  | 0
64 | LMR | Supply, Installation & Testing of Response Indicator | Nos | 25 |  |  | 0
65 | LMR | Supply, Installation & Testing of Addressable typr Electronic Hooter complete with line matching transformer & connected to the main control panel amplifier to produce alter / evacuation tone for public | Nos | 1 |  |  | 0
66 | LMR | Supply, Installation & Testing of of Addressable type Manual Call Point with a glass cover marked " IN CASE OF FIRE PRESS" | Nos | 2 |  |  | 0
67 | LMR | Supply, Installation, Testing & commissioning of Fault Isolator module | Nos | 1 |  |  | 0
68 | LMR | Supply of Cable (2cx 1.5 Sq mm cu Ar Cable) (Red colour only) with necessary accessaries and hardware etc inclusive of PVC). | Rmt | 200 |  |  | 0
69 | LMR | Supply, Installation, Testing & commissioning of Two Loop non - expandable addressable type Fire Alarm Panel with Battery backup with capacity for 99 addressable devices including event logging facility, printing facility, interface feature & including all necessary hardware & accessories, etc. complete as required. | Nos | 1 |  |  | 0
|  | Total of LMR Items (B) |  |  |  |  | 0
| C | CENTRALISED UPS SYSTEM
(POWER BACKUP SYSTEM)
70 | LMR | Supply, Installation, Testing & Comissioning of 20 KVA DSP based Online UPS with IGBT rectifier, IGBT inverter , nominal input voltage of 480V, 4 wired with 3 pole breaker and output nominal voltage 480V , 20KVA power output with 93% full load capacity with multifunction LCD status console , Emergency power off operating at temperature of 0-40 degress. | Set | 1 |  |  | 0
Double Conversion Technology with Static Bypass For 90 minute backup to the stated load complete with all necessary hardware & accessories, etc. complete as required.
71 | LMR | Required number of VRLA/SMF Battery - 12 V for Battery backup upto 30 minutes With Battery cabinets and Cables along with necessary hardware, accessories - Battery Breaker, Racks, Linkset & Battery to UPS Cablesetc. complete as required. | Set | 1 |  |  | 0
Network management card (OC WAP Card) for the UPS to connect to the server. (If required.)
72 | LMR | Delivery & Installation charges | Set | 1 |  |  | 0
Full set as above
EATON/APC/EMERSON
|  | Total of LMR Items (C) |  |  |  |  | 0
| D | AIR CONDITIONING SYSTEM
73 |  | Supply of Air Cooled cassette type Split Air Conditioner of following capacities consisting of assette type room unit (fan coil) with cordless remote control, outdoor condensing unit comprising of enegy efficient suitable rotary compressor for operation on single phase, 415V, 50Hz supply(3TR)/230V,50Hz(2TR & 1TR), upto 4 m distance refrigerant copper piping with 13mm nitrile rubber insulation, comprising of 1" dia drain PVC pipe with insulation 5m, canvas connections, full electrical cabling from power plug near indoor unit and to outdoor unit 4m distance, out door unit MS stand, suitable stabilizer etc complete as required. Approved makes, AC :- Carrier/Voltas/Bluestar - Stabilizer :- V Guard/Everest/Voltas
73a | LMR | 3TR minimum 3 star rated as per BEE | Nos | 3 |  |  | 0
73b | LMR | 2TR minimum 3 star rated as per BEE | Nos | 3 |  |  | 0
73c | LMR | 1TR minimum 3 star rated as per BEE | Nos | 3 |  |  | 0
74 | LMR | Installation, testing and commissioning of the 3TR machines including fixing the outdoor unit on a raised platform/MS Stand as per manufacturers recommendation and fixing of room (fan coil) unit on wall, providing and making interconnection between room & condenser as per site conditions with first charge refrigerant gas. | Lot | 3 |  |  | 0
75 | LMR | Installation, testing and commissioning of the 2TR machines including fixing the outdoor unit on a raised platform/MS Stand as per manufacturers recommendation and fixing of room (fan coil) unit on wall, providing and making interconnection between room & condenser as per site conditions with first charge refrigerant gas. | Lot | 3 |  |  | 0
76 | LMR | Installation, testing and commissioning of the 1TR machines including fixing the outdoor unit on a raised platform/MS Stand as per manufacturers recommendation and fixing of room (fan coil) unit on wall, providing and making interconnection between room & condenser as per site conditions with first charge refrigerant gas. | Lot | 3 |  |  | 0
77 | LMR | Supply, installation, testing and commissioning of suitable hard drawn copper refrigerant piping additional length for 3 TR,2TR,1TR machines with suitable mm nitrile rubber insulation & suitable size electrical cabing interconnecting the condensing unit to evaporating unit for split units as per site condition.Totaline/ Piyush/ Mandev | Rmt | 50 |  |  | 0
78 | LMR | Supply & fixing of PVC drain pipe additional length of 25mm dia ISI marked, connecting the drain lines from the indoor units to floor sump, with 9mm nitrile rubber insulation as per specification. Any ISI marked | Rmt | 50 |  |  | 0
|  | Total of LMR(D) |  |  |  |  | 0
|  | Total of LMR Items [A] + [B] + [C] + [D] |  |  |  |  | 0
|  | Total of DSR 2014 Items |  |  |  |  | 0
|  | Total of LMR Items |  |  |  |  | 0
|  | GRAND TOTAL |  |  |  |  | 0