## IO summary
BMS I-O (Input - Output) Summary
Sl. No | Description | Qty | DI | AI | DO | AO | Filed devices
1 | CHILLERS-2 | 2 |  | 2
a. | Chiller On/Off Command |  |  |  | 2 |  | Relay Contact
b. | Chiller Run Status |  | 2 |  |  |  | Potential free contact from the Chiller DB panel
c. | Chiller Auto/Manual Status |  | 2 |  |  |  | Potential free contact from the Chiller DB panel
d | Chiller trip/fault |  | 2 |  |  |  | Potential free contact from the Chiller DB panel
e | Individual Chiller Chilled water supply temp in (1) + out |  |  | 4 |  |  | Immersion type sensor
f | Ambient Temperature |  |  | 1 |  |  | Outside air temp & RH sensor
g | Ambient RH |  |  | 1
h | Header Chill water supply & Return Temperature |  |  | 2 |  |  | Immersion type sensor
i | Chiller water flow switch |  | 2 |  |  |  | Water flow switch
k | Butterfly Valve Open / Close Command |  |  |  | 4 |  | Relay Output from DDC to Motorized Butterfly Valves
l | Butterfly Valve Open / Close Status |  | 4 |  |  |  | Pot Free Contact From Motorized Butterfly Valves
| Sub Total |  | 12 | 8 | 6 | 0
| Primary Chilled Water Pumps | 3
1 | Pump start / stop |  |  |  | 3 |  | Volt Free Contact from BMS to Pump panel
2 | Pump run status |  | 3 |  |  |  | Differential Pressure Switch
3 | Pump Auto / Manual switch status |  | 3 |  |  |  | Volt Free Contact to BMS from Pump panel
| Sub Total |  | 6 | 0 | 3 | 0
| Secondary Chilled Water Pumps | 3
1 | Pump start / stop |  |  |  | 3 |  | Volt Free Contact from BMS to Pump panel
2 | Pump run status |  | 3 |  |  |  | Differential Pressure Switch
3 | Pump Auto / Manual switch status |  | 3 |  |  |  | Volt Free Contact to BMS from Pump panel
4 | VFD Speed Control |  |  |  |  | 3 | BMS Vender to provide VFD
5 | VFD Speed Feedback |  |  | 3 |  |  | BMS Vender to provide VFD
| Sub Total |  | 6 | 3 | 3 | 3
| Condeuser Pumps | 3
1 | Pump start / stop |  |  |  | 3 |  | Volt Free Contact from BMS to Pump panel
2 | Pump run status |  | 3 |  |  |  | Differential Pressure Switch
3 | Pump Auto / Manual switch status |  | 3 |  |  |  | Volt Free Contact to BMS from Pump panel
| Sub Total |  | 6 | 0 | 3 | 0
| CooLing Towerfans | 2
1 | Pump start / stop |  |  |  | 2 |  | Volt Free Contact from BMS to Pump panel
2 | Pump run status |  | 2 |  |  |  | Differential Pressure Switch
3 | Pump Auto / Manual switch status |  | 2 |  |  |  | Volt Free Contact to BMS from Pump panel
| Sub Total |  | 4 | 0 | 2 | 0
| Chiller Plant |  | 34 | 11 | 17 | 3
2 | AHU(GENEARAL) | 6
a | AHU ON/OFF command |  |  |  | 6 |  | Relay output from DDC
b | AHU run status |  | 6 |  |  |  | Differential pressure switch(Air)
c | AHU A/M status |  | 6 |  |  |  | Potential free contact from the AHU DB panel
d | AHU filter status |  | 6 |  |  |  | Differential pressure switch(filter)
e | Return Air Temperature sensor |  |  | 6 |  |  | Duct Temp. Sensor
g | 2 Way Modulating CHW Valve with Actuator |  |  |  |  | 6 | 2 way modulating valve + Actuator
3 | AHU- -( Opeation theatre) | 6
1 | AHU VFD ENABLE |  |  |  | 6 |  | AT AHU LOCAL PANEL
2 | AHU VFD SPEED CONTROL |  | 6 |  |  |  | AT AHU LOCAL PANEL
3 | AHU BLOWER STATUS |  | 6 |  |  |  | AIR DP SWITCH
4 | AHU AUTO MANUAL STATUS |  | 6 |  |  |  | AT AHU LOCAL PANEL
5 | AHU SUPPLY AIR TEMP |  |  | 6 |  |  | DUCT TEMP. SENSOR
6 | AHU RETURN AIR TEMP |  |  | 6 |  |  | DUCT TEMP. SENSOR
| AHU FRESH AIR TEMP |  |  | 6 |  |  | DUCT TEMP. SENSOR
7 | AHU RETURN AIR HUMIDITY |  |  | 6 |  |  | DUCT HUMIDITY SENSOR
8 | AHU CHW MODULATING VALVE Command |  |  |  |  | 6 | MODULATING VALVE
9 | AHU CHW MODULATING VALVE STATUS |  |  | 6 |  |  | MODULATING VALVE
10 | RETURN AIR FAN STATUS |  | 12 |  |  |  | AT AHU LOCAL PANEL
11 | FILTER STATUS |  |  | 12 |  |  | AIR DP TRANSMITTER
12 | ROOM TEMPERATURE |  |  | 6 |  |  | ROOM TEMP. SENSOR
13 | FRESH AIR DAMPER STATUS |  | 12 |  |  |  | AT DAMPER
14 | FRESH AIR DAMPER CONTROL |  |  |  | 12 |  | AT DAMPER
15 | PRE-FILTER STATUS |  | 12 |  |  |  | AIR DP SWITCH
16 | MICROVEE FILTER STATUS |  |  | 12 |  |  | AIR DP TRANSMITTER
| AHU SUB TOTAL |  | 72 | 66 | 24 | 12
4 | FCUs | 157
1 | Start/Stop |  |  |  | 157 |  | Potential Free Contact from BMS to FCU panel
2 | Room Air Temp |  |  | 157 |  |  | Temp. Sensor inbuilt with display and set poinit adjustment
3 | Modulate Chilled Water Valve |  |  |  |  | 157 | 2 Way Control Valve
4 | 3 speed fan control |  |  |  | 157 |  | Potential Free Contact from BMS to FCU panel
| Sub Total for FCU |  | 0 | 157 | 314 | 157
5 | Exhaust Fan | 10
1 | Fan ON/OFF command |  |  |  | 10 |  | Pot Free contact
2 | Fan run status |  | 10 |  |  |  | Pot Free contact
3 | Fan A/M status |  | 10 |  |  |  | Pot Free contact
| Total Exhaust fan |  | 20 | 0 | 10 | 0
6 | Water Treatment Plant - | 1
a | Pump On/Off Control |  |  |  | 2 |  | Relay output from DDC
b | Pump Flow Monitoring |  | 2 |  |  |  | Differential Pressure Switch
c | Pump A/M status |  | 2 |  |  |  | Potential free contact
d | Pump trip status |  | 2 |  |  |  | Potential free contact
e | Treated Water Sump Level Monitoring |  | 2 |  |  |  | Level Switch
| TOATAL FOR WATER TREATMENT PLANT |  | 8 | 0 | 2 | 0
| DRINKING WATER PUMP (2 Nos) | 2
a | Pump On/Off Control |  |  |  | 2 |  | Relay output from DDC
c | Pump A/M status |  | 2 |  |  |  | Potential free contact
e | Treated Water Sump Level Monitoring |  | 2 |  |  |  | Level Switch
| Total for DRINKING WATER PUMP |  | 4 | 0 | 2 | 0
| Water Management System |  | 12 | 0 | 4 | 0
8 | MV PANEL - 1 No | 1
a | Breaker On/Off status |  | 4 |  |  |  | Voltfree terminal from Panel
b | Earth Fault |  | 4 |  |  |  | Voltfree terminal from Panel
c | Over Current Alarm |  | 8 |  |  |  | Voltfree terminal from Panel
| Total MV Panel |  | 16 | 0 | 0 | 0
| TOTAL PLANT IO's |  | 166 | 234 | 373 | 172
9 | INTEGRATION
Third Party Integration on BACNET/Modbus
a | VRVInterface -Bacnet/Modbus communication | 3 |  |  |  |  | Through Software Integration
b | VFD for Secondary Pump | 4 |  |  |  |  | Through Software Integration
c | Energy Meter Communication | 12 |  |  |  |  | Through Software Integration
d | Lift | 6 |  |  |  |  | Through Software Integration