## Ele. estimate-4
PART II - Electrical Works
Sl No | Description | Qty | Unit | Rate( Rs in figures & Words) | Amount
A. LT Wiring
1 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FR PVC insulated copper conductor single core cable in recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FR PVC insulated copper conductor single core cable etc as required.
| Group B | 110 | Each
2 | Wiring for twin control light point with 1.5 sq.mm FR PVC insulated copper conductor single core cable in surface / recessed steel conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FR PVC insulated copper conductor single core cable etc as required. | 2 | Each
3 | Wiring for circuit/submain wiring along with earth wire with the following sizes of FR PVC insulated copper conductor, single core cable in surface medium class PVC conduit as required.
a | 2 x 1.5 sq.mm + 1 x 1.5 sq.mm earth wire | 650 | m
b | 2 x 2.5 sq.mm + 1 x 2.5 sq mm earth wire | 500 | m
c | 2 x 4.0 sq.mm + 1 x 4.0 sq mm earth wire | 400 | m
d | 4 x 6 sq. mm + 2 x 6 sq. mm earth wire | 150 | m
4 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
a | 20 mm | 250 | m
b | 25 mm | 250 | m
5 | Supplying and drawing 2 pair 0.5 sq mm FR PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. | 250 | m
6 | Supplying and fixing Telephone socket outlet on the existing modular plate & switch box including connections but excluding modular plate etc. as required. | 12 | Each
7 | Supplying and fixing stepped type electronic fan regulator-modular on the existing modular plate switch box including connections but excluding modular plate etc. as required. | 5 | Each
8 | Supply and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | 5 | Each
9 | Supplying and fixing following size / modules, PVC box alongwith modular base & cover for modular telephone/ data sockets in recess / surface etc as required.
a | 1 or 2 module | 15 | Each
10 | Supplying and fixing suitable size PVC box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. | 40 | Each
11 | Supplying and fixing suitable size PVC box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 45 | Each
12 | Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. | 30 | Each
13 | Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, false ceiling with chain and hook including connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | 50 | Each
14 | Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable etc. as required. | 5 | Each
15 | Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required.
a | Upto 450 mm sweep | 3 | Each
16 | Supplying and fixing extra conduit down rod of 20 cm length G.I. pipe 15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | 10 | Each
B. MCBs, DBs and Cable Trays
17 | Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required (But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.)
| 6way, Double door | 3 | Each
18 | Supplying and fixing following way prewired TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required.(But without MCB/ RCCB/ Isolator)
a | 4 way, Double door | 1 | Each
b | 6 way, Double door | 2 | Each
c | 8 way, Double door | 1 | Each
19 | Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 40 amps | 2 | Each
b | 63 amps | 3 | Each
20 | Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 25 amps | 1 | Each
b | 40 amps | 2 | Each
c | 63 amps | 3 | Each
21 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | Single pole | 60 | Each
b | Triple pole | 10 | Each
c | Triple pole and neutral | 4 | Each
22 | Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | 40 | Each
23 | Supply and fixing TP sheet steel enclosure on surface recess along with 16/25/32/ amps 415V "C" curve TP MCB complete with connections, testing and commissioing etc as required. | 10 | Each
24 | Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 10 | Each
25 | Supplying and fixing 30 amps, 415 volts, TPN industrial type, socket outlet, with 4 pole and earth, metal enclosed plug top alongwith 30 amps "C" curve, TPMCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 5 | Each
26 | Supply and installing 300mm x 50 mm depth x 1.6mm thick perforated GI cable trays with perforations not more than 17.5% in convenient sections, joined with connectors, GI suspenders including nuts and bolts, bends, tees etc as required | 50 | m
C. Earthing
27 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 2 | Each
28 | Earthing with GI earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 4 | Each
29 | Supply and laying 25mm x 5mm copper strip at 0.5m below ground as strip earth electrode, including connection / terminating with nut, bolt, spring, washer etc as required (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced 50mm). | 20 | m
30 | Supply and laying 25mm x 5mm GI strip at 0.5m below ground as strip earth electrode, including connection / terminating with nut, bolt, spring, washer etc as required (Jointing shall be done by overlapping and with 2 sets of GI nut bolt & spring washer spaced 50mm). | 50 | m
31 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 15 | m
32 | Providing and fixing 25 mm X 5 mm GI strip on surface or in recess for connections etc. as required. | 60 | m
33 | Providing and fixing 8 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 150 | m
D. MV & HV Cable laying and Termination
34 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
a | Upto 35 sq. mm | 70 | m
b | Above 35 sq. mm and upto 95 sq. mm | 80 | m
c | Above 95 sq. mm and upto 185 sq. mm | 50 | m
35 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
a | Upto 35 sq. mm (clamped with 1mm thick saddle) | 280 | m
b | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 150 | m
c | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 30 | m
36 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
a | Upto 35 sq. mm (clamped with 1mm thick saddle) | 100 | m
b | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 120 | m
c | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 70 | m
37 | Supplying and making cable route marker with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) of size 60 cm X 60 cm at the bottom and 50 cm X 50 cm at the top with a thickness of 10cm including inscription duly engraved as required. | 20 | Each
38 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
a | 3.5 x 185 sqmm cable | 4 | Each
b | 3.5 x 95 sqmm cable | 4 | Each
c | 3.5 x 70 sqmm cable | 2 | Each
d | 3.5 x 35 sqmm cable | 8 | Each
e | 3.5 x 25 sqmm cable | 10 | Each
f | 4 x 16 sqmm cable | 6 | Each
g | 4 x 10 sqmm cable | 4 | Each
h | 4 x 6 sqmm cable | 6 | Each
39 | Providing, laying and fixing of 100mm dia G.I. pipe (medium class) in ground complete with G.I. fittings including trenching (75 cm deep)and re-filling etc as required | 20 | m
40 | Providing, laying and fixing of 150 mm dia RCC pipe NP2 class (light duty) in ground complete with RCC collars, jointing with cement mortar 1:2 (1 cement : 2 fine sand) including trenching (75 cm deep) and refilling etc as required. | 40 | m
E. LT Panel Board and Accessories
41 | Supply, Installation, Testing & Commissioning of cubicle type Main MV panel board, made out of 2mm thick CRCA sheet, totally enclosed, IP42, free standing, floor mounting, dust and vermin proof, powder coated, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system, including internal wiring with suitable size wires, rotary handle, spreaders etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification.
Incomer
1 no. 200A, 25kA, TP+NL MCCB having isolation duty with E/F rlease, adjustable thermal magnetic release for O/L & SC protection.
Busbar
1 Set of 250 Amp TPN busbars of high conductivity electrolytic quality Aluminium alloy.
Instruments
1 No 3 phase Digital Multi function meter to read V, A, F with Acc class 1.
1 No 3 phase 4 wire CT operated energy meter, 5-10A, Acc. Class 1.
1 Set of phase indicating lamps, LED type, RYB.
1 Set of 2A 10kA C curve SP control MCB
1 Set of 200/5A, Class 1.0, 10VA, Cast Resin CT for metering.
1 Set of 200/5A, Class 1.0, 10VA, Cast Resin CT for APFC relay.
3 nos Ammeter (0-200A), Acc class 1 with 240 deg., defl. Scale.
Outgoing
6 nos. 63A, TPN C curve MCB.
2 nos. 25A, TPN C curve MCB.
| 4 nos. 40A, TPN C curve MCB. | 1 | Job
42 | Supply, Installation, Testing & Commissioning of 30kVAR APFC panel, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP42, free standing, floor mounting, dust and vermin proof, powder coated, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system, including internal wiring with suitable size wires, rotary handle, spreaders etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification.
Incomer
1 No 63A, TPN, C curve MCB.
Busbar
1 Set of 100 Amp TPN busbars of high conductivity electrolytic quality Aluminium alloy.
Instruments
1 No 3 phase Digital Multi function meter to read V, A, F with Acc class 1.
1 Set of phase indicating lamps, LED type, RYB.
1 Set of 2A 10kA C curve SP control MCB
1 Set of 60/5A, Class 1.0, 10VA, Cast Resin CT for metering.
1 no. 6 stage microprocessor based APFC relay
4 set On, Off push button
4 set On, Off LED type indication lamp
1 set Auto / manual selector switch.
Outgoing
2 No 32A, TPN, C curve MCB.
2 No 25A, TPN, C curve MCB.
2 Nos. 10kVAR MPP heavy duty capacitor with capacitor duty contactor.
1 Nos. 5kVAR MPP heavy duty capacitor with capacitor duty contactor.
| 1 No. 5kVAR MPP heavy duty capacitor directly connected. | 1 | Each
43 | KSEB Meter Board - Supply, Installation, Testing & Commissioning of Three phase meter box, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP54, wall / floor mounting, dust and vermin proof, powder coated, outdoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system including internal wiring with suitable size wires, rotary handle, spreaders, 3mm thick gland plate, hinged type door with neoprene gasket etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification.
Switchgear & other Accessories
3 phase CT operated energy meter from KSEB with all connections, glass view panel, control MCB, lockable compartment etc.
3 nos. Suitable ratio CT (as per KSEB) with Acc. Class 0.5, 10VA in locakable compartment.
3 nos 200A cutout fuse unit with fuse and 1 no. Neutral link.
1 no. 200A, FP, AC23A, 415V, 50Hz switch disconnector fuse unit with Din type HRC fuse of suitable rating (as per KSEB) in separate cubical.
1 Set of phase indicating lamps, LED type, RYB.
1 Set of 2A 10kA C curve SP control MCB
1 no of Analogue voltmeter, Acc. Class 1 with selector switch.
| The meter board shall have 250 Amp TPN busbars of high conductivity electrolytic quality Aluminium alloy, earth bus of required size, 4P terminal connectors, control wiring with all reqiuired accessories complete. | 1 | Each
F. LT Cables
44 | Supply of the following size 1.1kV grade XLPE insulated PVC sheathed, armoured Aluminium conductor power cable confirming to IS 7098 (part 1) ammended upto date.
a | 3.5 x 185 sqmm cable | 120 | m
b | 3.5 x 95 sqmm cable | 150 | m
c | 3.5 x 70 sqmm cable | 60 | m
d | 3.5 x 35 sqmm cable | 120 | m
e | 3.5 x 25 sqmm cable | 100 | m
f | 4 x 16 sqmm cable | 140 | m
g. | 4 x 10 sqmm cable | 140 | m
h | 4 x 6 sqmm cable | 60 | m
G. Light Fixtures
45 | Supply of 1x28W flourescent tube fitting, powder coated CRCA steel channel complete with all electrical accessories like electronic ballast, lamp holder, 28W T5 lamp etc complete as required. (Philips TMS122M IxTL-528W EBT / Wipro WIF 90128 SG / GE GET CI 1x28 C/S HF) | 30 | Each
46 | Supply of 2x28W surface mounting flourescent tube light luminaire with mirror optic with all electrical accessories like electronic ballast, lamp holder, 28W T5 lamps etc complete as required. (Philips TPS814 2xTL5-28W EPB D8 / GE PFS 228 MI O) | 6 | Each
47 | Supply and installation of recess mounted type 2x36W CFL cleanroom light fitting with option of rear opening / front opening in robust CRCA housing, glass cover with all electrical accessories like electronic ballast, lamp holder, 36W CFL lamps, mounting chain, hook etc complete as required. (Philips FCS650 2xPL-L36W EBP FOP GT / Wipro WIP 43236 SGA / GE CRP 236CFL BO) | 8 | Each
48 | Supply of 1x36W surface mounting mirror optic luminaire with paralite P5 louvers with all electrical accessories like electronic ballast, lamp holder, 36W CFL lamps etc complete as required. (Wipro WVP 25136 SGW / GE GE CFL 2x18W MOP) | 15 | Each
49 | Supply and installation of 2x36W recess mounted direct - indirect downlight luminaire, with translucent acrylic diffuser, powder coated CRCA housing complete with all electrical accessories like electronic ballast, lamp holder, 36W CFL lamp, mounting chain, hook etc complete as required. (Philips FBS580 2xPL-L36W IC OD DF-WH / Wipro WVP 76236 SGA) | 6 | Each
50 | Supply of 4x28W surface mounting luminaire with reflectors, closed version with all electrical accessories like electronic ballast, lamp holder, 28W T5 lamps etc complete as required. (Wipro WHF 30428 SGW / Philips TPS325 4xTL-5-28W EBP) | 1 | Each
51 | Supply & installation of recess mounted 1x18 watts down light fixture, with aluminium reflector, CRCA sheet housing, fresnel lens, complete with all accessories like ballast, 18W CFL lamp etc complete as required. (Wipro WCP 34118 SG / Philips FBH150 M IxPL-C/4P 18W HFM / GE GECCFL1x18 DN) | 16 | Each
52 | Supply of 1x18W surface mounted luminaire with opal acrylic diffuser complete with all electrical accessories like electronic ballast, lamp holder, 18W T8 lamps etc. complete with all mounting accessories etc as required. (Philips TMS520/ 118 / Wipro WRF 21118 / GE TRI 118) | 5 | Each
53 | Supply of ceiling fan 1200 mm sweep, double ball bearing, approved colour and quality with original down rod,suspension shackle,canopy etc with out regulator complete with all accessories as required. ( Usha Sonata max / Crompton High Breeze) | 5 | Each
54 | Supply and installation of 400 mm sweep, wall fan, swinging type with speed control, necessary adapter, of approved colour, for single phase 230 volt, 50Hz AC supply complete with motor, capacitor all accessories as required complete. (Usha Helix High speed or Equi). | 5 | Each
55 | Supply of heavy duty exhaust fan 300 mm sweep, 900 rpm, metal blades of approved colour, for single phase 230 volt, 50Hz AC supply complete with motor, capacitor and all accessories as required complete. | 2 | Each
56 | Supply of 250mm sweep, 1250 rpm, louvered ventilating fan suitable for single phase 230 volt, 50Hz AC supply complete with motor, capacitor, louvers/shutters and all accessories as required complete. (Make : Usha Crisp Air or equivalent) | 4 | Each
H. UPS and MCBs
57 | Supply, installation, testing & commissioning of 15 kVA, 3 phase, input, 3 phase output, true on-line UPS system with 20 minutes back up (full load), including all accessories, Tubular batteries VRLA type with powder coated MS cabinet, battery cabling including all accessories as required complete having following specification.
Fully digital controlled based on DSP
Power factor corrected from end > 0.9
Pure sine wave output.
Full time output voltage & frequency regulation
Auto regulation of battery end voltage
Intelligent interface with LED/LCD display
Static bypass switch & manual by pass switch
| Auto temperature compensation | 1 | Nos
58 | Supplying and fixing following rating, 415 Volts, "C" series, miniature circuit breaker suitable for power loads of following poles in the existing MCB DB complete with connections, testing and commissioning etc as required.
a | 40A TP MCB | 2 | Each
b | 63A TP MCB | 4 | Each
59 | Supply and fixing FP sheet steel enclosure on surface recess along with 40 amps 415V FP Isolator complete with connections, testing and commissioing etc as required. | 10 | Each
I. Telephone system
60 | Supply, installation, testing & commissioing of Digital EPBAX, PCM/TDM, 100% non-blocking, main box equipped with
4 Analogue Trunk lines
4 Analogue Extensions
8 Digital display interface
Voice guided FAX / DID module
Analog Clip (both on Trunk and Extension)
Flexible numbering Scheme, Call back on busy/ no answer
Call Forward – Internal/ External, Optional ADSL interface
Call pickup: group/selective, CTI protocol via V.24. Conference
DND- Do Not Disturb. Music on hold
| The device shall be expandable up to 10 P&T Lines and 50 extensions. (Similar to Siemes Hipath 1150 Medium). | 1 | Each
61 | Supply and installation of push button telephone (Similar to Siemens Euroset 802 or Equ). | 10 | Each
62 | Supply and installation of push button telephone, speaker with clip telephone (Similar to Siemens Euroset E2025C or Equ). | 1 | Each
63 | Supply and laying 20 pair 0.5 sqmm FR PVC insulated annealed copper conductor, jelly filled armoured telephone cable in surface / through pipe / underground including excavation and re-filling including all accessories as required. | 50 | m
64 | Supply and Installation of 50 pair MDF box, back mount frame and original krone connectors with all accessories. | 1 | Each
65 | Supply and Installation of 20 pair MDF box, back mount frame and original krone connectors with all accessories. | 1 | Each
66 | Supply and Installation of Impulse protection module for protecting trunk lines, digital lines, external extensions, internal extensions & overhead lines with all required accessoires. | 15 | Each
J. Network system & access control
67 | Supply & fixing modular type computer outlet (RJ-45) with modular base and cover plate, GI box complete with all accessories, connection etc. complete as required. | 10 | Each
68 | Supply and laying 4 pair CAT 6 UTP cable in the exisitng surface / recessed steel / PVC conduit as required. | 320 | m
69 | Supply, installation, testing & commissioning of 24 port unmanaged Gigabit 10/100/1000 Mbps Unmanaged Switch, RoHS compliant with all required accessories. | 1 | nos
70 | Supply and installation of 6-24 port fully loaded 110 connect jack panel 1U with cable manager and all required accessories. | 1 | nos
71 | Supply & installation of Cat 6, 4ft, RJ45-RJ45, UTP, Patch cord with all required accessories. | 10 | nos
72 | Supply & installation of Cat 6, 7ft, RJ45-RJ45, UTP, Patch cord with all required accessories. | 10 | nos
73 | Supply and installation of 9 U wall mounted Network Rack made of steel, powder coated, front glass cover with PDU's, cable manager and cooling fans including all required accessories. | 1 | nos
74 | Supply, installation, testing and commissioing of access control system for sterile corridor door and ante room door separately with card controller, door magnetic latch, access card (min 10 nos expandable), cabling between the control and latch including all required accessroies for the propoer operation. | 2 | Job
K. OHP system
75 | Supply, installation, testing & commissioning of LCD Projector with 2100 lumen (lamp mode Standard) with contrast ratio of 3000:1 with a resolution of 1024 X 768, supplied with cordless remote control, VGA cable, ceiling mount kit with all required accessories as required. (Similar to Sony VPL-EX225 or Equ). | 1 | Each
76 | Supply & installtaion of pull down screen, High Gain mat white with size 7 ft X 5 ft with all required accessories as required. (Similar to Liberty Grand view or Equ). | 1 | Each
L. Miscellaneous
77 | Supply and providing 6 mm thick & 1 m wide electrical grade chequered type rubber mat to withstand 3.3 KV dielectric strength conforming to IS 5429/ 1969. | 8 | m
78 | Supply, fabrication and fixing 3 nos MS Fire buckets on suitable fabricated MS angle iron stand with hook, painting with red paint & filled with dry sand as required with all required accessories. | 1 | Set
79 | Supply and providing First Aid Chart duly framed and placed in a conspicuous location for clear vision. | 1 | Each
80 | Supply and providing Electrical main single line Diagram duly framed and placed in a conspicuous location for clear vision. | 1 | Each
GRAND TOTAL - (PART II)