ANNEXURE- I

cold room technical specification

(Amendment No. HLL/MKG/WHO/VACCINE-001 dated 17th June 2014)

| s. no | parameter | value |
| --- | --- | --- |
| 1 | ambient temperature | 40 deg c |
| 2 | designed room temperature | 2 to 8 Deg C |
| 3 | product to be stored | Vaccines for human use |
| 4 | product incoming temperature [°c] | incoming @ 15 deg c |
| 5 | product final temperature required[°c] | final @ 4 deg c |
| 6 | qty of product stored per day/batch [in kgs] | 30,000 vials, each bottle carries 6 ml liquid pentavalent) |
| 7 | pull down time [hrs] | 12 hours |
| 8 | room size | 4 x 3 x2.4 meters (inner size) |
| 9 | material of insulation | puf |
| 10 | thickness of insulation [mm] | 80 mm |
| 11 | wall lamination out/in | 0.5 mm pcgi/ 0.5 mm ss 304 |
| 12 | ceiling [out/in] | 0.5 mm pcgi/ 0.5 mm ss 304 |
| 13 | type of floor insulation | 60 mm thick PUF with 0.5 mm GI+ 6 to 12 mm plywood + 1.2 mm AL Chk plate |
| 14 | thickness of floor insulation [mm] | 60 mm |
| 15 | size of door | 900 x 2000 mm, suitable for 80 mm thick puf insulated wall |
| 16 | type of door | swing panel mounted type, 0.5 mm pcgi/ 0.5 mm ss 304 (same as panel finish) with internal clear plastic strip curtain |
| 17 | type of refrigeration system | split type |
| 18 | type of cooling | dx cooling |
| 19 | capacity of refrigeration system [kw ] | 4 kw |
| 20 | type of refrigerant | r404a |
| 21 | type of compressor | hermetic |
| 22 | type of condenser | air cooled |
| 23 | no of condensing units | 2 no's [1 w+1 s] |
| 24 | moc for condensing units | powder coated gi, cu tubes with al fins |
| 25 | no of evaporator units | 2 no's [1 w+1 s] |
| 26 | electrical panel for ref system | free standing /inbuilt in cond. unit |
| 27 | type of evaporator units | forced air cooled |
| 28 | moc for evaporator units | ss 304 casing, al fins cu tubes |
| 29 | lighting inside the rooms | suitable for 150 lux luminosity |
| 30 | type of light fitting | tungsten filament light(vapour proor) |
| 31 | temperature indicator cum controller | micro-processor based controller |
| 32 | no. of temperature sensor required in the cold room for temp. monitoring & storing through single data logger. | 5 no’s |
| 33 | door opening with access control (swipe cord type) | required |
| 34 | audio & visual alarm hooter in the coldroom when temp. exceeds the maximum limit & sms alert required to the concerned person | required |
| 35 | power supply | 230 v/415 V,50hz,1/3 phase, a.c. supply |
| 36 | data logger for storing temp. reading of five sensor | software with 21 cfr part 11 compliance for temp. storing & monitoring |
| 37 | door open sensor linked with alarm | required |
| 38 | Vendor to consider following for quote | - Power cable, copper tubes (liquid & suction line) with insulation & drain pipe – 6rmt. - Civil wall breaking for connecting copper tube, power cable etc. from IDU to ODU. |

Validation REQUIREMENT:

- DQ/IQ/OQ and PQ documentation.

- Validation PQ should cover temperature mapping and penetration studies.

- 16 temperature probes shall be used for the temperature mapping studies for 48 hours in cold room.

- 4 temperature probes shall be used for Penetration/ Dip test (to find product temperature) studies for 48 hours.

- Data logger and all probes should have calibration certificate with traceability.

Note: If any deviations on above points, vendor to mention it separately.

Annexure V

PRICE SCHEDULE

(Amendment No. HLL/MKG/WHO/VACCINE-001 dated 17th June 2014)

| BILL OF QUANTITY FOR WALK-IN COLD ROOM |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| S.No. | ITEM DESCRIPTION | QTY | UNIT | SUPPLY |  |  |  | INSTALLATION |  |  |  |
|  |  |  |  | RATE |  | AMOUNT |  | RATE |  | AMOUNT |  |
| 1 | SUPPLY, INSTALLATION, COMMISSIONING AND VALIDATION OF COLD ROOM (AS PER ABOVE ATTACHED TECHNICAL SPECIFICATION) | 1 | LOT |  |  |  |  |  |  |  |  |
| 2 | EXTRA COPPER PIPE (SUCTION & LIQUID) WITH INSULATION FOR SUCTION LINE | 1 | RMT |  |  |  |  |  |  |  |  |
| 3 | EXTRA ELECTRICAL CABLE WITH CONDUIT | 1 | RMT |  |  |  |  |  |  |  |  |
| 4 | EXTRA PVC DRAIN PIPE | 1 | RMT |  |  |  |  |  |  |  |  |
| TOTAL BASIC PRICE |  |  |  |  |  |  |  |  |  |  |  |
| EXCISE DUTY |  |  |  |  |  |  |  |  |  |  |  |
| SALES TAX (CST @ 2% / VAT) |  |  |  |  |  |  |  |  |  |  |  |
| SERVICE TAX |  |  |  |  |  |  |  |  |  |  |  |
| TOTAL PRICE |  |  |  |  |  |  |  |  |  |  |  |
| TOTAL (SUPPLY & INSTALLATION) INCLUDING ALL TAXES & DUTIES |  |  |  |  |  |  |  |  |  |  |  |
| Note: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1. The quoted price shall be for supply, installation, commissioning, validation & complete qualification package ( DQ, IQ, OQ & PQ) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. The quoted price shall be inclusive of all applicable duties, taxes, freight charge, packing & insurance. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3. Form 'C' will be provided for CST |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4. Do refer to the technical specification. |  |  |  |  |  |  |  |  |  |  |  |  |  |

NB: Unit price shall be written in figures and words

Total Tender price in Rupees: ________________________________________________________

In words: _______________________________________________________________________________________________

Note: -If there is a discrepancy between the unit price and total price, then the unit price shall prevail.

Name			: _________________________

Business Address 	: _________________________

Place			: _________________________                           		Signature of Tenderer : ________

Date			: _________________________                                      		Seal of the Tenderer   : ________