##### HLL LIFECARE LIMITED

AKKULAM  FACTORY, SREEKARIAM  P.O. THIRUVANANTHAPURAM - 17

Amendment (3rd)  Dtd 26.06.2015 to TENDER NOTICE

Ref: TENDER No. HLL/AFT/TDG/ODSH/EQP/2015-16/02 DATED 25/05/2015

## Following Amendments are made in the Tender for SUPPLY AND INSTALLATION OF DIESEL GENERATORS FOR SNCU IN HOSPITALS IN ODISHA STATE.

DOCUMENTS COMPRISING BID AMENDMENT IN SUPPLY OF 25 KVA & 50 KVA DG SET

| S N | TENDER DETAILS |  |  |
| --- | --- | --- | --- |
| ## TENDER FOR SUPPLY AND INSTALLATION OF 12 NOS DIESEL GENERATORS FOR SNCU HOSPITALS IN ODISHA STATE TENDER No. HLL/AFT/TDG/ODSH/EQP/2015-16/02 DATED 25/05/2015 |  |  |  |
| 1 | Extension of Tender opening date | ORIGINAL TENDER | (a) Last Date and Time for Receipt of Bids is 16/06/2015, AT 11.00 AM ## (b) Date and Time of Opening of Bid is : 16/06/2015, AT 11.AM |
|  |  | AMENDED DATE & TIME | (a) Last Date and Time for Receipt of Bids is 08/07/2015, AT 2.30 PM (b) Date and Time of Opening of Bid is : 08/07/2015, AT 3.PM |
| 2 | SSI Unit Benifits | ORIGINAL TENDER | Not mentioned |
|  |  | ADDITION | Section II, Instruction to Bidders, Clause 7.1.l : SSI Benefits: SSI exceptions shall be considered subject to submission of copies of valid SSI Registration Certificate, which specifies excemption of Tender Fee, EMD etc for specified item as well as the specific capacity of the item in the tender. |
| 4 | Period of Validity of Bids | ORIGINAL TENDER | ITB 13.1 Bids shall be valid for One year from the date of opening of Price Bid |
|  |  | AMENDMENT | ITB 13.1 The Price shall be valid during pendency of the contract i.e. till the period of supply, Erection and Commissioning of DG Sets as per tender terms. |
| 5 | 1. Earthing and earthing strip 2. Length of exhaust piping | ORIGINAL TENDER | Not mentioned |
|  |  | ADDITION | 1. Earthing and earthing strips shall be on HLL/Purchaser;s Scope 2. Tenderer shall quote 5” and 3” diameter exhaust pipe for one meter each. In case any additional quantity required, will be paid extra. |
| 6 | Inspection and Tests | ORIGINAL TENDER | Not mentioned |
|  |  | ADDITION | GCC, Sl No. 6.5 : DG shall be run at NO LOAD for 8 hours, check and confirm that the temperature of Lubricants and Coolants within the limit during Commissioning. After completion of the NO LOAD trial, DG shall be loaded in steps of 25%, 50%, 100% LOAD in a span of 8 hours and also confirm the temperature of engine oil and coolants within the limit and no abnormal vibration, noise and oil leakage. |
|  | SECTION V Technical Specifications | ORIGINAL TENDER | It should be CPCB, Approved Acoustic Enclosure. |
|  |  | AMENDMENT | It should be CPCB-II, Approved Acoustic Enclosure. |
|  | SECTION V Technical Specifications | ORIGINAL TENDER | Meter, MCB with Acoustic Enclosure as per CPCB Norms |
|  |  | DELETION | Deleted |
|  | SECTION V Technical Specifications | ORIGINAL TENDER | Water-Cooled Four Stroke Multi Cylinders |
|  |  | AMENDMENT | Water-Cooled Multi Stroke Multi Cylinders |
|  | SECTION V Technical Specifications: Scope of Wrok | ORIGINAL TENDER | Scope of the work shall include supply, Erection, Testing and Commissioning. |
|  |  | AMENDMENT | Scope of the work shall include Supply, Testing and Commissioning |
|  | SECTION V Technical Specifications Make: | ORIGINAL TENDER | Kirloskar Electric / Ashok Leyland/Cummins/Mahindra/Equivalant |
|  |  | AMENDMENT | Kirloskar Green / Ashok Leyland/Cummins/Mahindra/Equivalant |
|  | SECTION V Technical Specifications: Engine | ORIGINAL TENDER | Engine shall be of Radiator Cooled, Four Stroke, Multi-Cylinder conforming to relevant standards |
|  |  | AMENDMENT | Engine shall be of Radiator Cooled, Multi Stroke, Multi-Cylinder conforming to relevant standards |
|  | SECTION V Technical Specifications: Intallation, Testing & Commissioning | ORIGINAL TENDER | Supply, Installation, Testing & Commissioning of the whole system shall be in the scope of the supplier. |
|  |  | AMENDMENT | Supply, Testing & Commissioning of the whole system shall be in the scope of the supplier. Testing : DG shall be run at NO LOAD for 8 hours, check and confirm that the temperature of Lubricants and Coolants within the limit during Commissioning. After completion of the NO LOAD trial, DG shall be loaded in steps of 25%, 50%, 100% LOAD in a span of 8 hours and also confirm the temperature of engine oil and coolants within the limit and no abnormal vibration, noise and oil leakage. |
|  | SECTION V Technical Specifications Annual Comprehensive Maintenance Contral (ACMC) | ORIGINAL TENDER | Supplier has to provide service support within 8 Hours. |
|  |  | AMENDMENT | Supplier has to provide service support within 8 Hours through the authorized servicing party of the Generator |
|  | SECTION V Technical Specifications Service Part | ORIGINAL TENDER | 100% after Erection, Testing, Commissioning and Handing Over of the complete system at 11 Hospitals in Odisha State against Performance Bank Guarantee valid for a period of ONE year. |
|  |  | AMENDMENT | Testing and Commissioning shall be done by the supplier at free of cost |
|  | SECTION V Technical Specifications Special Conditions (Sl No. 6) | ORIGINAL TENDER | The DG set shall be placed on the foundation by the supplier. Foundation shall also be done by the Supplier |
|  |  | AMENDMENT | The unloading of DG set shall be done by the supplier’s cost. Leading, positioning & installation shall be done by HLL/Purchaser. The supplier may submit drawing for foundation of the DG set. |
|  | SECTION V Technical Specifications Special Conditions (Sl No. 8) | ORIGINAL TENDER | A Competent Technical person from the supplier shall be present at the time of Trial Run and for the successful Commissioning of the DG Set. |
|  |  | AMENDMENT | A Competent Technical person from the supplier shall be present at the time of Testing & Trial Run and for the successful Commissioning of the DG Set |

All other terms and conditions in the tender notice and  tender document remain unchanged.

JOINT GENERAL MANAGER (MATERIALS)