# TENDER NOTICE

SUBJECT : INVITATION TO TENDER FOR ANNUAL MAINTENANCE CONTRACT FOR HVAC SYSTEM  AT KFB – REG.

Sealed  & superscripted tender under Two Bid System  (Technical and Commercial) are invited for operation, Maintenance & Validation  of HVAC and Airhandling System, as per GMP standards in Formulation Plant, Bulk Drug Plant, Inspection Section and Laminar airflow bench in Laboratory  at our factory site at Kanagala for one year.

The last date for submission of duly filled and completed tender documents at our office is on   05th February, 2013 up to 3.00 pm.

The tender documents may be down loaded from our Web Site www.lifecarehll.com

Sr. Manager (Purchase)

## ANNEXURE  – 1

### INSTRUCTIONS TO  BIDDER AND TERMS AND CONDITIONS

1)	This is TWO BID System comprising of:

  - Technical Bid and

  - Commercial Bid

2) Both the bids shall be submitted in Sealed cover separately. Tender Nos. of the Technical and Commercial Bids shall be submitted in two separate sealed covers separately.  Tender Name Technical Bid and Commercial Bids shall be superscripted on the respective covers in order to clearly identify between the two bids.  The two scripts separately marked bids enclosed in a single sealed cover by superscripting on the envelope “QUOTATION FOR AMC OF HVAC SYSTEM” complete in all respects addressed to the Sr. Manager (Purchase) HLL Lifecare Limited, Kanagala – 591 225 Dist. Belgaum should reach us on or before  3.00 pm on or before 05th February, 2013

3) The Technical bid should have the Technical Questionnaire duly filled up and attached with supporting documents.  The Technical Bid only will be opened first and the bidders will be evaluated.  The Commercial Bids of those bidders whose offers are qualified and others will be returned to the rest of the bidders.

THERE IS NO SELPERATE FORMAT FOR COMMERCIAL BID BUT THE AMOUNT QUOTED MUST BE LUMPSUM FOR A YEAR FOR ALL THE ACTIVITIES COVERED IN ANNEXURE.

4) The Tender Document Fee of Rs. 501/- has to be paid along with the  Technical Bid.

5) HLL Lifecare Limited shall not be responsible for postal delay if any, in the delivery of bidding the document or non-receipt of the same.

6) EMD of Rs. 10,000/- (Rupees ten thousand only) should  be remitted by Demand Draft only, drawn in favour of HLL Lifecare  Limited, Payable at State Bank of India, Nipani and shall be enclosed with Technical bid.  Tender without EMD will be  out rightly rejected. However, SSI Units  who wish to avail  exemption from payment of EMD  should produce an exemption certificate  issued  by the concerned DIC or NSIC  stating that the SSI Unit is exempted from payment of  EMD in respect of the relevant tender number indicated in the tender document.

7) In the event of the date mentioned for receipt of Bid being declared  subsequently as holiday for the administrative office, the due date for submission  of bids will be the following working day and time.

8) Bids received after the deadline for the submission will not be considered.

9) Unsealed tenders received are liable to be rejected and it  will be on sole risk of  tenderers.

10) The bidder is expected to examine all specifications, instructions, forms, terms and conditions given in the document.

11) The tender should be complete in all respects and incomplete tenders are liable for rejection.

12) The validity of Technical bid for the vendors who qualify will  be for a  period of two years at the discretion of HLL Lifecare Ltd.,

13) The price bid (Commercial Bid) who qualify in the Technical Bid only be opened.  The date and time of opening of Price Bid will be intimated separately.  The price bids of tenderers who do not qualify will be returned.

14) Parties invited to participate in the tender may collect additional data from Electrical Department/study system on site to quote.

15) The jurisdiction of any dispute, suits and proceedings arising out of this tender  shall be  only  in the courts  of Hukkeri Taluk, Belgaum District.

16) There shall not be any corrections/overwriting on the commercial bid if so the same are to be duly attested.

17) Suppression of facts will disqualify the tender document.

18) HLL reserves the right to qualify or not a tender without assigning any reasons.  The decision of HLL will be final and no correspondence will be entertained in this regard.

19) The last date for receipt of Technical & Prince Bid documents will be up to 3.00 PM on 05th February, 2013 and completed tenders in sealed cover superscripted with tender number along with EMD amount of Rs. 10,000/- (Rupees ten thousand only)  by Demand Draft drawn in favour of HLL Lifecare Limited, Payable at State Bank of India, Nipani 591 237 should reach us latest by 3.00 pm on the above date.  Also enclosed a separate Demand Draft for Rs. 501/-  (Inclusive of S.T) towards the cost of tender documents.

20) The contractor has to pay the wages to their employees as per rules and regulations and the proof shall be submitted if required.

21) Acceptance/rejection of the tender is entirely at the discretion of the HLL.

22) The details of activities to be performed under the said contract scope of job works, frequency of validation, number of systems, location of systems and specification of systems, instructions to the bidders etc., are enclosed in the relevant annexure.

23) Material cost involved to be claimed separately with prior approval and producing bills at DG S &D Rates.

24) The quoted amount should be inclusive of all taxes.

25) Statutory deductions if any like Work Contract Tax., PF, ESI, Income Tax etc., are applicable  as per rules and the  same will be recovered from the payment.

26) The bidder has to enclose a signed photocopy of the  enclosures indicating that they accept the scope of the work and bid for the same.

27) The tenderer should put his signature on all pages of the tender documents along with Annexures.

28) The rates quoted are final.

29) Amount quoted should be lump sum for the services and the manpower deployment, and excluding any consumables, spares and material used. Manpower deployment is partly continuous around the clock, and partly as and when required. Around the clock manpower is required for the operations that are covered under schedules A.1 to A.5, A.11 and A.13 of annexure AN2. Manpower is to be arranged, as and when required for activities covered under schedules A.6 to A.9, A.10 and A.12, and A.14 of annexure AN2. Optimisation of amount of manpower deployed, entirely at the convenience of the bidder, BUT MUST ENSURE THE ACTIVITIES COVERED IN ANNEXURE AN2, TIMELY, IRRESPECTIVE OF MANPOWER PROVIDED BY HIM/THEM.

30) Proportionate deduction would apply to the billed amount for not timely-carrying out any activity, covered in annexure AN2.

31) Material cost involved be claiming separately, with prior approval and producing bills at DG S&D rates or as per the price quoted in the commercial bid.

32) The company reserves the right to reject any or all the tenders either partly or completely without assigning any reason.

33) Payment will be made after satisfactory completion of work on monthly basis.

34) During execution of work, the Contractor or authorized representative should be present at site.

35)  In case of any damages caused to our(HLL Lifecare Ltd.) property by you/your workmen while executing the above job, the company (HLL)  shall recover the cost of such damages from you.

36) In case of any accident to the labours engaged by the party while executing the work party shall responsible for the same and shall pay the compensation as  per   WCA.

37) Insurance for the labours shall be arranged by the party at their own cost as per WCA.

38) All the works to be carried out as per instructions of Engineer-in-charge.

## ANNEXURE  – 2

## Part I - Operation & Maintenance

General activities to be carried out under the Annual Maintenance Contract of operation and maintenance of HVAC and Air Handling Systems

  - Daily operation of all HVAC and AHU plants (As per AN3 Part A to Part E) and system tuning to maintain area parameters as per needs of process and latest GMP and ISO standards.

  - Monitoring and recording of area parameters like temperature, humidity and differential pressure once in shift for all the production area. Necessary corrective actions to be taken if found any abnormality.

Displaying area parameters, clearly and visibly, at the entrance of each area.

  - Monthly checking and recording of airflow through the filters and diffusers. Necessary corrective actions to be taken if found any abnormality.

  - Periodic cleaning of filters for HVAC system as mentioned in A.1 above. Frequency of the filter cleaning will be as given below.

| Sl No | Type of Filter | Cleaning Frequency |
| --- | --- | --- |
| 1 | Pre Filter | Once in a week |
| 2 | Micro Filter | Once in a week |
| 3 | Fresh Air Filter | Once in a Week |
| 4 | Return filter | Once in a Shift |
| 5 | Hepa Filter | Disposal as per mentioned in Quality Manual. (As and when required) |

  - Monthly Preventive maintenance of the system and recording the same as per mentioned in Part – II of this Annexure.

  - Semi-annually Preventive Maintenance of the system and recording the same as per mentioned in Part – III of this Annexure.

  - Periodical inspection of the system integrity and function of all HVAC and AHU plants of all the areas of all the plants mentioned in schedule A.1 of this annexure, execute corrective action and report problem that are not covered under the scope of the AMC. Maintaining emergency preparedness for HVAC failure.

  - Trouble shooting the break downs of the system to the component level of all the HAVC systems mentioned in schedule A.1 of this annexure and rectifying them. Analysis and recording of breakdowns and identifying the root cause and reporting the same to HLL for corrective and preventive action. [Material cost involved to be claimed separately, with prior approval and producing bills at DG S&D rates. The word “component” includes, compressors, evaporators, refrigerant line, expansion valves, blowers, motors, ducts, filters, room doors, measuring devices fixed for on line process value monitoring, electrical control panels, electrical interlocks, safety interlocks, and any fasteners or structures used to hold these components in their secured place (excepting civil structures like building, wall and column)

Providing guarantee for major parts replaced, like compressor, fan and duct work etc.

  - Optimising preventive maintenance and filter cleaning frequency for the systems in consultation with system in-charge in HLL Lifecare Ltd, and record keeping for the same, to achieve “zero” breakdown. This preventive and corrective action is checked and approved by HLL Lifecare Ltd, as the need arise, to which the service provider (bidder) has to adhere.

  - Maintaining log books and record for all activities, attendance etc and getting it certified by authority in charge.

  - For starting and stopping of the system Standard Operating Procedures (SOPs) to be followed. These SOPs will be given by HLL.

  - Deploying sufficient manpower, for all the activities listed in this annexure, of suitable minimum qualification and training, (continuously around the clock-(minimum 2 manpower/shift) and partly as and when required, and including minimum of one supervisor at our site all the 365 days, generally in general shift and be available in shifts if required, who should has a qualification at the minimum of diploma in AC & R engineering, an experience of two years, and accessibility on mobile network) required to ensure the maintenance as per GMP standards and achieving “zero” breakdowns, and to carry out the activities mentioned above.

  - Providing training for the deployed manpower & maintaining training record.

  - Any hand-tools, stationery required to carry out the above-referred work are to be arranged by the contractor.

  - House keeping of AHU & HVAC unit to be maintained.

  - Validation of the complete system mentioned in AN3 as per ISO 14644. Details of the validation is as per mentioned in Part IV. Frequency of the validation should be once in a 6 month.

## Part II - Checklist for Monthly Maintenance

- Disconnect the power supply to the AHU and place “under maintenance” board for the same.

- Clean the AHU with lint free cloth.

- Grease the bearings of the blower and motor if required.

- Check the motor terminals for tightness, rectify if required

- Clean the drain tray of cooling coil.

- Tighten the base bolts of the blower and motor.

- Check the V- belt for tightness, rectify if required..

- Check for gas leakage, if any, rectify the same.

- Check the refrigeration gas into the system and top up if required.

- Reconnect the power supply and take trials to ascertain proper working.

- Run the blower and check for leakages through the doors and duct joints of AHU.

- Check dampers for smooth operation and check their locking arrangements.

- Record all the observation on Preventive Maintenance Check list.

## Part III – Checklist for Semi-annual Maintenance

- Disconnect the power supply by switching off the Switch Fuse Unit (SFU) at panel and put under maintenance board.

- Check the main and control wiring of the panel for loose connections, tighten as required. Clean contacts of starters and selector switch with Corrosion Rust Cleaner (CRC 2-26).

- Open the blower section of AHU and clean the blower fan.

- Clean the cooling coil externally with jet water spray.

- Clean the drain tray of cooling coil.

- Carry out the preventive maintenance checks of Monthly schedule as mentioned above.

- Paint the AHUs rusted parts, if required.

- Check the doors for proper closing / opening rectify if required.

- Record all the observations on the Preventive Maintenance Checklist

## Part IV – Validation of HVAC

General activities to be carried out under the Annual Maintenance Contract for the validation of the HVAC and Air Handling Systems

- Validation of all the HVAC system mentioned in AN3 as per ISO 14644. Validation should include but not limited to following tests mentioned.

  - Filter integrity test for all the filters in the system

  - Measurement of air velocity from each HEPA filter/Diffuser.

  - Calculation of Air changes per hour.

  - Measurement of Temperature, Humidity and Differential Pressure in each area.

  - Particle-count in each area.

  - Manometer calibration, Air flow measurement and filter integrity check (Specific to Laminar airflow bench in laboratory)

Treating any variation in any one of the above parameters as breakdown and carrying out corrective action as required and re-validating the same.

- All the equipments used for the validation should have the proper calibration records and same should be traceable upto National and International standards through an unbroken chain. Copy of the records to be submitted to HLL as a part of the validation documents.

###### ANNEXURE  – 4

FORMAT FOR TECHNICAL BID

| Sl No | Particulars | Response |
| --- | --- | --- |
| 1(a) 1(b) | Have you installed and commissioned at lest 3 clean room systems of GMP-certified, class-100000, of minimum 20 TR each? Enclose the commissioning reports of the same. OR Have you undertaken the contract for Operation and Maintenance of at least 3 clean room systems of GMP-certified, class-100000, of minimum 20 TR each? OR Have you installed, commissioned and undertaken the contract for Operation and Maintenance of any clean room systems of GMP-certified, class-100000, of minimum 20 TR each? Enclose the commissioning reports of the same. Have you undertaken the contract for validation of at least 3 clean room systems of GMP- certified, class-100000, of minimum 20 TR each? |  |
| 2(a) 2(b) | Can you employ sufficient technicians for operation and maintenance in all three shifts? All the manpower should have the relevant qualification and minimum two years of experience in clean room system installation or maintenance. Supporting documents are enclosed |  |
| 3(a) 3(b) | Can you employ supervisor for onsite inspection, documentation in general shift? Supervisor should have the relevant qualification and minimum two years of experience in clean room system installation or maintenance. Supporting documents are enclosed. |  |
| 4 | Can you ensure to attend any sort of breakdown in the HVAC system within 24 hours? Required spares will be kept with the HLL. |  |
| 5 | Have you enclosed the customer feedbacks from at least three clients for the particulars. 1(a) As per GMP requirement satisfaction report. 1(b) As per GMP requirement satisfaction report. |  |
| 6 | In your commercial bid have you quoted for all the activities as per ANNEXURE AN2 - Part 1 (Operation & Maintenance) |  |
| 7 | Name and address of the bidder |  |
| 8 | Authorized signatory’s name, designation and signature for all correspondence |  |

SPECIAL NOTE:

- The quotation should include specific answers strictly with respect to our tender specifications and specification deviation if any, should be highlighted with clarifications. Otherwise, the quotation will not be considered.

- The quotation along with its enclosure should be furnished with original only. Quotation received by FAX will not be considered unless post conformation copy is received within 5 days from the date of tender opening.

- The supplier should furnish the quantitative values with respect to specified values in the Technical specification of the Quote clearly instead of mentioning either “Complied” , “Agreed” or “Confirmed” etc., otherwise, the Tender Quote is liable to be rejected.