## BOQ
SETTING UP OF BURNS UNIT AT TRIVANDRUM MEDICAL COLLEGE.
PART C - HVAC SYSTEM
Item | Description of items | Unit | Qty | Rate Rs (in figures & words) | Amount in Rs
PART I | MACHINERY
1 | Supply, intallation, testing and commissioning (SITC) of 8.5 TR capacity aircooled Outdoor condensing unit with scroll compressor as per specifications complete with suitable capacity drive motor, air cooled condenser with all accessories, hermetically sealed scroll compressor, electronic microprocessor pendant controller with digital display, first charge R 22 refrigerant gas, vibration isolator pads and saftey devices like thermal protector, pressure relief valve, over load relays single phase preventor, high-low pressure cut out, suitable for three phase 440V supply. | Each | 1
2 | Supply, installation, testing and commissioning of suitable hard drawn copper refrigerant piping for 8.5TR machine with 13 mm nitrile rubber insulation interconnecting the condensing unit to evaporating unit for packaged units as per site condition | RM | 31
3 | SITC of DX type double skinned air handling units, ceiling suspended type 8.5 TR, 1300 lps capcity complete with suitable DIDW blower (asper approved make), blower section, static pressure of 50mm of water column, built in pre filter(EU4) & fine filter(EU7) and controls connected to condensing units, insulated SS drain pan, 6 row cooling coil, electric motor, belt drive package with TEFC motor class 'B' insulation, suitable for 3 phase, 415 V, 50Hz supply, suitable AHU panel, ARI certified, belt guards, electrical cabling from nearby isolator, suitable supports for suspending from slab, vibration isolator, etc. conforming to specifications. The air handling unit shall have 1 inlet refrigerant coils and 1 outlet refrigerant coils suitable for 1 numbers of 8.5 TR capacity ODU and shall conform to specifications. | Each | 1
4 | Supply, installation, testing and commissioning of Air Cooled High Wall mounted Split Air Conditioner of following capacity consisting of high wall mounted type room unit (fan coil) with cordless remote control and one number outdoor condensing unit comprising of enegy efficient suitable rotary compressor for operation on single phase, 230 V, 50Hz supply, fixing the outdoor unit on a raised platform as per manufacturers recommendation and fixing of room (fan coil) unit on wall, standard 4 m distance refrigerant copper piping with 13mm nitrile rubber insulation, providing and making interconnection between room & condenser as per site conditions, comprising of 1" dia drain PVC pipe with insulation 4m, canvas connections, full electrical cabling from power plug near indoor unit and to outdoor unit, ODU MS stand, first charge refrigarant gas, suitable stabilizer etc complete as required.
4.1 | 1.5 TR 5 star rated as per BEE | Each | 1
5 | Supply, Laying and Fixing of 4C 4Sq.mm size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Aluminium conductor cable conforming to IS 7098 (Part 1) amended upto date with brass compression glands on surface/ cable tray/ wall / build in trench etc as required from the Indoor to outdoor units of all units for control wiring. | RM | 16
6 | Supply, installation, testing and commissioning PVC drain pipe of 25mm dia ISI marked, connecting the drain lines from the indoor units to floor sump, with 9mm nitrile rubber insulation as per specification | RM | 16
7 | Supply and fixing Heater package with Humidistat and contactor for humidity control | Each | 1
PART II | AIR DISTRIBUTION
8 | Supply, installation, testing and commissioning of factory fabricated rectangular GSS sheet metal ducting for Supply/return/fresh air duct/collar connecting to indoor unit as per ducting specifications and with suitable supports using MS angles, channels, rods, anchor bolts, etc to roof /truss as per IS 655 and as per specifications.
8.1 | 20 G | SQM | 5
8.2 | 22 G | SQM | 16
8.3 | 24 G | SQM | 124
9 | SITC of External thermal insulation on supply air ducts using min 12mm thick nitrile rubber class "O" closed cell type with antimicrobial protection as per specifications | SQM | 124
10 | Supply, installation, testing and commissioning of Acoustic duct lining using 10mm nitrile rubber insulation open cell type inside the ducts, antimicrobial protection at the outlets of all indoor units upto 4m distance from fan outlet as per spec provided. | SQM | 20
11 | Supply, installation and comissioning of underdeck insulation with 20 mm thick closed cell elastomeric Nitrile Rubber density of 40kg/m3 on ceiling with necessary adhesive with fixtures, supports etc. | SQM | 121
12 | Supply, fabrication, installation, testing of flexible connections made out of fire resistant flexible double canvas sleeve. | Set | 1
13 | Supply, installation, testing and comissioning of Powder coated extruded aluminimum Continuous grilles 16mm frame, 15deg deflection for supply / return air 150mm wide as per spec | SQM | 3
14 | SITC of Powder coated extruded aluminimum supply air diffusers 4 way both side coated with collar damper aluminuim extruded black anodized . (300mmX300mm/600mmx600mm) | SQM | 1
15 | SITC of Powder coated extruded aluminium return air diffusers 4 way both side coated without VCD.(300mmX300mm/600mmx600mm) | SQM | 1
16 | SITC of Fire Control Damper made of 16G GSS sheet blade and frame with 165mm casing, heavy duty interlocking blades and fuly enclosed bade linkage mechanism, SS lateral seal blade seals, self lubricating sintered bronze bushes, fire rating as per UL555-1995 tested as per BS-476 part 20 with 18G extended sleeve 450mm and with fusible link, spring mechanism control panel temp sensor, smoke sensor, limit swith with lever for auto shut off in case of fire/smoke as per specifications. | SQM | 1
17 | SITC of multi blade type volume control dampers made of extruded auminium for ducts/ collars to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distributions system in main ducts, return ducts & other area as per specification. | SQM | 1
18 | SITC of Fresh air GI louvers of size 300x300 mm with wire mesh and birds screen for IDUs/AHUs as per specifications. | SQM | 1
19 | Supply installation testing and balancing of continous Perforated Stainless Steel Grilles for supply and return air grilles in accordance with the approved shop drawings size 610 x 610 mm & 450 x 450 mm | SQM | 1
20 | Supply, installation, testing and comissioning of Inline Centrifugal duct fan with dynamically balanced impeller of 500cfm capacity, min 10 mm static , complete with GI box, with single phase direct driven motor with class B, IP44 protection with an internal automatic safety thermal overload protection, dynamically balanced impeller of following capacity, with an operating sound level of less than 55dB at 3 m distance. | Each | 1
TOTAL PART C -HVAC SYSTEM

## Rate Analysis (hidden)
RATE ANALYSIS FOR HVAC EQUIPMENTS
Item No | 8.5 TR ODU
1 | S.No. | DESCRIPTION | AMOUNT
| 1 | Basic Price | 115000
| 2 | Refigerant gas | Included
|  | Discount @5% | 5750
| A | Sub Total | 109250
| 3 | Excise duty @ 12.36% of A | Included
| B | Sub Total | 109250
|  | VAT @ 12.625% of B | Included
| 4 | Testing & Commissioning charges @ 10% of A | 10925
| 5 | Packaging, Forwarding etc. @ 1% of B | 1092.5
| 6 | Insurance, freight etc. @ 3% of B | 3277.5
| C | Sub Total | 124545
| 7 | Overheads & contractors profit @ 15% of C | 18681.75
|  | TOTAL | 143226.75
|  | SAY INR | 143226.75
RATE ANALYSIS FOR CU PIPING
8.5TR
| S.No. | DESCRIPTION | AMOUNT
| 1 | Basic Price(rubber sleeve insulation and electrical wiring interconnecting the condensing unit to evaporating unit included) | 1200
| 2 | Discount nil | 0
| A | Sub Total | 1200
| 3 | Duty included | 0
| B | Sub Total | 1200
| 4 | Testing & Commissioning charges included | 0
| 5 | VAT @ 12.625% | included
| C | Sub Total | 1200
| 6 | Overheads & contractors profit @ 15% | 180
|  | TOTAL | 1380
|  | SAY INR | 1380
3 | RATE ANALYSIS FOR AHU .CAPACITY
8.5TR
| 1 | Basic Price | 168000
| 2 | Hepa filter/Fine filter/Pre filter | Included
|  | Discount @15% | 25200
| A | Sub Total | 142800
| 3 | Excise duty @ 12.36% of A | 17650.08
| B | Sub Total | 160450.08
|  | VAT @ 14% of B | 22463.0112
| 4 | Testing & Commissioning charges @ 10% of A | 16045.008
| 5 | Packaging, Forwarding etc. @ 1% of B | 1604.5008
| 6 | Insurance, freight etc. @ 3% of B | 4813.5024
| C | Sub Total | 182913.0912
| 7 | Overheads & contractors profit @ 15% of C | 27436.9637
|  | TOTAL | 210350.0549
|  | SAY INR | 210350.0549 |  | 3013.92
6 | RATE ANALYSIS FOR DRAIN PIPING
| S.No. | DESCRIPTION | AMOUNT
| 1 | Basic Price | 110
| 2 | Discount nil | 0
| A | Sub Total | 110
| 3 | Duty included | 0
| B | Sub Total | 110
| 4 | Testing & Commissioning charges included | included
| 5 | VAT @ 12.625% | included
| C | Sub Total | 110
| 6 | Overheads & contractors profit @ 15% | 16.5
|  | TOTAL | 126.5
|  | SAY INR | 127
4 | RATE ANALYSIS FOR SPLIT AIR CONDITIONERS 1.5 TR CAPACITY
| S.No. | DESCRIPTION | 1.5 TR
| 1 | Basic Price | 36600
| 2 | Discount | Nil
| A | Sub Total | 36600
| 3 | Excise duty of A | Included
| B | Sub Total | 36600
| 4 | Testing & Commissioning charges@5% of B | Included
| 5 | Packaging, Forwarding etc. @ 1% of B | Included
| 6 | Insurance, freight etc. @ 3% of B | Included
| 7 | Stabilizer | 1600
| C | Sub Total | 38200
| 8 | Overheads & contractors profit @ 15% of C | 5730
|  | TOTAL | 43930
|  | SAY INR | 43930
8 | RATE ANALYSIS FOR GI SHEET with fabrication & erection
8.1 | S.No. | DESCRIPTION | 20 Gauge
| 1 | Basic Price | 750
| 2 | Support/MS Flanges | 75
| A | Sub Total | 825
| 3 | Duty 12.36% of A | 101.97
| B | Sub Total | 926.97
| 4 | VAT @ 14.5% of B | 134.4107
| C | Sub Total | 1061.3807
| 5 | Fabrication & Fixing @ 10% of C | 106.1381
| D | Sub Total | 1167.5187
| 7. | Overheads & contractors @ 15% | 175.1278
|  | TOTAL | 1342.6465
|  | SAY INR | 1343
8.2 | S.No. | DESCRIPTION | 22 Gauge | 24 Gauge
8.3
| 1 | Basic Price | 650 | 550
| 2 | Support/MS Flanges | 75 | 75
| A | Sub Total | 725 | 625
| 3 | Duty 12.36% of A | 89.61 | 77.25
| B | Sub Total | 814.61 | 702.25
| 4 | VAT @ 14.5% of B | 118.1184 | 101.8263
| C | Sub Total | 932.7284 | 804.0762
| 5 | Fabrication & Fixing @ 10% of C | 93.2728 | 80.4076
| D | Sub Total | 1026.0013 | 884.4839
| 7. | Overheads & contractors @ 15% | 153.9002 | 132.6726
|  | TOTAL | 1179.9015 | 1017.1565
|  | SAY INR | 1180 | 1017
9 | RATE ANALYSIS FOR DUCT /ACOUSTIC INSULATION
10
| S.No. | DESCRIPTION | Thermal insulation | Acoustic 10mm
| 1 | Basic Price | 552 | 1180
| 2 | Adhesive prIce | 50 | 50
| A | Sub Total | 602 | 1230
| 3 | Discount @ 30% of A | 60.2 | 369
| B | Sub Total | 541.8 | 861
| 4 | Excise duty 12.36% of B | 66.9665 | 106.4196
| C | Sub Total | 608.7665 | 967.4196
| 5 | VAT @ 12.5% of C | 76.0958 | 120.9274
| D | Sub Total | 684.8623 | 1088.3471
| 6 | Packaging, Forwarding etc. @ 1% of D | 6.8486 | 10.8835
| 7 | Insurance, freight etc. @ 3% of D | 20.5459 | 32.6504
| 8 | Labour Charges for Erection & commissioining @ 5% of D | 34.2431 | 54.4174
| E | Sub Total | 746.4999 | 1186.2983
| 9 | Overheads & contractors profit @ 15% of E | 111.975 | 177.9447
|  | TOTAL | 858.4749 | 1364.243
|  | SAY | 858 | 1364
13 | RATE ANALYSIS GRILLES
| S.No. | DESCRIPTION | 150 mm
Amount (Rs.)
| 1 | Basic Price | 6896
| 2 | Discount Included
| A | Sub Total | 6896
| 3 | Excise duty Included
| 4 | VAT @ 12.5% Included
| B | Sub Total | 6896
| 5 | Packaging, Forwarding etc. @ 1% of B | Included
| 6 | Insurance, freight etc. @ 3% of B | Included
| 7 | Labour Charges for Erection & commissioining @ 5% of B | Included
| C | Sub Total | 6896
| 8 | Overheads & contractors profit @ 10% of C | Included
|  | TOTAL | 6896
|  | SAY | 6896
RATE ANALYSIS DIFFUSER
| S.No. | DESCRIPTION | RAD
| S.No. | DESCRIPTION
Amount (Rs.)
| 1 | Basic Price | 3974
| 2 | Discount @ 10% | 397.4
| A | Sub Total | 3576.6
| 3 | Excise duty 12.36% | 442.0678
| B | Sub Total | 4018.6678
| 4 | VAT @ 12.5% of B | 502.3335
| C | Sub Total | 4521.0012
| 5 | Packaging, Forwarding etc. @ 1% of C | 45.21
| 6 | Insurance, freight etc. @ 3% of C | 135.63
| 7 | Labour Charges for Erection & commissioining @ 5% of C | 226.0501
| D | Sub Total | 4927.8913
| 8 | Overheads & contractors profit @ 15% of D | 739.1837
|  | TOTAL | 5667.075
|  | SAY | 5667
14 | RATE ANALYSIS FOR SA DIFFUSER/RA DIFFUSER
15
| S.No. | DESCRIPTION | SAD | RAD
| 1 | Basic Price | 7938 | 7938
| 2 | Damper prIce | 3974 | 0
| A | Sub Total | 11912 | 7938
| 3 | Discount @ 10% of A | 1191.2 | 793.8
| B | Sub Total | 10720.8 | 7144.2
| 4 | Excise duty 12.36% of B | 1325.0909 | 883.0231
| C | Sub Total | 12045.8909 | 8027.2231
| 5 | VAT @ 12.5% of C | 1505.7364 | 1003.4029
| D | Sub Total | 13551.6272 | 9030.626
| 6 | Packaging, Forwarding etc. @ 1% of D | 135.5163 | 90.3063
| 7 | Insurance, freight etc. @ 3% of D | 406.5488 | 270.9188
| 8 | Labour Charges for Erection & commissioining @ 5% of D | 677.5814 | 451.5313
| E | Sub Total | 14771.2737 | 9843.3824
| 9 | Overheads & contractors profit @ 15% of E | 2215.6911 | 1476.5074
|  | TOTAL | 16986.9647 | 11319.8897
|  | SAY | 16987 | 11320
16 | RATE ANALYSIS FOR FIRE DAMPER
| S.No. | DESCRIPTION | Fire damper with fusible link
| 1 | Basic Price | 9072
| 2 | Fusible link & accessories price | 6810
| A | Sub Total | 15882
| 3 | Discount @ 10% of A | 1588.2
| B | Sub Total | 14293.8
| 4 | Excise duty 12.36% of B | 1766.7137
| C | Sub Total | 16060.5137
| 5 | VAT @ 12.5% of C | 2007.5642
| D | Sub Total | 18068.0779
| 6 | Packaging, Forwarding etc. @ 1% of D | 180.6808
| 7 | Insurance, freight etc. @ 3% of D | 542.0423
| 8 | Labour Charges for Erection & commissioining @ 5% of D | 903.4039
| E | Sub Total | 19694.2049
| 9 | Overheads & contractors profit @ 15% of E | 2954.1307
|  | TOTAL | 22648.3356
|  | SAY | 22648
17 | RATE ANALYSIS FOR VOLUME CONTROL DAMPER/FRESH AIR DAMPER
18 | S.No. | DESCRIPTION | Fresh Air Damper | Volume Damper
| 1 | Basic Price | 886 | 9072
| 2 | Discount @ 10% | 88.6 | 907.2
| A | Sub Total | 797.4 | 8164.8
| 3 | Excise duty 12.36% | 98.5586 | 1009.1693
| B | Sub Total | 895.9586 | 9173.9693
| 4 | VAT @ 12.5% of B | 111.9948 | 1146.7462
| C | Sub Total | 1007.9535 | 10320.7154
| 5 | Packaging, Forwarding etc. @ 1% of C | 10.0795 | 103.2072
| 6 | Insurance, freight etc. @ 3% of C | 30.2386 | 309.6215
| 7 | Labour Charges for Erection & commissioining @ 5% of C | 50.3977 | 516.0358
| D | Sub Total | 1098.6693 | 11249.5798
| 8 | Overheads & contractors profit @ 15% of D | 164.8004 | 1687.437
|  | TOTAL | 1263.4697 | 12937.0168
|  | SAY | 1263 | 12937
20 | CENTRIFUGAL DUCT FAN 500 CFM
| 1 | Basic Price | 10440 |  | 15750
| 2 | Accessories | Included
|  | Discount | Nil
| A | Sub Total | 10440
| 3 | Excise duty @ 12.36% of A | 1290.384
| B | Sub Total | 11730.384
| 4 | VAT @ 12.625% of B | 1480.961
| 5 | Erection charges @ 10% of A | 1173.0384
| 6 | Packaging, Forwarding etc. @ 1% of B | 117.3038
| 7 | Insurance, freight etc. @ 3% of B | 351.9115
| C | Sub Total | 14853.5987
| 8 | Overheads & contractors profit @ 15% of C | 2228.0398
|  | TOTAL | 17081.6386 |  |  | 3013.92
|  | SAY INR | 17081.6386 |  |  | 23.184

## Invt MB Lab (hidden)
AIR CONDITIONING WORKS.
INVENTORY
Item |  | ICU | TOTAL
No. | Description of items
PART A | MACHINERY
1 | Supply, intallation, testing and commissioning (SITC) of 8.5 TR capacity aircooled Outdoor condensing unit with scroll compressor | 1 | 1 | 99 | 0.66 | 1399.32
2 | Supply, installation, testing and commissioning of suitable hard drawn copper refrigerant piping for 8.5TR machine with 13 mm nitrile rubber insulation | 28 | 31 |  | 1300 | 1532.7936 | 12.7733
[5 empty] | 3100.032 | 25.8336 | 3100.032 | 20.6669
3 | SITC of DX type double skinned air handling units, ceiling suspended type 8.5TR, 1700 lps capcity complete with suitable DIDW blower | 1 | 1 | 2798.64 | 18.6576 | 1399.32
4.1 | Split AC 1.5TR | 1 | 1
5 | Supply, Laying and Fixing of 4C 4Sq.mm size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Aluminium conductor cable | 14 | 16
6 | Supply, installation, testing and commissioning PVC drain pipe of 25mm dia | 14 | 16
7 | Heater Package | 1 | 1
PART B | AIR DISTRIBUTION
8 | Supply, installation, testing and commissioning of factory fabricated rectangular GSS sheet metal ducting for Supply/return/fresh air duct/collar
8.1 | 20 G | 4 | 5
8.2 | 22 G | 14 | 16 | 1.2 | 9.6 | 144 | 2016
8.3 | 24 G | 112 | 124 |  | 1.2
9 | SITC of External thermal insulation on supply air ducts | 112 | 124 | 1.8 | 3.6 | 129.6
10 | Supply, installation, testing and commissioning of Acoustic duct lining | 18 | 20
11 | Supply, installation, testing and commissioning of underdeck insulation | 110 | 121 | 100.6155
[6 empty] | 2.2 | 37.4
12 | Supply, fabrication, installation, testing of flexible connections made out of fire resistant flexible double canvas sleeve. | 1 | 1 |  |  |  | 26.4
13 | Supply, installation, testing and comissioning of Powder coated extruded aluminimum Continuous grilles | 2 | 3 | 1.62
14 | SITC of Powder coated extruded aluminimum supply air diffusers 4 way | 1 | 1
15 | SITC of Powder coated extruded aluminium return air diffusers 4 way | 1 | 1
16 | SITC of Fire Control Damper with fusibile link as per specifications. | 1 | 1
17 | SITC of multi blade type volume control dampers | 1 | 1
18 | SITC of Fresh air GI louvers | 1 | 1
19 | SS Grill | 1 | 1
19 | Inline fan | 1 | 1