## Edt 15.01.14
SETTING UP OF BURNS UNIT AT TRIVANDRUM MEDICAL COLLEGE.
Sl No | Description of Items | Unit | Quantity | Rate in Rs | Amount in Rs
A | Wiring
1 | Wiring for light point / fan point / exhaust fan point / call bell point with 1.5 sq.mm FR PVC insulated copper conductor single core cable in surface/recessed PVC conduit with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sqmm, FR PVC insulated copper conductor single core cable etc. as required.
1.1 | Group B | Point | 35
2 | Wiring for circuit/submain wiring along with earth wire with the following sizes of FR PVC insulated copper conductor, single core cable in surface/recessed PVC conduit as required.
2.1 | 2 x 1.5 sqmm + 1.5 sqmm earth wire | Rm | 150
2.2 | 2 x 2.5 sqmm + 2.5 sqmm earth wire | Rm | 680
2.3 | 2 x 4 sq. mm + 1 x 4 sq. mm earth wire | Rm | 150
2.4 | 2 x 6 sq. mm + 1 x 6 sq. mm earth wire | Rm | 100
3 | Telephone wiring in existing conduit : Supplying and drawing following pair 0.5 sq.mm FR PVC insulated copper conductor,unarmored telephone cable in the existing surface/recessed PVC conduit as required
3.1 | 2 Pair | Rm | 100
3.2 | 4 Pair | Rm | 30
4 | Supplying and fixing of following sizes of PVC conduit along with the accessories in surface/ recess including painting in case of surface conduit , or cutting the wall and making good the same in case of recessed conduit as required for wiring.
4.1 | 20mm | Rm | 100
4.2 | 25mm | Rm | 50
5 | Supplying and fixing following modular switch/socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
5.1 | Telephone socket outlet | Each | 5
6 | Supplying and fixing stepped type electronic fan regulator on existing modular plate switch box including connections but excluding modular plate etc.as required. | Each | 5
7 | Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | Each | 20
8 | Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required.
8.1 | 1 or 2 Module (75mmX75mm) | Each | 10
9 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection, painting etc. as required | Each | 50
10 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess including providing and fixing 6 pin 15/16 & 5/6 amps modular socket outlet and 15/16 amps modular switch, connection, painting etc. as required | Each | 20
11 | Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | Each | 15
12 | Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required.
12.1 | Upto 450 mm sweep | Each | 3
13 | Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable etc. as required. | Each | 5
14 | Supplying and fixing extra down rod of 10 cm length G.I. pipe ,15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | Each | 20
15 | Supplying and fixing following way prewired SP&N MCB distribution board of steel sheet for 240 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required. (But without MCB/ RCCB/ Isolator)
15.1 | 12 way, Double door | Each | 2
16 | Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required (But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.)
16.1 | 4 way, Double door | Each | 1
16.2 | 6 way, Double door | Each | 1
17 | Supplying and fixing following way prewired TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required.(But without MCB/ RCCB/ Isolator)
17.1 | 4 way, Double door | Each | 2
17.2 | 6 way, Double door | Each | 1
18 | Supplying and fixing 5 amps to 32 amps rating, 240 volts `B' curve, miniature circuit breaker suitable for lighting and other loads of following poles in the exisiting MCB DB complete with connections,m testing and commissioning etc, as required.
18.1 | Single pole | Each | 60
18.2 | Triple pole | Each | 10
19 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | Each | 20
20 | Supplying and fixing following rating, double pole, 240 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
20.1 | 40 amps | Each | 2
21 | Supplying and fixing following rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
21.1 | 40 amps | Each | 2
22 | Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
22.1 | 40 amps | Each | 5
23 | Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
23.1 | 25 A | Each | 1
23.2 | 40 A | Each | 3
24 | Supplying and fixing DP sheet steel enclosure on surface/ recess along with 25/32amps 240 volts "C" curve DP MCB complete with connections, testing and commissioning etc. as required. | Each | 2
25 | Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | Each | 5
26 | Supplying and fixing TP sheet steel enclosure on surface/ recess along with 16/25/32amps 415 volts "C" curve TP MCB complete with connections, testing and commissioning etc. as required. | Each | 5
27 | Providing and fixing 8 SWG dia G.I. Wire on surface or in recess for loop earthing as required. | Rm | 400
28 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
28.1 | 3.5C x 35 sqmm | Each | 2
28.2 | 4C x 16 sqmm | Each | 8
28.3 | 4C x 10 sqmm | Each | 8
28.4 | 4C x 6 sqmm | Each | 4
29 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size on wall surface as required.
29.1 | Upto 35 sq. mm (clamped with 1mm thick saddle) | Rm | 520
30 | Supply of following size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Aluminium conductor power cable conforming to IS 7098 (Part 1) amended upto date.
30.1 | 3.5C x 35 sqmm | Rm | 200
30.2 | 4C x 16 sqmm | Rm | 180
30.3 | 4C x 10 sqmm | Rm | 140
30.4 | 4C x 6 sqmm | Rm | 50
31 | Supply of 1x28W, indoor surface mountable fluorescent CRCA sheet steel power coated body light fixture, 28W T5 lamp, electronic HPF ballast, lamp holder, prewired complete with all necessary accessories suitable for operation on 230V, 50Hz AC supply as required (Philips TMS122 M 2xTL5-28W EBT / Crompton T5GP28EB / Bajaj BTIR 128) | Each | 10
32 | Supply and installation of recess mounted type 2x36W CFL cleanroom light fitting with option of rear opening / front opening in robust CRCA housing, glass cover with all electrical accessories like electronic ballast, lamp holder, 36W CFL lamps, mounting chain, hook etc complete as required. (Philips FCS650 2xPL-L36W EBP FOP GT / Crompton CRFW12236EB / Bajaj BPRF 236C LHD) | Each | 8
33 | Supply of 1x18W surface mounted luminaire with opal acrylic diffuser complete with all electrical accessories like electronic ballast, lamp holder, 18W T8 lamps etc. complete with all mounting accessories etc as required. (Philips TMS520/ 118 / Crompton T5JB13114EB9) | Each | 5
34 | Supply of 1200 mm sweep min three star rated ceiling fan complete with motor, double ball bearing, blades, canopy, 30 cm down rod and without speed regulator suitable for 230 V 50 HZ, AC supply confirms to IS 374/1979 as required complete. (Make Usha Technix or Crompton High Breeze Plus or equivalent). | Each | 5
35 | Supply of medium duty exhaust fan 300 mm sweep, 900 rpm, metal blades of approved colour, for single phase 230 volt, 50Hz AC supply complete with motor, capacitor and all accessories as required complete. | Each | 3
36 | Supply, installation, testing & commissioning of 4 kVA, 3 phase input, 1 phase output, true on-line UPS system with 30 minutes back up (full load), including all accessories, SMF batteries VRLA type with powder coated MS cabinet, battery cabling including all accessories as required complete having following specification.
Fully digital controlled based on DSP
Power factor corrected from end > 0.9
Pure sine wave output.
Full time output voltage & frequency regulation
Auto regulation of battery end voltage
Intelligent interface with LED/LCD display
Static bypass switch & manual by pass switch
| Auto temperature compensation | Each | 1
37 | Supplying and fixing following rating, 415 volts, C curve MCB in the existing DB, enclosure complete with connections, testing and commissioning etc. as required.
37.1 | 40A TP MCB | Each | 4
37.2 | 63A TP MCB | Each | 1
37.3 | 63A FP MCB | Each | 2
38 | Supply and laying 4 pair CAT 6 UTP cable in the exisitng surface / recessed steel / PVC conduit as required. | Rm | 150
39 | Supply & fixing modular type computer outlet (RJ-45) with modular base and cover plate, GI box complete with all accessories, connection etc. complete as required. | Each | 12
40 | Supply and fixing of 10 pair MDF box, back mount frame and original krone connectors with all accessories. | Each | 1
41 | Supply and providing 6 mm thick & 1 m wide electrical grade chequered type rubber mat to withstand 3.3 KV dielectric strength conforming to IS 5429/ 1969. | Rm | 2
TOTAL PART B-ELECTRICAL WORKS