## Est Edt
CONSTRUCTION OF TWO STOREYED BUILDING FOR MCH BLOCK AT CHC, FORT, THIRUVANANTHAPURAM
PART II - ELECTRICAL WORKS
Sl No | Description of Items | Unit | Quantity | Rate in Rs(Words & Figures) | Amount in Rs
A. Wiring
1 | Wiring for light point / fan point / exhaust fan point / call bell point with 1.5 sq.mm FR PVC insulated copper conductor single core cable in surface/recessed PVC conduit with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sqmm, FR PVC insulated copper conductor single core cable etc. as required.
1.1 | Group C | Point | 265
2 | Wiring for twin control light point with 1.5 sq.mm FR PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FR PVC insulated copper conductor single core cable etc as required. | Point | 4
3 | Wiring for circuit/submain wiring along with earth wire with the following sizes of FR PVC insulated copper conductor, single core cable in surface/recessed PVC conduit as required.
3.1 | 2 X 1.5 sqmm + 1.5 sqmm earth wire | m | 600
3.2 | 2 X 2.5 sqmm + 2.5 sqmm earth wire | m | 3000
3.3 | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | m | 600
4 | Telephone wiring in existing conduit : Supplying and drawing following pair 0.5 sq.mm FR PVC insulated copper conductor,unarmored telephone cable in the existing surface/recessed PVC conduit as required
4.1 | 2 Pair | m | 250
4.2 | 4 Pair | m | 200
5 | Supplying and drawing co-axial TV cable RG-6 grade, 0.7 mm solid copper conductor PE insulated, shielded with fine tinned copper braid and protected with PVC sheath in the existing surface/ recessed steel/ PVC conduit as required. | m | 200
6 | Supplying and fixing of following sizes of PVC conduit along with the accessories in surface/ recess including painting in case of surface conduit , or cutting the wall and making good the same in case of recessed conduit as required for wiring.
6.1 | 20mm | m | 300
6.2 | 25mm | m | 250
6.3 | 32mm | m | 150
7 | Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
7.1 | 150 mm X 150 mm X 60 mm deep | Nos | 6
7.2 | 200 mm X 250 mm X 60 mm deep | Nos | 10
8 | Supplying and fixing following modular switch/socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
8.1 | Telephone socket outlet | Each | 15
8.2 | TV antenna socket outlet | Each | 2
9 | Supplying and fixing stepped type electronic fan regulator on existing modular plate switch box including connections but excluding modular plate etc.as required. | Each | 45
10 | Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | Each | 50
11 | Supply and fixing following size/modules, GI box along with the modular base &cover plate for modular switches in recess etc.as required.
11.1 | 1 or 2 Module (75mm x 75mm) | Each | 20
12 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection, painting etc. as required | Each | 120
13 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess including providing and fixing 3pin 15/16 modular socket outlet and 15/16 amps modular switch, connection, painting etc. as required | Each | 35
14 | Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | Each | 95
15 | Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable etc. as required. | Each | 45
16 | Supplying and fixing extra down rod of 10 cm length G.I. pipe ,15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | Each | 60
17 | Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required.
17.1 | Upto 450 mm sweep | Each | 20
B. | MCBs & DBs
18 | Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required (But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.)
18.1 | 6 way Double door | Each | 2
19 | Supplying and fixing following way prewired TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required.(But without MCB/ RCCB/ Isolator)
19.1 | 4 way, Double door | Each | 4
19.2 | 6 way, Double door | Each | 4
19.3 | 8 way, Double door | Each | 2
20 | Supplying and fixing following way prewired SP&N MCB distribution board of steel sheet for 230 volts on surface/ recess complete with loose wire box, terminal connectors for all incoming and outgoing circuits, duly prewired with suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, powder painted including earthing etc. as required.(But without MCB/ RCCB/ Isolator)
20.1 | 8 way Double door | Each | 4
21 | Supplying and fixing 5 amps to 32 amps rating, 240 volts `C' curve, miniature circuit breaker suitable for lighting and other loads of following poles in the exisiting MCB DB complete with connections,m testing and commissioning etc, as required.
21.1 | Single pole | Each | 100
21.2 | Double pole | Each | 4
21.3 | Triple pole | Each | 8
21.4 | Triple pole and neutral | Each | 8
22 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | Each | 50
23 | Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
23.1 | 40 amps | Each | 7
23.2 | 63 amps | Each | 6
24 | Supplying and fixing following rating, double pole, (single phase and neutral), 230 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
24.1 | 25 amps | Each | 2
24.2 | 40 amps | Each | 2
25 | Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
25.1 | 25 amps | Each | 4
25.2 | 40 amps | Each | 7
25.3 | 63 amps | Each | 4
26 | Supplying and fixing DP sheet steel enclosure on surface/ recess along with 25/32 amps, 240 volts "C" curve DP MCB complete with connections, testing and commissioning etc. as required. | Each | 2
27 | Supplying and fixing TP sheet steel enclosure on surface/ recess along with 16/25/32 amp, 415 volts "C" curve TP MCB complete with connections, testing and commissioning etc. as required. | Each | 12
28 | Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top along with 20 amps `C' series, SP, MCB in sheet steel enclosure on surface or in recess, with chained metal cover for the socket outlet and complete with connections testing and commissioning etc, as required. | Each | 8
29 | Supplying and fixing 20 amps, 415 volts, TPN industrial type, socket outlet, with 4 pole and earth, metal enclosed plug top along with 20 amps `C' series, TP, MCB in sheet steel enclosure on surface or in recess, with chained metal cover for the socket outlet and complete with connections testing and commissioning etc, as required. | Each | 2
C. Earthing
30 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providingmasonry enclosure with cover plate having locking arrangement and watering pipe etc. withcharcoal/ coke and salt as required. | Set | 6
31 | Earthing with GI earth plate 600 mm X 600 mm X 6 mm thick including accessories, andproviding masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | Set | 6
32 | Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including connection/ termination with GI thimble etc. as required. | m | 200
33 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | m | 120
34 | Providing and fixing 25 mm X 5 mm GI strip on surface or in recess for connections etc. as required. | m | 150
35 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | m | 400
D. MV Cable Laying
36 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
36.1 | Above 95 sq. mm and upto 185 sqmm | m | 120
37 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC /Hume / Metal pipe as required.
37.1 | Above 95 sq. mm and upto 185 sqmm | m | 10
38 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
38.1 | Upto 35 sq. mm (clamped with 1mm thick saddle) | m | 490
38.2 | Above 35 sqmm upto 95 sq. mm (clamped with 25x3 mm MS flat clamp) | m | 20
38.3 | Above 95 sqmm upto 185 sq. mm (clamped with 25/40x3 mm MS flat clamp) | m | 20
E. MV Cable End Termination & Hume pipe
39 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
39.1 | 3.5C x 185 sqmm | Each | 2
39.2 | 3.5C x 70 sqmm | Each | 2
39.3 | 3.5C x 35 sqmm | Each | 6
39.4 | 3.5C x 25 sqmm | Each | 4
39.5 | 4C x 16 sqmm | Each | 4
39.6 | 4C x 10 sqmm | Each | 8
39.7 | 4C x 6 sqmm | Each | 12
40 | Providing, laying and fixing following dia RCC pipe NP2 class (light duty) in ground complete with RCC collars, jointing with cement mortar 1:2 (1 cement : 2 fine sand) including trenching (75 cm deep) and refilling etc as required.
40.1 | 300 mm dia | m | 20
F. LT Panels
41 | Supply, Installation, Testing & Commissioning of Main panel, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP42, free standing, floor mounting, dust and vermin proof, powder coated, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system, including internal wiring with suitable size wires, rotary handle, spreaders etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification.
Incomer
200A, TPN, MCCB, thermal magnetic with adjustable OL, SC, setting 415V, 50Hz, complete with handle assembly having door interlock - 1 no.
Busbar
1 Set of 250 Amp TPN busbars of high conductivity electrolytic quality Aluminium alloy.
Instruments
1 No 3 phase Digital Multi function meter to read V, A, F with Acc class 1.
(0-200)A Ammeter Acc. class 1 with 240 deg defl. Scale - 3 nos
1 No 3 phase 4 wire CT operated energy meter, 5-10A, Acc. Class 1.
1 Set of phase indicating lamps, LED type, RYB.
1 Set of 2A 10kA C curve SP control MCB
1 Set of 200/5A, Class 1.0, 10VA, Cast Resin CT for metering.
Outgoing
2 Nos 125A, TPN, MCCB, thermal magnetic with adjustable OL, SC, setting 415V, 50Hz, complete with handle assembly having door interlock.
| 4 Nos. 63A, TPN, C curve, MCB | Job | 1
42 | KSEB Meter Board - Supply, Installation, Testing & Commissioning of Three phase meter box, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP54, wall / floor mounting, dust and vermin proof, powder coated, outdoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system including internal wiring with suitable size wires, rotary handle, spreaders, 3mm thick gland plate, hinged type door with neoprene gasket etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification.
Switchgear & other Accessories
Space provision for accomodating 3 phase CT operated energy meter from KSEB with all connections, glass view panel, control MCB, lockable compartment etc.
3 nos. Suitable ratio CT (as per KSEB) with Acc. Class 0.5, 10VA in locakable compartment.
3 nos 200A cutout fuse unit with fuse and 1 no. Neutral link.
1 no. 200A, FP, AC23A, 415V, 50Hz switch disconnector fuse unit with Din type HRC fuse of suitable rating (as per KSEB) in separate cubical.
1 Set of phase indicating lamps, LED type, RYB.
1 Set of 2A 10kA C curve SP control MCB
1 no of Analogue voltmeter, Acc. Class 1 with selector switch.
| The meter board shall have 250 Amp TPN busbars of high conductivity electrolytic quality Aluminium alloy, earth bus of required size, 4P terminal connectors, control wiring with all reqiuired accessories complete. | Each | 1
43 | Supply, Installation, Testing & Commissioning of Utility panel, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP42, free standing, floor mounting, dust and vermin proof, powder coated, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system, including internal wiring with suitable size wires, rotary handle, spreaders etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification.
Incomer
125A, TPN, MCCB, thermal magnetic with adjustable OL, SC, setting 415V, 50Hz, complete with handle assembly having door interlock - 1 no.
Busbar
1 Set of 150 Amp TPN busbars of high conductivity electrolytic quality Aluminium alloy.
Instruments
1 No 3 phase Digital Multi function meter to read V, A, F with Acc class 1.
1 No 3 phase 4 wire CT operated energy meter, 5-10A, Acc. Class 1.
1 Set of phase indicating lamps, LED type, RYB.
1 Set of 2A 10kA C curve SP control MCB
1 Set of 125/5A, Class 1.0, 10VA, Cast Resin CT for metering.
Outgoing
6 Nos. 32A, TPN, C curve, MCB
| 8 Nos. 25A, TPN, C curve, MCB | Job | 1
G. UPS & MCBs
44 | Supply, installation, testing & commissioning of 10 kVA, 3 phase, input, 1 phase output, true on-line UPS system with 30 minutes back up (full load), including all accessories, SMF batteries VRLA type with powder coated MS cabinet, battery cabling including all accessories as required complete having following specification.
Fully digital controlled based on DSP
Power factor corrected from end > 0.9
Pure sine wave output.
Full time output voltage & frequency regulation
Auto regulation of battery end voltage
Intelligent interface with LED/LCD display
Static bypass switch & manual by pass switch
| Auto temperature compensation | No | 1
45 | Supplying and fixing following rating, 415 volts, C curve MCB in the existing DB, enclosure complete with connections, testing and commissioning etc. as required.
45.1 | 40A TPN MCB | Nos | 4
45.2 | 63A TPN MCB | Nos | 4
45.3 | 63A DP MCB | Nos | 1
H Cables
46 | Supply of following size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Aluminium conductor power cable conforming to IS 7098 (Part 1) amended upto date.
46.1 | 3.5C x 185 sqmm | m | 150
46.2 | 3.5C x 70 sqmm | m | 20
46.3 | 3.5C x 35 sqmm | m | 70
46.4 | 3.5C x 25 sqmm | m | 100
46.5 | 4C x 16 sqmm | m | 80
46.6 | 4C x 10 sqmm | m | 110
46.7 | 4C x 6 sqmm | m | 210
I. Light fittings & Fan
48 | Supply of 1x28W, indoor surface mounted fluorescent CRCA sheet steel power coated body light fixture, 28W T5 lamp, electronic HPF ballast, lamp holder, prewired complete with all necessary accessories suitable for operation on 230V, 50Hz AC supply as required (Bajaj BTER 128 / Crompton T5JB1328REB9 / Havells LHIT 12128032) | nos | 80
49 | Supply and installation of 2x28W, indoor recess mounted T5 luminaire with powder coated CRCA sheet steel housing with low depth darklite mirror louver, 28W T5 lamp, electronic HPF ballast, prewired complete with all necessary accessories suitable for operation on 230V, 50Hz AC supply as required (Bajaj BTMRA 228 V2 / Crompton T5CQ11228EB / Havells LHCDT 1228433) | nos | 30
50 | Supply and installation of 12W, indoor recess mounted LED downlighter with housing, diffuser, electronic driver, lamp, prewired complete with all necessary accessories suitable for operation on 230V, 50Hz AC supply as required (Bajaj BZSLO 12W WH / Crompton LCDV-12-CDL / Havells LHEBJNP5PZ1W015) | nos | 35
51 | Supply & installation of 2x36W recess mounted front openable clean room luminaire light fixtures complete with electronic ballast, lamp, prewired complete with all necessary accessories suitable for operation on 240V single phase 50 Hz AC supply as required. ( Bajaj BPRF 236 C LHD / Crompton CRFW12236EB / Havells LHHC02236127) | nos | 10
52 | Supply & installation of 2x36W, recess mounted fluorescent light fixture with CRCA housing, micro optics, 36 W lamps, prewired complete with all necessary accessories like chain hook etc for installation suitable for operation on 230V, 50Hz AC supply as required.( wipro WVP 24236 SGA 2 x 36 W CFL (TC-L) or equivalent. | nos | 50
53 | Supply of 1x14W, indoor surface mounted fluorescent CRCA sheet steel power coated body light fixture, 14W T5 lamp, electronic HPF ballast, lamp holder, prewired complete with all necessary accessories suitable for operation on 230V, 50Hz AC supply as required (Bajaj BTER 114 / Crompton T5JB 13114EB / Havells LHFYBYF10A1W014) | nos | 12
54 | Supply of 1x9W bulk head luminaire with anodised aluminum body, epoxy white powder coated, heat resistant prisamatic glass cover, lamp etc complete with all accessories as required. (Bajaj BJBE 19 / Crompton ICBH10 / Havells LHLK01160099). | nos | 5
55 | Supply of 1200 mm sweep min three star rated ceiling fan complete with motor, double ball bearing, blades, canopy, 30 cm down rod and without speed regulator suitable for 230 V 50 HZ, AC supply confirms to IS 374/1979 as required complete. (Make Usha Technix or Crompton High Breeze Plus). | nos | 45
56 | Supply of 300mm sweep, metal blades with safety guard suitable for single phase 230 volt, 50Hz AC supply complete with motor, capacitor and all accessories as required complete. (Make : Usha Turbo or Crompton Transair or equivalent) | nos | 2
57 | Supply of 250mm sweep, plastic body with safety shutter suitable for single phase 230 volt, 50Hz AC supply complete with motor, capacitor and all accessories as required complete. (Make : Usha Crisp Air or Crompton Brisk air) | nos | 20
58 | Supply of 400mm sweep, powder coated guard suitable for single phase 230 volt, 50Hz AC supply complete with motor, capacitor and all accessories as required complete. (Make : Usha Striker Hi-speed or equivalent) | nos | 4
J. Telephone & Network system
59 | Supply, installation, testing & commissioning of 8 port Gigabit 10/100/1000 Mbps Unmanaged Switch, RoHS compliant with all required accessories. | nos | 1
60 | Supply & drawing Cat 6E cable in the existing surface / recessed steel / PVC conduit including connection to outlet as required. | m | 250
61 | Supplying and fixing Network modular type socket outlet (RJ-45) in 1/2 module GI modular box with modular plate including connections etc. as required. | Nos | 6
62 | Supply and laying of 10 pair 0.5 sqmm FR PVC insulated annealed copper conductor, un armoured telephone cable in surface / recess including all accessories as required. | m | 100
63 | Supplying and fixing following Telephone krone module in box made of plastic including hinged door, krone module with connection etc. as required.
63.1 | 10 pair krone module | Nos | 2
63.2 | 20 pair krone module | Nos | 1
F. Others
64 | Supply & laying ISI marked 2m x 1m x 6mm for 415V electrical grade chequered type rubber mat. | Nos | 15
65 | Supply and fixing anodised aluminum glass framed shock treatment chart. | Each | 2
TOTAL (PART II)