## Abstract
NAME OF WORK : Construction of Two Storeyed Building for MCH Block at CHC, Fort, Thiruvananthapuram
Item No | Description of Item | Quantity | Unit | Rate | Amount
PART - A- CIVIL WORKS
SUB HEAD : - I EARTH WORK EXCAVATION
1 | Earth work in excavation by mechanical means (Hydraulic excavator)/ manual means over areas (exceeding 30cm in depth. 1.5 m in width as well as 10 sqm on plan) including disposal of excavated earth,with all leads and lifts, disposed earth to be levelled and neatly dressed. | 889 | cum
2 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering etc complete, with all leads and lifts as directed by the Engineer in charge. | 852 | cum
3 | Earth filling with contractors own earth (excluding rock) in trenches, plinth sides of foundations etc in layers not exceeding 20 cm in depth, consolidating each deposited layer by ramming and watering etc complete with all leads and lifts as directed by the Engineer in Charge | 195 | cum
4 | Providing anti-termite treatment and creating a chemical barrier to the building by injecting chemical emulsion of required concentrations under raft slab and beam and alround the footings. Column pits, trenches, pits, tunnels, wall trenches, back fill, plinth filling junction of wall and floor, side walls of basement floor external perimeter of building, surrounding of pipes, expansion joints, etc., as per IS specification and as per instructions of chemical manufacturer and also as directed. The treatment shall be carried out strictly in accordance with IS 6313 - Part II - Latest issue etc. complete. The work shall include the cost of all materials, cost of labour, cost of equipment and machinery, hire charges of equipments & machinery, lead & lift, loading and unloading, transportation and all other incidental charges etc., complete. The work shall be carried out as per the directions of the Engineer-in-Charge of the work.
| Note:Plinth area of the building at Ground floor will be measured and paid for. | 606 | sqm
SUB HEAD - II:- PLAIN CEMENT CONCRETE
5 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:4:8 (1 Cement : 4 coarse sand : 8 graded stone aggregate 40 mm nominal size) | 78 | cum
6 | Providing and laying damp-proof course 40 mm thick with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 12.5 mm nominal size).and Applying a coat of residual petroleum bitumen of grade of VG-10 of approved quality using 1.7 kg per square metre on damp proof course after cleaning the surface with brushes and finally with a piece of cloth lightly soaked in kerosene oil. | 45 | sqm
7 | Making plinth protection 50 mm thick of cement concrete 1:3:6 (1 cement: 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) over 75mm thick bed of dry brick ballast 40 mm nominal size, well rammed and consolidated and grouted with fine sand, including finishing the top smooth. | 160 | sqm
SUB HEAD- III: REINFORCED CEMENT CONCRETE.
8 | Providing and laying in position machine batched and machine mixed design mix M-25 grade cement concrete for reinforced cement concrete work, using cement content as per approved design mix, including pumping of concrete to site of laying but excluding the cost of centering, shuttering, finishing & reinforcement, including admixtures in recommended proportions as per IS: 9103 to accelerate, retard setting of concrete, improve workability without impairing strength and durability as per direction of Engineer-in-charge. All works upto plinth level | 159 | cum
9 | Providing and laying in position machine batched and machine mixed design mix M-25 grade cement concrete for reinforced cement concrete work, using cement content as per approved design mix, including pumping of concrete to site of laying but excluding the cost of centering, shuttering, finishing and reinforcement, including admixtures in recommended proportions as per IS: 9103 to accelerate, retard setting of concrete, improve workability without impairing strength and durability as per direction of Engineer-in-charge. All works above plinth level upto floor V level. | 388 | cum
10 | Providing and laying cement concrete in retaining walls, return walls, walls (any thickness) including attached pilasters, columns, piers, abutments, pillars, posts, struts, buttresses, string or lacing courses, parapets, coping, bed blocks, anchor blocks, plain window sills, fillets, sunken floor,etc., up to floor five level, excluding the cost of centering, shuttering and finishing : 1:3:6 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) | 2 | cum
11 | Add for using extra cement in the items of design mix over and abovethe specified cement content therein. | 383 | qntl
12 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete above plinth level. Thermo Mechanically Treated bars. | 46800 | kg
13 | Centering and shuttering including strutting, propping etc. and removalof form for :
a | Foundations, footings, bases of columns, etc. for massconcrete | 602 | sqm
b | Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc. | 254 | sqm
c | Suspended floors, roofs, landings, balconies and accessplatform. | 2515 | sqm
d | Lintels, beams, plinth beams, girders, bressumers and cantilevers. | 491.862 | sqm
e | Columns, Pillars, Piers, Abutments, Posts and Struts. | 684.18 | sqm
f | Stairs, (excluding landings) except spiral-staircases. | 75.2 | sqm
g | Weather shade, Chajjas, corbels etc., including edges. | 208 | sqm
SUB HEAD IV : BRICK WORK.
14 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 50 in foundation and plinth in: Cement mortar 1:6 (1 cement : 6 coarse sand) | 5.5 | cum
15 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 50 in superstructure above plinth level up to floor V level in all shapes and sizes: In cement mortar 1 : 6 (1 cement : 6 coarse sand). | 260 | cum
16 | Half brick masonry with common burnt clay F.P.S. (non modular) bricks of class designation 50 in superstructure above plinth level up to floor V level. Cement mortar 1:4 (1 cement :4 coarse sand) | 1483 | sqm
17 | Extra for providing and placing in position 2 Nos 6mm dia. M.S. bars at every third course of half brick masonry. | 1483 | sqm
SUB HEAD V : GRANITE WORK
18 | Providing and fixing 18 mm thick gang saw cut, mirror polished, premoulded and prepolished, machine cut for kitchen platforms, vanity counters, window sills, facias and similar locations of required size, approved shade, colour and texture laid over 20 mm thick base cement mortar 1:4 (1 cement : 4 coarse sand), joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels. Granite of any colour and shade Area of slab over 0.50 sqm | 76 | sqm
19 | Providing edge moulding to 18 mm thick marble stone counters, Vanities etc., including machine polishing to edge to give high gloss finish etc. complete as per design approved by Engineer-in-Charge. Granite work | 193 | m
20 | Extra for pre finished nosing to treads of steps of granite stone. | 96 | m
21 | Extra for Granite stone flooring in treads of steps and risers using single length up to 2.00 metre | 33 | Sqm
SUB HEAD VI: ALUMINIUM WORK.
22 | Providing and fixing aluminium work for doors, windows, ventilators and partitions withextruded built up standard tubular sections/ appropriate Z sections and other sections ofapproved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) : | 2959.462 | kg
a) For fixed portion . Powder coated aluminium (minimum thickness of powder coating 50 micron) of required colour as directed by the engineer in charge.
23 | For shutters of doors, windows & ventilators including providing and fixing hinges/ pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately) Powder coated aluminium ( minimum thickness of powder coating 50 micron) of required colour as directed by the engineer in charge. | 1678.14 | kg
24 | Providing and fixing 12 mm thick prelaminated particle board flat pressed three layer or graded wood particle board conforming to IS: 12823 Grade l Type ll, in panelling fixed in aluminum doors, windows shutters and partition frames with C.P. brass / stainless steel screws etc. complete as per architectural drawings and directions of engineer-in-charge. Pre-laminated particle board with decorative lamination on both sides | 98.46 | sqm
25 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge. ( Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.50 mm thickness | 195.33 | sqm
26 | Providing and fixing 3M farasa froasted/mat film of thickness 25 microns self adhesive of approved colour, shade and quality with cutting as per approved design and pattern including cleaning of glass and making surface smooth for fixing of film all completeas per direction of Engineer in charge 3m milky milky product coed sh2mamm to glazed window/doors | 195.33 | Sqm
27 | Providing and fixing double action hydraulic floor spring of approved brand and manufacture IS : 6315 marked, DORMA make or equivalent for doors including cost of cutting floors as required, embedding in floors and cover plates with brass pivot and single piece M.S. sheet outer box with slide plate etc. complete as per the direction of Engineer-in-charge With Stainless Steel cover plate | 32 | each
28 | Providing and fixing aluminium handles ISI marked anodised ( anodic coating not less than grade AC 10 as per IS: 1868) transparent or dyed to required colour or shade with nuts and screws etc. complete-
| 125 mm | 16 | each
| 100mm | 60 | each
29 | Providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS: 1868) transparent or dyed to required colour or shade with nuts and screws etc. complete-
| 250 X 10 mm | 60 | each
| 150x10mm | 60 | each
30 | Providing and fixing IS : 3564 marked aluminium extruded section body tubular type universal hydraulic door closer with double speed adjustment with necessary accessories and screws etc. complete. | 60 | each
31 | Providing and fixing 100mm brass locks (best make of approved quality) for aluminium doors including necessary cutting and making good etc. complete. | 60 | each
32 | Providing fixing aluminium casement windows fastener of required length for aluminium windows with necessary screws etc. complete. Powder coated minimum thickness 50 micron aluminium. | 60 | each
33 | Providing and fixing stainless steel (SS 304 grade) adjustable friction windows stays of approved quality with necessary stainless steel screws etc. to the side hung windows as per direction of Engineer- in-charge complete. 255 X 19 mm | 60 | each
34 | Providing and fixing aluminium hanging floor door stopper, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) Transparent or dyed to required colour and shade, with necessary screws etc. complete. Twin rubber stopper | 60 | each
SUB HEAD VII: WOOD WORK
35 | Providing wood work in frames of doors, windows, clerestory windowsand other frames, wrought framed and fixed in position with hold fastlugs or with dash fasteners of required dia & length ( hold fast lugs ordash fastener shall be paid for separately).-Second class Teak wood. | 0.0742 | cum
36 | Providing 40x5mm flat iron hold fast 40cm long including fixing to frame with 10mm diameter bolts,nuts and wooden plugs and embedding in cement concrete block 30x10x15cm 1:3:6 mix (1 cement : 3 coarse sand : 6 graded stone aggregate 20mm nominal size | 8 | each
37 | Providing and fixing panelled or panelled and glazed shutters for doors, windows and clerestory windows, including ISI marked M.S. pressed butt hinges bright finished of required size with necessary screws, excluding panelling which will be paid for separately, all complete as per direction of Engineer-in-charge. Second class teak wood 35 mm thick shutters | 3.6103 | sqm
38 | Providing and fixing panelling or panelling and glazing in panelled or panelled and glazed shutters for doors, windows and clerestory windows (Area of opening for panel inserts excluding portion inside grooves or rebates to be measured). Panelling for panelled or panelled and glazed shutters 25 mm to 40 mm thick : Second class teak wood | 3.6103 | sqm
SUB HEAD VIII: STEEL WORK
39 | Providing and fixing M.S. grills of required pattern in frames of windows etc. with M.S. flats, square or round bars etc. including priming coat with approved steel primer all complete. Fixed to openings/ wooden frames with rawl plugs screws etc. | 1881 | Kg
40 | Steel work in built up tubular (round, square or rectangular hollow tubes etc.) trusses etc., including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer, including welding and bolted with special shaped washers etc. complete. Hot finished welded type tubes. | 2840 | kg
41 | Providing and fixing stainless steel (Grade 304) railling made of hollow tubes, channels, plates etc. including welding, grinding, buffing, polishing and making curvature (wherever required) and fitting the same with necessary stainless steel nuts and bolt complete i/c fixing the railling with necessary accessories & Stainless steel dash fasteners, stainless steel bolts etc., of required size, on the top of the floor or the side of waist slab with suitable arrangemant as per approval of Engineering-in-charge .( for payment purpose only weight of stainless steel members shall be considered excluding fixing accessories such as nuts, bolts, fasteners etc. ) | 175 | kg
42 | Providing and fixing M.S. fan clamp type I of 16 mm dia M.S. bar bent to shape with hooked ends in R.C.C. slabs during laying including painting the exposed portion of loop, all as per standard design complete. | 100 | each
SUB HEAD IX: FLOORING
43 | Providing and fixing Ist quality ceramic glazed wall tiles (Size 300 x400) conforming to IS:15622of thickness 5 mm or nearest size of approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge in skirting, risers of steps and dados over 12mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm including pointing in white cement mixed with pigment of matching shade complete. as approved by Engineer in charge ( Basic Price of Tile not less than Rs.400 per Sqm) | 1271 | sqm
44 | Providing and laying Ceramic joint free antiskid floor tiles of size 400x400 mm ,thicknes 7.5mm or nearest size of 1st quality conforming to IS : 15622, of approved make, in all colours, shades, except White, Ivory, Grey, Fume Red Brown, laid on 20 mm thick bed of cement mortar 1:4 (1 Cement : 4 Coarse sand), including pointing the joints with white Cement and matching pigments etc.complete.as approved by Engineer in charge (Basic price of Tile not less than Rs.370per sqm). | 56 | sqm
45 | Providing and fixing 1st quality germ free & joint free wall tiles( Size 600x300mm) of thickness 10 mm or nearest size of approved make in all colours, shades except begundy, bottle green, black or any size as approved by Engineer - in - Charge in skirting, risers of steps and dados over 12 mm thick bed of Cement Mortar 1: 3 ( 1 Cement : 3 Coarse sand ) and jointing with grey cement slurry @ 3.3 kg per sqm including pointing in white cement mixed with pigment of matching shade complete.as approved by Engineer in charge. (Basic Price of Tile not less than Rs. 839 per sqm.) | 521 | sqm |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
46 | Providing and laying vitrified floor tiles of (Size of Tile 600x600 mm) of 10mm thickness or nearest size with water absorption less than 0.08% and conforming to IS : 15622, of approved make, in all colours and shades, laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand), including grouting the joints with white cement and matching pigments etc., complete.as approved by Engineer in charge. (Basic price of Tile not less than Rs. 865 per sqm) | 725 | sqm
47 | Providing and fixing homogeneous antistatic Polyvinyl chloride sheet roll from fused jointed in flooring and skirting in approved pattern on a smooth and damp proof base using rubber based adhesives of approved quality and manufacturer like Dunlop S-758, Fevicol SR 998, Pidilite or equivalent as per IS 3462,BS 2050 & BS 3261 including rolling with light wooden roller weighing about 5 kg and having surface resistance in the range of 4x104Ω- 5x108 Ω all complete as directed by Engineer-in-charge, in approved colour and shade.- Pidilite Roffler anstistatic SL or equivalent. .2 mm Thick sheet | 285.924 | sqm
48 | Chequerred precast cement concrete tiles, 22 mm thick in footpath & courtyard, jointed with neat cement slurry mixed with pigment to match the shade of tiles, including rubbing and cleaning etc. complete, on 20 mm thick bed of cement mortar 1:4 (1 cement: 4 coarse sand). Light shade pigment using white cement. ( Basic price.of Tile not less than Rs. 470 per sqm) | 51 | sqm
49 | Providing and laying 60mm thick factory made cement concrete interlocking paver block of M -30 grade made by block making machine with strong vibratory compaction, of approved size, design & shape, laid in required colour and pattern over and including 50mm thick compacted bed of coarse sand, filling the joints with fine sand etc. all complete as per the direction of Engineer-in-charge. (Basic price of Block not less than Rs.325 per sqm.) | 50 | sqm
SUB HEAD X : ROOFING
50 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion, (i) Single socketed pipes. 110 mm diameter | 338 | m
51 | Providing and fixing unplasticised -PVC pipe clips of approved design to unplasticised - PVC rain water pipes by means of 50x50x50 mm hard wood plugs, screwed with M.S. screws of required length including cutting brick work and fixing in cement mortar 1:4 (1 cement : 4 coarse sand) and making good the wall etc. complete - 110 mm | 200 | each
52 | Providing and fixing to the inlet mouth of rain water pipe cast iron grating 15cm diameter and weighing not less than 440 grams. | 40 | each
53 | Providing and fixing on wall face unplasticised-PVC moulded fittings/ accessories for unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion. bend 87.5 degree
a | 110 mm bend. | 100 | each
Shoe( plain)
b | 110 mm shoe | 50 | each
54 | Providing and fixing semicircular 110mm PVC pipe for gutter with iron brackets 40 x 3 mm size, bolts , nuts and washers including making necessary connections with rain water pipes complete. | 500 | m
55 | Providing and fixing tiled false ceiling of approved materials of size 595x595 mm in true horizontal level suspended on inter locking metal grid of hot dipped galvanized steel sections ( galvanized @ 120 gsm/sqm, both side inclusive) consisting of main "T" runner with suitably spaced joints to get required length and of size 24x38mm made from 0.30mm thick (minimum) sheet, spaced at 1200mm center to center and cross "T" of size 24x25mm made of 0.30mm thick (minimum) sheet, 1200mm long spaced between main "T" at 600mm center to center to form a grid of 1200x600 mm and secondary cross "T" of length 600mm and size 24x25mm made of 0.30 mm thick (minimum) sheet to be interlocked at middle of the 1200x600mm panel to form grids of 600x600mm and wall angle of size 24x24x0.3 mm and laying false ceiling tiles of approved texture in the grid including, wherever, required, cutting/making, opening for services like diffusers, grills, light fittings, fixtures, smoke detectors etc. Main "T" runners to be suspended from ceiling using GI slotted cleats of size 27 x 37 x 25 x1.6 x mm fixed to ceiling with
12.5 mm dia and 50 mm long dash fasteners, 4mm GI adjustable rods with galvanised butterfly level clips of size 85 x 30 x 0.8 mm spaced at 1200mm center to center along main T, bottom exposed width of 24 mm of all T-sections shall be pre-painted with polyester paint, all complete at all heights as per specifications drawings and as directed by Engineer-in-charge.
| GI Metal Ceiling Lay in plain Tegular edge Global white color tiles of size 595x595 mm, and 0.5mm thick with 8mm drop; made of G I sheet having galvanizing of 100 gms/sqm(both sides inclusive) and electro statically polyester powder coated of thickness 60 microns (minimum), including factory painted after bending. | 576.5054 | sqm
56 | Providing & fixing on roof pressed clay tile (Mangalore tile) of 20 mm nominal thickness and of approved size and as per approved pattern on steel frame work complete (steel frame work to be paid separately). | 118 | sqm
SUB HEAD XI: FINISHING
57 | 6 mm cement plaster of mix:1:3 (1 cement:3 fine sand) | 915 | sqm
58 | 15mm cement plaster on rough side of single or half brick wall of mix 1:6 (1 cement : 6 coarse sand) | 811 | sqm
59 | 12 mm cement plaster of mix : 1:6 (1 cement: 6 coarse sand) | 187.936 | sqm
60 | 18 mm cement plaster in two coats under layer 12 mm thick cement plaster 1:5 (1 cement : 5 coarse sand) finished with a top layer 6 mm thick cement plaster 1:6 (1 cement : 6 fine sand). | 1285.63 | sqm
61 | Finishing walls with Acrylic smooth exterior paint of required shade:- New work (Two or more coats applied @ 1.67 ltr/10 sqm over and including base coat of water proofing cement paint applied @ 2.2 kg/10sqm.) | 1286 | sqm
62 | Wall painting with Plastic emulsion paint of approved brand and manufacture to give an even shade –Two or more coats on new work. | 1915 | sqm
63 | Applying one coat of cement primer of approved brand and manufacture on wall surface – Cement Primer | 1915 | sqm
64 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade : Two or more coats on new work | 95 | sqm
65 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. | 1915 | sqm
66 | Melamine polishing on wood work (Two or more coat). | 80.64 | sqm
SUB HEAD XII: WATER PROOFING
67 | Providing and laying water proofing treatment to vertical and horizontal surfaces of depressed portions of W.C., kitchen and the like consisting of :
Ist course of applying cement slurry @ 4.4 kg.sqm mixed with water proofing compound conforming to IS 2645 in recommended proportions including rounding off junction of vertical and horizontal surface.
IInd course of 20mm cement plaster 1:3 (1 cement : 3 coarse sand) mixed with water proofing compound in recommended proportion including rounding off junction of vertical and horizontal surface.
IIIrd course of applying blown or residual bitumen aplied hot at 1.7kg per sq.mm of area.
| IVth course of 400 micron thick PVC sheet, (Overlaps at joints of PVC sheet should be 100mm wide and pasted to each other with bitumen @ 1.7 Kg/sq.m) | 75 | sqm
68 | Providing and laying intergral cement based water proofing treatment including preparation of surface as required for treatment of roofs, balconies, terraces etc consisting of following operations.
Applying a slurry coat of neat cement using 2.75 kg/sqm. of cement admixed with water proofing compound confrming to IS 2645 and approved by Engineer-in-charge over the RCC slab including adjoiing walls upto 300mm height including cleaning the surface before treatement.
Laying brick bats with mortar using broken bricks / brick bats 25mm to 115mm size with 50% of cement mortar 1:5 (1 cement mortar 1:5 (1 cement : 5 coarse sand) admixed with water proofing compound conforming to IS : 2645 and approved by Engineer –in-charge over 20mm thick layer of cement mortar of mix 1:5 (1 cement : 5 coarse sand) admixed with proprietary water proofing compound conforming to IS : 2645 and approved by Engineer-in-charge to require slope and treating similarly the adjoining walls upto 300mm height including rounding of junctions of walls and slabs.
After two days of proper curing applying a second coat of cement slurry using 2.5kg/sqm of cement admixed with water proofing compound conforming to IS : 2645 and approved by Engineer-in-charge
Finishing the surface wiht 20mm thick jointless cement mortar of mix 1:4 (1 cement : 4 coarse sand) admixed with water proofing compound conforming to IS 2645 and approved by Engineer-in-charge including laying glass fibre cloth of approved quality in top layer of plaster and finally finishing the surface with trowel with neat cement slurry and making of 300 x 300 mm square 3mm deep.
The whole terrace so finished shall be flooded with water for a minimum period of two weeks for curing and for final test. All above operations to be done in order and as directed and specified by the Engineer-in-charge.
| With average thickness of 120mm and minimum thickness at khurra as 65mm | 560 | sqm
69 | 40 mm thick marble chips flooring, rubbed and polished to granolithic finish, under layer 31mm thick cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 12.5mm nominal size) and top layer 9mm thick with white, black, chocolate, grey, yellow or green marble chips of sizes from 4mm to 7mm nominal size laid in cement marble powder mix 3:1 (3 cement : 1 marble powder) by weight in proportion of 4:7 (4 cement marble powder : 7 marble chips) by volume including cement slurry etc. complete.
| Ordinary cement without any pigment. | 560 | sqm
SUB HEADX XIII : PVC WORK
70 | Providing and fixing factory made PVC door frame manufactured by M/s Rajshri or equivalent of size 50x47 mm with a wall thickness of 5 mm. made out of extruded 5 rigid PVC foam sheet mitred at corners and joined with 2 Nos. of 150 mm long brackets of 15x15mm M.S. square tube,the vertical door profiles to be reinforced with 19x19 mm M.S. square tube of 19 guage, EPDM rubber gasket weather seal to be provided through out the frame. The door frame to be fixed to the wall using M.S. screws of 65/100 mm size complete as per manufactures specification and direction of Engineer-in-charge | 125 | m
71 | Providing and fixing 30mm thick factory made PVC rigid foam panelled door shutters manufactured by M/s Rajshri or equivalent made from M.S. tube of 19 guage thickness, size 19x19 mm for styles and 15x15 mm for top and bottom rails, covered with heat moulded PVC "C" channel of 5 mm thick and 75 mm wide PVC sheets for top rail, lock rail and bottom rail on either side and 5 mm thick 20mm wide cross PVC sheet as gap insert for top rail and bottom rial, panelling of 5mm thick PVC sheet fitted in the M.S. frame welded/ sealed to the styles and rails with 5x30mm PVC sheet beading on either side and joined together with solvent cement adhesive etc., complete as per manufacture specification and direction of Engineer-in-charge fixed to frames with 4 Nos. M.S. powder coated butt hinges (For W.C. and bathroom shutters). | 42 | sqm
SUB HEAD XIV :SANITARY INSTALLATIONS& WATER SUPPLY
72 | Providing and fixing water closet squatting pan (Indian type W.C. pan) with 100 mm sand cast Iron P or S trap, 10 litre low level white P.V.C. flushing cistern, including flush pipe, with manually controlled device (handle lever) conforming to IS : 7231, with all fittings and fixtures complete, including cutting and making good the walls and floors wherever required : White Vitreous china Orissa pattern W.C. pan of size 580x440 mm with integral type foot rests | 10 | each
73 | Providing and fixing white vitreous china pedestal type water closet (European type W.C.pan) with seat and lid, 10 litre low level P.V.C. flushing cistern with manually controlled device (handle lever), conforming to IS: 7231, Parryware/ Hindware/ Seabrid/ Orient (Coral) with all fittings and fixtures complete including cutting and making good the walls and floors wherever required :- | 10 | each
74 | Supply and fixing wall hanging type water closet with flushing cistern('HIND WARE'/' CERA' (special colours) or equivalent), with seat cover, along with all necessary requirement for fixing etc. complete. | 5 | each
75 | Providing and fixing wash basin with C.I. brackets, 15 mm C.P. brass pillar taps, 32 mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever require White Vitreous China Flat back wash basin size 550x400 mm with single 15 mm C.P. brass pillar tap
| Wash basin size 550x400mm with single 15mm C.P.brass pillar tap | 30 | each
76 | Providing and fixing Stainless Steel A ISI 304 (18/8) kitchen sink as per IS: 13983 with C.I. brackets and stainless steel plug 40 mm, including painting of fittings and brackets, cutting and making good the walls wherever required: Kitchen sink with drain board 510x1040 mm bowl depth 250 mm | 2 | each
77 | Providing and fixing white vitreous china laboratory sink with C.I. brackets, C.P. brass chain with rubber plug, 40 mm C.P brass waste and 40mm C.P. brass trap with necessary C.P. brass unions complete, including painting of fittings and brackets, cutting and making good the wall wherever required: Size 450x300x150 mm | 8 | each
78 | Providing and fixing P.V.C waste pipe for sink or wash basin, including P.V.C waste fittings complete :- | 60 | each
Flexible pipe :-32 mm dia.
79 | Providing and fixing trap of self cleansing design with screwed down or hinged grating with or without vent arm complete, including cost of cutting and making good the walls and floors | 40 | Each
a)100mm inlet and 75mm outlet.
80 | Providing and jointing PVC pipes of (pressure10 Kg/cm2) for water supply including testing of joints, concealing the pipes , & trenching & refilling wherever required etc complete.
a | 20mm PVC pipe | 100 | Rm
b | 25mm PVC pipe | 200 | Rm
c | 32mm PVC pipe | 200 | Rm
d | 40mm PVC pipe | 200 | Rm
81 | Providing and fixing C.P grating of approved quality and colour. 150 mm nominal size square 100 mm diameter of the inner hinged round grating | 25 | Nos
82 | Providing and fixing C.P. brass long body bib cock of approved quality conforming to IS standards and weighing not less than 690 gms. 15mm nominal bore | 25 | Nos
83 | Providing and fixing unplasticised rigid P.V.C pipe conforming to IS Standards(pressure 6kg/cm2) in drainage lines including cutting and making good the walls,cutting and refilling of earth, jointing all etc complete
a | 110mm dia | 50 | Rm
b | 75mm dia | 50 | Rm
84 | Providing & fixing PVC Fittings and fixtures Conforming IS specifications including cutting and making good the walls etc complete
a | 110mm dia plain elbow | 50 | each
b | 75mm dia plain elbow | 50 | each
c | 110mm dia door elbow | 50 | each
d | 75mm dia door elbow | 50 | each
e | 110mm dia plain bend | 50 | each
f | 75mm dia plain bend | 50 | each
g | 110mm dia door tee | 50 | each
h | 75mm dia door tee | 50 | each
i | 110mm dia air cowl | 50 | each
j | 75mm dia air cowl | 50 | each
k | 110mm dia offset | 40 | each
l | 75mm dia offset | 40 | each
85 | Providing and fixing C.P. brass bib cock of approved quality conforming to IS:8931 15mm nominal bore | 10 | each
86 | Providing and fixing C.P. brass stop cock (concealed) of standard design and of approved make conforming to IS:8931. 15mm nominal bore | 25 | each
87 | Providing and fixing unplasticised P.V.C connection pipe with brass unions :- 45 cm length
a | 15MM nominal bore | 25 | each
88 | Providing and fixing gun metal gate valve with CI wheel of approved quality(screwed end) –
| 32mm dia nominal bore | 2 | each
89 | Providing and fixing ball valve (brass) of approved quality complete.High or low pressure with plastic floats 25 mm nominal bore | 5 | each
90 | Providing and fixing mirror of superior glass (of approved quality) and of required shape and size with plastic moulded frame of approved make and shade with 6 mm thick hard board backing : Rectangular shape 453x357 mm | 30 | each
91 | Providing and fixing CP towel rail complete with brackets fixed to wooden cleats with CP brass screws with concealed fittings arrangement of approved quality and colour.450 mm long towel rail with total length of 495 mm, 78 mm wide and effective height of 88 mm, weighing not less than 170 gms | 30 | each
92 | Providing and fixing CP soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements, weighing not less than 106 gms. | 30 | each
93 | Providing and fixing white vitreous china flat back or wall corner type lipped front urinal basin of 430x260x350 mm and 340x410x265 mm sizes respectively with automatic flushing cistern with standard flush pipe and C.P. brass spreaders with brass unions and G.I clamps complete, including painting of fittings and brackets, cutting and making good the walls and floors wherever required : One urinal basin with 5 litre white P.V.C. automatic flushing cistern | 2 | EACH
DRAINAGE
94 | Providing and fixing Porcelain Gully trap of 300 x 300 mm inside dimension for the waste line with cement concrete in1:4:8 (1 cement : 4 coarse sand : 8 graded stone aggregate 40mm nominal size) for foundation and with necessary brick masonry in cement mortar 1:4 (1 cement : 4 coarse sand) and plastering with 12mm thick cement plaster in cement mortar 1:4 (1 cement : 4 fine sand) including neat cement flushing coat and providing RCC top slab with 1:2:4 mix etc complete | 10 | each
95 | Constructing brick masonry manhole in cement mortar 1:4 (1 cement : 4 coarse sand) with R.C.C. top slab with 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand : 8 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design: Inside size 90x80 cm and 45 cm deep including C.I. cover with frame (light duty) 455x610 mm internal dimensions, total weight of cover and frame to be not less than 38 kg (weight of cover 23 kg and weight of frame 15 kg): With common burnt clay F.P.S. (non modular) bricks of class designation 50 | 10 | each
96 | Extra for depth for manholes :- With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 5 | m
97 | Constructing soak pit 1.20x1.20x1.20 m filled with brickbats including S.W. drain pipe 100 mm diameter and 1.20 m long complete as per standard design. | 5 | each
SUB HEAD: XV - ROAD WORK
98 | Preparation and consolidation of sub grade with power road roller of 8 to 12 tonne capacity after excavating earth to an average of 22.5cm depth, dressing to camber and consolidating with road roller including making good the undulations etc. and re-rolling the subgrade and disposal of surplus earth with lead upto 50 metres. | 50 | sqm
Supplying and stacking at site.
99 | 53 mm to 22.4 mm size stone aggregate | 50 | sqm
100 | Laying, spreading and compacting stone aggregate of specified sizes to WBM specifications in uniform thickness, hand picking, rolling with 3 wheeled road/ vibratory roller 8-10 tonne capacity in stages to proper grade and camber, applying and brooming requisite type of screening/ binding material to fill up interstices of coarse aggregate,watering and compacting to the required density . | 5 | cum
101 | Providing and laying in position cement concrete of specified grade excluding the cost of centring and shuttering - All work upto plinth: 1 : 5 : 10 (1 Cement : 5 coarse sand : 10 graded stone aggregate 40 mm nominal size). | 5 | cum
102 | Providing and laying at or near ground level factory made kerb stoneof M-25 grade cement concrete in position to the required line, level and curvature, jointed with cement mortar 1:3 (1 cement: 3 coarse sand), including making joints with or without grooves (thickness of joints except at sharp curve shall not to more than 5mm), including making drainage opening wherever required complete etc. as per direction of Engineer-in-charge (length of finished kerb edging shall be measured for payment). (Precast C.C. kerb stone shall be approved by Engineer-in-charge). | 1.5 | CUM
TOTAL (PART A)