## boq
PART IV- FIRE PROTECTION SYSTEM ESTIMATE FOR FORT HOSPITAL
Sl. No. | Description of item | Unit | Qty | Rate Rs in figures & words | Amount
1 | FIRE ALARM SYSTEM
1.1 | Supply, installation, testing and commissioning of Conventional type Manual Call Point (break glass type) complete with push button, enclosed in box with provision for cable or conduit coupling. The unit to be painted fire red outside, white inside and written 'In case of fire break glass' compatible for connecting to Alarm Panel. | each | 2
1.2 | Supply, installation, testing and commissioning of Conventional type Hooter cum Speaker at different locations complete with all fixing accessories, etc. under false ceiling, roof, wall, etc, with a time delay of max 30sec, compatible for connecting to Alarm Panel complete as required. | each | 2
1.3 | Supply, Installation, Testing & Commissioning of Conventional type Fire Alarm Panel with 2 Zones ( each zone compatible for least 16 devices) ) including battery backup. The panel shall have LED indication with sounder during device activation, | each | 1
1.4 | Supplyand installation, testing and commissioning of armoured 2C x 1.5 Sq.mm FRLS copper cable ISI marked with proper clamping, supports and terminations. | Rm | 66
TOTAL FOR FIRE DETECTION & ALARM SYSTEM
2 | HYDRANT/SPRINKLER SYSTEM
2.1 | a) Supplying, Installation, testing and commissioning of electric driven mon block pump (terrace pump) sets suitable for automatic operation and consisting electrical control panel with DOL Starter and accessories of the following complete in all respect as required
Pump rated for 450lpm, 35m head end suction, type, C.I body volute type coupled with suitable HP SQ cage induction motor,sychoronous speed 2900rpm, suitable for operation on 415V, 3phase 50Hz, AC with IP 55 class of protection for enclosure, horizontal foot mounted type with class F insulation
M.S. fabricated common base plate, coupling, coupling guard, foundation bolts etc. as required.
| Suitable cement concrete foundation duly plastered with anti vibration pads. | set | 1
2.2 | Supply, installation, testing and commissioning of pressure gauge 0-200 PSI ( 0 - 14 Kg ) range, 3/8" BSP bottom entry, 4" dial weather proof with stainless steel internals, siphon tube amd ball valve including fittings, etc. complete as required | each | 1
2.3 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589 and 1239 including drop forged fittings like elbows, tees flanges, tapers, nuts bolts, gaskets etc, fixing the pipe on the wall/ceiling with suitable clamps and painting with primer and two or more coats of synthetic enamel paint of required shade complete as required.
2.3.1 | 100 mm dia | Rm | 25
2.3.2 | 80 mm dia | Rm | 7
2.4 | Supplying, fixing, testing & commissioning of dual plate non-return valve of following sizes confirming to IS : 5312 complete with rubber gasket, GI bolts, nuts, washers etc. as required.
2.4.1 | 100 mm dia | each | 1
2.5 | Supply, installation, testing and commissioning of gun metal fire hydrant valve, single headed oblique type 63 mm instantaneous outlets with female socket for hose connection and inlet side with flange suitable for 100 mm pipe flange, valve conforming to 1S:5290 complete with blank cap chain, etc | each | 3
2.6 | Supplying and fixing First-aid Hose Reel with MS construction spray painted in Post office Red, conforming to IS 884 with up to date amendments, complete with the following as required. (a) 30 m. long 20 mm (nominal internal dia water hose Thermoplastic (Textile reinforced) Type-2 as per IS: 12585 (b) 20 mm (nominal internal ) dia gun metal globe valve & nozzle. (c) Drum and brackets for fixing the equipments on wall. (d) Connections from riser with 40 mm dia stop valve (gun metal) & M.S. Pipe | set | 2
2.7 | Supplying and fixing 63 mm dia, 15 mtr. Long RRL hose pipe with 63 mm dia Male and Female Gun metal couplings duly binded with GI wire, rivets etc. conforming to IS 636 (type-A) as required. | each | 6
2.8 | Supplying & fixing 63 mm dia Gun metal branch pipe with 20 mm (nominal internal diameter) size Gun Metal nozzle conforming to IS 903, suitable for instantaneous connection to inter-connect hose pipe coupling as required. | each | 3
2.9 | Supply, installation, testing and commissioning of hose boxes wall/pedestal type of size 750 x 250 x 600 mm made out of 16 SWG MS sheet steel with front side glass, locking arrangement and painted with approved colour completed as required and as per specifications. | each | 3
2.1 | Supply, installation, testing and commissioning of Fire brigade collective breaching with 4 nos. of (twin Siamese) 150 mm flanged out let connection and built in check valves complete as required. | set | 1
2.11 | Supply, and fixing of Air release valve all riser pipes as per specification | set | 1
2.12 | Supplying and fixing, testing & commissioning of butterfly valve of rating PN 1.0 with cast Iron body, SG Iron seat ISI marked complete with nuts, bolts, washers, gaskets, conforming to IS 13095 following sizes as required.
2.12.1 | 100 mm dia | each | 3
TOTAL FIRE HYDRANT/SPRINKLER SYSTEM
3 | PORTABLE FIRE EXTINGUISHERS
3.1 | Supply and fixing of Water type Fire Extinguisher 9 litres on wall with hook plate and anchor fastening of ISI marked with internal plastic lining and solid drawn body with 60 grams CO2 cartridge with gun metal plunger and 1.0 M long discharge hose confirming to IS 940 and complete in all respects including initial fill with CO2. | each | 6
3.2 | Supply & fixing of of Carbon-dioxide extinguisher on wall of ISI marked 4.5 Kg capacity made of high pressure seamless steel cylinder (CCE marked ) confirming to IS 2878, 8149. complete with wheel type valve with one meter long braided high pressure discharge hose complete in all respects including initial fill with CO2 gas. | each | 2
TOTAL FOR FIRE EXTINGUISHERS
TOTAL (PART IV)

## Analysis
RATE ANALYSIS
1 | Fire Detection System
1.1 | Sl. No. | Description | Unit | Qty. | Rate | Amount
[5 empty] | (Rs) | (Rs)
Manual Call Point
Cost
Materials
| A | Cost | No | 1 | 800 | 800
| B | Discount |  |  |  | Nil
800
| C | VAT @ 4.04% |  |  |  | Included
| D | Carriage, insurance 1% |  |  |  | Included
800
| E | Cost of Fixing & labour | @ | 5% |  | Included
800
| F | Add for Contractor's profits and overheads @ 15% |  |  |  | 120
|  | Total |  |  |  | 920
[5 empty] | Say | 920
1.2 | Sl. No. | Description | Unit | Qty. | Rate | Amount
[5 empty] | (Rs) | (Rs)
Hooter
Cost
Materials
| A | Cost | No | 1 | 1000 | 1000
| B | Discount |  |  |  | Nil
1000
| C | VAT @ 4.04% |  |  |  | Included
| D | Carriage, insurance 1% |  |  |  | Included
1000
| E | Cost of Fixing & labour | @ | 5% |  | Included
1000
| F | Add for Contractor's profits and overheads @ 15% |  |  |  | 150
|  | Total |  |  |  | 1150
[5 empty] | Say | 1150
1.3 | Sl. No. | Description | Unit | Qty. | Rate | Amount
[5 empty] | (Rs) | (Rs)
Detail of Cost for fire alarm panel
Materials
| A | Cost | No | 1 | 14000 | 14000
| B | Discount |  |  |  | Nil
14000
| C | VAT @ 4.04% |  |  |  | Included
| D | Carriage, insurance 1% |  |  |  | Included
14000
| E | Cost of Fixing & labour | @ | 5% |  | Included
14000
| F | Add for Contractor's profits and overheads @ 15% |  |  |  | 2100
|  | Total |  |  |  | 16100
[5 empty] | Say | 16100
1.4 | Sl. No. | Description | Unit | Qty. | Rate | Amount
[5 empty] | (Rs) | (Rs)
1.5 FRLS cable
| A | Cost | Rm | 1 | 180 | 180
|  | Sub Total |  |  |  | 180
| C | Excise Duty | @ | 12.36% |  | Included
|  | Sub Total |  |  |  | 180
12.36
| C | VAT @ 4.04% |  |  |  | Included |  | 4.04
| D | Carriage, insurance 1% |  |  |  | Included |  | 19.5
| E | Labour @ 15% |  |  |  | Included
|  | Sub Total |  |  |  | 180
| F | Add for Contractor's profits and overheads @ 15% |  |  |  | 27
|  | Total |  |  |  | 207
[5 empty] | Say | 207
Add CI
Final Amount
0 | Sl. No. | Description | Unit | Qty. | Rate | Amount
[5 empty] | (Rs) | (Rs)
PVC Conduit
| A | Cost | Rm | 1 | 56.5 | 56.5 | SOR 2012
|  | Sub Total |  |  |  | 56.5
| C | Excise Duty | @ | 12.36% |  | Included
|  | Sub Total |  |  |  | 56.5
12.36
| C | VAT @ 4.04% |  |  |  | Included |  | 4.04
| D | Carriage, insurance 1% |  |  |  | Included |  | 19.5
| E | Labour @ 15% |  |  |  | 8.475 | SOR 2011
|  | Sub Total |  |  |  | 64.975
| F | Add for Contractor's profits and overheads @ 15% |  |  |  | 9.7462
|  | Total |  |  |  | 74.7212
[5 empty] | Say | 75
Add CI
Final Amount
2 | Fire Hydrant System
2.1 | Fire Terrace Pump
| Sl. No. | Description | Unit | Qty. | Rate | Amount
[5 empty] | (Rs) | (Rs)
Detail of Cost for terrace fire pump
Materials
| A | Cost of pump | M | 1 | 42000 | 42000
| B | Discount Included
42000
| C | VAT @ 4.04% |  |  |  | Included
| D | Carriage 1% |  |  |  | Included
42000
| E | Cost of Fixing Materials |  | LS |  | Included
| F | Labour 5% |  |  |  | Included
|  | Total |  |  |  | 42000
| G | Add for Contractor's profits and overheads @ 15% |  |  |  | 6300
| F | Add DOL Starter |  |  |  | Included
|  | Cost of Fire pump Terrace |  |  |  | 48300
[5 empty] | Say | 48300
2.2 | Sl. No. | Description | Unit | Qty. | Rate | Amount
[5 empty] | (Rs) | (Rs)
Detail of Cost for Pressure gauge
Materials
| A | Cost of pressure gauge | No. | 1 | 2000 | 2000
| B | VAT @ 12.63% |  |  |  | Included
| C | Carriage 1% |  |  |  | Included
2000
| D | Cost of Fixing Materials |  | LS |  | Included
| E | Labour @5% |  |  |  | Included
|  | Total |  |  |  | 2000
| F | Add for Contractor's profits and overheads @ 15% |  |  |  | 300
|  | Cost of Guage |  |  |  | 2300
[5 empty] | Say | 2300
2.3.1 | MS Heavy Duty Pipe 100mm
| Sl. No. | Description | Unit | Qty. | Rate | Amount
[5 empty] | (Rs) | (Rs)
Detail of Cost for 100 mm dia MS (Heavy class) pipe
Materials
| A | Cost of pipe | M | 10 | 1900 | 19000
| B | Discount -included
19000
| C | Add for Fittings 10% |  |  |  | Included
| D | Add for Wastage 2% |  |  |  | Included
19000
| E | VAT @ 4% |  |  |  | Included
| F | Carriage 1% |  |  |  | Included
19000
| G | Labour 10% |  |  |  | Included
19000
| H | Add for Contractor's profits and overheads @ 15% |  |  |  | 2850
|  | Cost for 10 Metre Pipe |  |  |  | 21850
|  | Cost for one Metre pipe |  |  |  | 2185
[5 empty] | Say | 2185
2.3.2 | MS Heavy Duty Pipe 80mm
| Sl. No. | Description | Unit | Qty. | Rate | Amount
[5 empty] | (Rs) | (Rs)
Detail of Cost for 80 mm dia MS (Heavy class) pipe
Materials
| A | Cost of pipe | M | 10 | 1650 | 16500
| B | Discount -included
16500
| C | Add for Fittings 10% |  |  |  | Included
| D | Add for Wastage 2% |  |  |  | Included
16500
| E | VAT @ 4% |  |  |  | Included
| F | Carriage 1% |  |  |  | Included
16500
| G | Labour 10% |  |  |  | Included
16500
| H | Add for Contractor's profits and overheads @ 15% |  |  |  | 2475
|  | Cost for 10 Metre Pipe |  |  |  | 18975
|  | Cost for one Metre pipe |  |  |  | 1897.5
[5 empty] | Say | 1898
2.4.1 | Sl. No. | Description | Unit | Qty. | Rate | Amount
[5 empty] | (Rs) | (Rs)
Detail of Cost for 100 mm Non-Return Valve
Materials
| A | Cost of valve | M | 1 | 6500 | 6500
| B | Disocount |  |  |  | Nil
6500
| C | CST @ 5% |  |  |  | Included
| D | Carriage 1% |  |  |  | Included
6500
| E | Cost of Fixing Materials @ 2% |  |  |  | Included
| F | Labour 5% |  |  |  | Included
6500
| G | Add for Contractor's profits and overheads @ 15% |  |  |  | 975
|  | Cost of Valve |  |  |  | 7475
[5 empty] | Say | 7475
2.5 | Sl. No. | Description | Unit | Qty. | Rate | Amount
[5 empty] | (Rs) | (Rs)
Detail of Cost for Single headed hydrant landing valve
Materials
| A | Cost of single headed landing valve | No. | 1 | 8000 | 8000
| B | Excise Duty @ 12.36% |  |  |  | Included
8000
| C | VAT @ 5% |  |  |  | Included
| D | Carriage 1% |  |  |  | Included
8000
| E | Labour 5% |  |  |  | Included
8000
| F | Add for Contractor's profits and overheads @ 15% |  |  |  | 1200
9200
[5 empty] | Say | 9200
2.6 | Sl. No. | Description | Unit | Qty. | Rate | Amount
[5 empty] | (Rs) | (Rs)
Detail of Cost for Hose Reel
Materials
| A | Cost of hose reel | No. | 1 | 8500 | 8500
| B | VAT @ 15% |  |  |  | Included
| C | Carriage 1% |  |  |  | Included
8500
| D | Labour 5% |  |  |  | Included
8500
| E | Add for Contractor's profits and overheads @ 15% |  |  |  | 1275
|  | Cost of RRL hoses |  |  |  | 9775
[5 empty] | Say | 9775
2.7 | Sl. No. | Description | Unit | Qty. | Rate | Amount
[5 empty] | (Rs) | (Rs)
Detail of Cost for RRL Hoses 15 m
Materials
| A | Cost of RRL Hoses | No. | 1 | 6000 | 6000
| B | Cost of Adaptor included | No. | 1 |  | 0
6000
| C | VAT @ 5% |  |  |  | Included
| D | Carriage 1% |  |  |  | Included
6000
| E | Labour 5% |  |  |  | Included
6000
| F | Add for Contractor's profits and overheads @ 15% |  |  |  | 900
|  | Cost of RRL hoses |  |  |  | 6900
[5 empty] | Say | 6900
2.8 | Sl. No. | Description | Unit | Qty. | Rate | Amount
[5 empty] | (Rs) | (Rs)
Detail of Cost for Branch Pipe
Materials
| A | Cost of hose reel | No. | 1 | 2200 | 2200
| B | Duties @ 12.36% |  |  |  | Included
2200
| C | VAT@ 15% |  |  |  | Included
| D | Carriage 1% |  |  |  | Included
2200
| E | Labour 5% |  |  |  | Included
2200
| F | Add for Contractor's profits and overheads @ 15% |  |  |  | 330
|  | Cost of Branch Pipe |  |  |  | 2530
[5 empty] | Say | 2530
2.9 | Sl. No. | Description | Unit | Qty. | Rate | Amount
[5 empty] | (Rs) | (Rs)
Detail of Cost for fire hose cabinet
Materials
| A | Cost of FHC | No. | 1 | 4000 | 4000
| C | VAT @ 15% |  |  |  | Included
| D | Carriage 1% |  |  |  | Included
4000
| E | Labour 5% |  |  |  | Included
4000
| F | Add for Contractor's profits and overheads @ 15% |  |  |  | 600
|  | Cost of FHC |  |  |  | 4600
[5 empty] | Say | 4600
2.1 | Sl. No. | Description | Unit | Qty. | Rate | Amount
[5 empty] | (Rs) | (Rs)
Detail of Cost for Fire brigade point with check valve
Materials
| A | Cost of connection | No. | 1 | 7500 | 7500
| B | duties @ 12.36% |  |  |  | Included
7500
| B | VAT @ 15% |  |  |  | Included
| C | Carriage 1% |  |  |  | Included
7500
| D | Labour 5% |  |  |  | Included
7500
| E | Add for Contractor's profits and overheads @ 15% |  |  |  | 1125
8625
[5 empty] | Say | 8625
2.11 | Air Release Valve
| Sl. No. | Description | Unit | Qty. | Rate | Amount
[5 empty] | (Rs) | (Rs)
Detail of Cost for Air release valve
Materials
| A | Cost of valve | No. | 1 | 1500 | 1500
| B | VAT @ 12.625% |  |  |  | Included
| C | Carriage 1% |  |  |  | Included
|  | Total |  |  |  | 1500
| D | Labour 5% |  |  |  | Included
|  | Total |  |  |  | 1500
| E | Add for Contractor's profits and overheads @ 15% |  |  |  | 225
|  | Cost of Valve |  |  |  | 1725
[5 empty] | Say | 1725
2.12.1 | Sl. No. | Description | Unit | Qty. | Rate | Amount
[5 empty] | (Rs) | (Rs)
Detail of Cost for CI butter fly valve (100mm)
Materials
| A | Cost of Valve | No. | 1 | 6000 | 6000
| B | VAT @ 12.625% |  |  |  | Included
| C | Carriage 1% |  |  |  | Included
|  | Sub Total |  |  |  | 6000
| D | Cost of Fixing Materials @ 2% |  |  |  | 120
| E | Labour 5% |  |  |  | Included
|  | Sub Total |  |  |  | 6120
| F | Add for Contractor's profits and overheads @ 15% |  |  |  | 918
|  | Cost of Valve |  |  |  | 7038
[5 empty] | Say | 7038
3.1 |  | Fire Extinguisher-Watertype 9 kg
| A1 | Materials
| A | Basic price |  |  |  | 2500
| B | Discount |  |  |  | Nil
| C | Accessories |  |  |  | Included
| D | Excise duty |  |  |  | Included
| E | VAT incl CESS | 12.62 | % |  | Included
|  | SubTotal A1 |  |  |  | 2500
|  | Transportation | 1 | % |  | Included
|  | Sub Total |  |  |  | 2500
| F | Add for Contractor's profits and overheads @ 15% | 15 | % |  | 375
|  | TOTAL |  |  |  | 2875
3.2 |  | Fire Extinguisher- CO2 type 4.5 kg
Materials
| A | Basic price |  |  |  | 6000
| B | Discount |  |  |  | Nil
| C | Accessories |  |  |  | Included
| D | Excise duty |  |  |  | Included
| E | VAT incl CESS | 12.62 | % |  | Included
|  | SubTotal A1 |  |  |  | 6000
|  | Transportation | 1 | % |  | Included
|  | Sub Total |  |  |  | 6000
| F | Add for Contractor's profits and overheads @ 15% | 15 | % |  | 900
|  | TOTAL |  |  |  | 6900