## ELECTRICAL
PART D: ELECTRICAL WORKS
SL.NO | DESCRIPTION OF ITEM | QTY. | UNIT | RATE (RS.) | AMOUNT (RS.)
SCHEDULE ITEMS
INTERNAL WIRING
Note:
Rates of only ISI marked PVC conduit, FR PVC insulated multi-stranded copper conductor single core cables, modular plate type switches and socket outlets in M.S. box of 18 SWG and earth wire have been taken in the following items unless and otherwise specified, only such conduits, cables switches and socket outlets shall be used in the work as per list of approved makes attached with tender documents.
1 | Wiring for Light /Ceiling Fan / Exhaust Fan/ Call Bell point with 1.5 sq.mm FR PVC insulated multi-stranded copper conductor cable in surface / recessed PVC conduit, with modular switch, modular plate, suitable GI box, and earthing the point with 1.5 sq.mm. FR PVC insulated copper conductor single core cable etc as required.
| Group -C | 191 | Point | 664 | 126824
2 | Wiring for Light plug 2 x 2.5 sq.mm FR PVC insulated multi-stranded copper conductor, single core cable in recessed ISI marked PVC conduit along with 1 No. 2.5 sq.mm FR PVC insulated copper earth wire for loop earthing as required. | 355 | Metre | 131 | 46505
3 | Wiring for power plug 2 x 4 sq.mm FR PVC insulated multi-stranded copper conductor single core cable in surface / recessed PVC conduit along with 1 No. 4 sq.mm insulated copper earth wire for loop earthing as required. | 460 | Metre | 162 | 74520
4 | Wiring for power plug with 2 x 6 sq.mm FR PVC insulated multi-stranded copper conductor single core cable in surface / recessed PVC conduit along with 1 No. 6 sq.mm FR PVC insulated copper earth wire for loop earthing as required. | 990 | Metre | 206 | 203940
5 | Wiring for power plug with 4 x 6 sq.mm FR PVC insulated multi-stranded copper conductor single core cable in surface / recessed PVC conduit along with 2 Nos. 6 sq.mm PVC insulated solid copper earth wire for loop earthing as required. | 900 | Metre | 358 | 322200
6 | Supplying and fixing of M.S. box of 18 SWG in recessed including providing and fixing modular plate type 5 pin 6 Amp socket outlet, 6 Amp switch and plug top including connections, an painting etc. as required. (Light Plug). | 71 | Each | 288 | 20448
7 | Supplying and fixing of M.S. box of 18 SWG in recessed including providing and fixing modular plate type Universal 6 pin 16 Amp. Socket outlet, 16 Amp switch and plug top including connections, and painting etc. as required. (Power Plug). | 23 | Each | 366 | 8418
8 | Supplying and fixing of M.S. box of 18 SWG in recessed including providing and fixing modular plate type 5 pin, 6 Amps socket outlet without switch with plug top complete including connections, and painting etc. as required. (Exit / Emergency Light Points). | 4 | Each | 288 | 1152
9 | Wiring for circuit wiring with 2 x 2.5 sq.mm FR PVC insulated multi-stranded copper conductor single core cable with 1 x 2.5 sq.mm. FR PVC inculated earth wire in recessed PVC conduit as required. | 358.125 | Metre | 131 | 46914.375
10 | Wiring for group light points with 2 x 2.5 sq.mm FR PVC insulated multi-stranded copper conductor single core cable in recessed PVC conduit with accessories like junction boxes, bends, socket and connectors including continuous running of 1 No. 2.5 sq.mm FR PVC insulated solid copper conductor earth wire complete with earthing the fixtures and outlet boxes as per specification and drawings (basements, staircase and well light point wiring). | 100 | Metre | 131 | 13100
11 | Providing, fixing, testing and commissioning of under noted rating flush type industrial socket outlet with plug top controlled by ELCB/MCB all mounted in M.S. sheet steel box duly painted in recess / surface complete as required (excluding, wiring and conduit)
a | 20 Amps 3 pin socket outlet controlled by DP MCB. | 31 | Each | 693 | 21483
b | 32A, 3 phase, 5 pin socket outlet controlled by 32A, TPN pole MCB | RO | Each | 1983
12 | Providing, fixing, testing and commissioning of call bell/buzzer suitable for D.C/A.C, single phase, 230 V, complete as required. | RO | Each | 54
13 | Supplying and fixing of following sizes of PVC conduit along with the accessories in surface / recess including cutting the wall and making good the same in case of recessed conduit as required as per specification.
a) | 20mm dia PVC conduit | 800 | Metre | 56.5 | 45200 | 101700
b) | 25mm dia PVC conduit | 500 | Metre | 64.5 | 32250
c) | 32mm dia PVC conduit | 500 | Metre | 80.5 | 40250
14 | Wiring for sub mains wiring with following sizes of FR PVC insulated, multi-stranded copper conductor single core cables in surface / recessed PVC conduit as required.
a) | 4 x 6 sq.mm + 2 x 6 sq.mm. earth wire | RO | Metre | 358
b) | 4 x 10 sq.mm + 2 x 10 sq.mm. earth wire | 360 | Metre | 562 | 202320
c) | 4 x 16 sq.mm + 2 x 16 sq.mm. earth wire | 50 | Metre | 789 | 39450
d) | 4 x 25 sq.mm + 2 x 16 sq.mm. earth wire | 50 | Metre | 789 | 39450
M.V. PANELS/ DISTRIBUTION BOARD
15 | Supplying, fixing, connecting, testing and commissioning of following way, three poels and neutral, prewired, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete suitable for incomer MCB and RCCB , with loose wire box, terminal blocks, duly prewired qith suitable size FR PVC insulated copper conductor up to terminal blocks, tinned copper busbar, netral link, earth bar, din bar, detachable gland, interconnectons, phosphatised and powder coated including earthing etc as required.
a | 4-way, double door | RO | Nos. | 6816
b | 12-way, double door | 8 | Nos. | 12762 | 102096
16 | supplying fixing following rating four pole 415 volts, isolator in existing MCB DB complete with connections, testing and commisioning etc., as required.
a | 40 amps, c-curve | RO | Nos. | 554
b | 63 amps, c-curve | 8 | Nos. | 563 | 4504
17 | supplying fixing following rating four pole 415 volts, four pole (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commisioning etc., as required.
A. | 40 amps | RO | Nos. | 1703
B. | 63 amps | 8 | Nos. | 1965 | 15720
18 | supplying and fixing 5 amps to 32 amps rating of SP MCB, 240 volts, “C” series, miniature circuit breaker suitable for inductive load in existing MCB DB complete with connections, testing and commissioning etc., s required. | 288 | Nos. | 141 | 40608
19 | Supply and fixing of H.T. Danger notice plate of 250x200mm made of mild steel at least 2mm thick and vitreous enameled white on both side with inscription in signal red colour on front side as required. | 6 | Each | 135 | 810
20 | Providing and fixing MV danger plate of 200 x 150mm of mild steel at least 2mm thick and vitreous enameled white paint on both side and with inscription in signal red colour on front side as required. | 4 | Each | 121 | 484
L.T. CABLES
21 | Supply and making end termination with brass double compression gland including providing and crimping of Aluminium solderless lugs / ferrules for XLPE armoured power Aluminium conductor cable 1.1 KV grade of following sizes:-
a) | 3.5 x 185 sq.mm | 4 | Set | 616 | 2464
b) | 3.5x 150 sq.mm | 4 | Set | 458 | 1832
c) | 4 x 25 sq.mm | 10 | Set | 192 | 1920
d) | 4 x 16 sq.mm | 12 | Set | 188 | 2256
e) | 4 x 10 sq.mm | RO | Set | 146
22 | Supply and fixing of perforated1.6 mm thick CRCA sheet steel power coated cable tray of following sizes complete with bend/tee joints, coupling plate & nuts bolts etc. including providing and fixing of M.S. painted hanger etc. as required.
a) | 300mm wide 50mm depth | 20 | Metre | 677 | 13540
EARTHING
23 | Earthing with GI earth plate 600 x 600 x 6mm thick including accessories and providing masonry enclosure with cover plate having locking arrangement with watering pipe complete with coke and salt etc. as required. | 4 | Each | 3996 | 15984
24 | Earthing with CU earth plate 600 x 600 x 6mm thick including accessories and providing masonary enclosure with cover plate having locking arrangement with watering pipe complete with coke and salt etc. as required. | 4 | Each | 8559 | 34236
25 | Supply and fixing of following sizes of copper/GI strip in GI pipe from earth electrode including cost of GI pipe 'B' class as required.
a | 25mm x 5mm GI | 40 | Metre | 364 | 14560
26 | Supply and fixing of following of copper/GI strip on surface or in recess for connections etc. as required.
a) | 50mm x 6mm copper | 40 | Meter | 1439 | 57560
b) | 25mm x 5mm GI | 60 | Metre | 120 | 7200
27 | Providing and fixing of 6 SWG GI wire on surface or in recess for loop earthing along with the existing surface/recessed conduit for sub main wiring / cable as required. | RO | Metre | 19.5
T.V. , TELEPHONE SYSTEM & LAN SYSTEM
28 | Supplying, drawing, connecting and testing of 0.5 mm dia annealed copper conductor PVC insulated PVC sheathed telephone wire in existing conduit/wire way duct etc. as required of following sizes:
a) | 4 Pair (8 core) | RO | Metre | 24
b) | 2 Pair (4 core) | 880 | Metre | 15.5 | 13640
29 | Supplying and fixing of following sizes of PVC conduit along with the accessories in surface / recess including cutting the wall and making good the same in case of recessed conduit as required as per specification.
a) | 20mm dia PVC conduit | 1000 | Metre | 56.5 | 56500
b) | 25mm dia PVC conduit | 200 | Metre | 64.5 | 12900
c) | 32mm dia PVC conduit | 200 | Metre | 80.5 | 16100
30 | Supplying and fixing M.S. box with modular type telephone (RJ-11) outlet complete as required. | 22 | Each | 89 | 1958
31 | Supplying and fixing M.S. box with modular type coaxial outlet for TV antenna complete as required. | 1 | Each | 93 | 93
32 | Providing, laying, connecting and testing of unarmoured TV cable RG-6 PVC insulated cable along wall or ceiling or through existing pipe. | 30 | Metre | 22 | 660
MV CABLES
33 | Supplying and making indoor cable end termination with cast resin compound, including lugs and other jointing materials complete with all accessories for following sizes of 3 core, XLPE aluminium conductor cable of 11 KV grade as required.
a. | 3Cx120 Sq.mm. | 4 | set | 2775 | 11100
34 | Supplying and making outdoor cable end termination with cast resin compound, including lugs and other jointing materials complete with all accessories for following sizes of 3 core, XLPE aluminium conductor cable of 11 KV grade as required.
| 3Cx120 Sq.mm. | 4 | set | 6562 | 26248
NON SCHEDULE ITEMS
35 | Providing, fixing, testing and commissioning of under noted rating flush type industrial socket outlet with plug top controlled by ELCB/MCB all mounted in M.S. sheet steel box duly painted in recess / surface complete as required (excluding, wiring and conduit)
a) | 20 Amps 3 pin socket outlet controlled by DP ELCB (30 mA) | 2 | Each | 2879.7976 | 5759.5953
FANS & LIGHT FIXTURES:
36 | Supplying, fixing, connecting, testing and commissioning of 4x14 watt T-5 light fixture recessed mounting CAT-2 luminaire with 3D lamellae complete with electronic ballast, lockable holders and fluorescent lamp including connection etc. as required similar to Philips Cat no. Xtend TBS669M4xTL514W EBP D6. | 42 | Each | 4870.2388 | 204550.0275
37 | Supplying, fixing, connecting, testing and commissioning of 1 x 28 watt T-5 light fixture luminaire complete with electronic ballast, lockable holders and fluorescent lamp including connection etc. as required similar to Philips cat no. Adernov2 | 4 | Each | 690.929 | 2763.716
38 | Supplying, fixing, connecting, testing and commissioning of recessed type down-lighter with reflector and louver ,fitting complete with,holder, electronic ballast 1 x 18 W lamp including connections etc. as required similar to Philips Cat no. FBT150 1xPLC/2P18W . | 29 | Each | 1443.23 | 41853.67
39 | Supplying, fixing, connecting, testing and commissioning of recessed type down-lighter with reflector and louver ,fitting complete with,holder, electronic ballast 2 x 18 W lamp including connections etc. as required similar to Philips Cat no. FBH225P 2xPLC/2P18W . | 71 | Each | 1821.905 | 129355.255
40 | Supplying of 1x70 watt Metal halide light fixture with lamps, ballast including wiring and connections etc as required similar to Philips cat no. MPF922 1xMHNTD-70W | 2 | Each | 7905.95 | 15811.9
41 | Supplying, fixing, connecting, testing and commissioning of Bulkhead type light fitting with opal acrylic cover complete with , wire guard, holder, electronic ballast 1 x 11 W lamp including connections etc. as required similar to Philips Cat. No. FXC101 | 2 | Each | 1178.1575 | 2356.315
42 | Supplying, erection, connecting, testing and commissioning of 1200mm sweep ceiling fan complete with blades, down rod, shackle insulator, canopy etc. including providing of electronic step regulator with faceplate matching the existing modular switches as required. | 19 | Each | 2018.13 | 38344.47
43 | Supplying, erection, connecting, testing and commissioning of following size exhaust fan complete with gravity louver and connection with 3 core flexible wire as required.
| a) 305mm 1400 RPM | 6 | Each | 4301.897 | 25811.382
44 | Supplying, fixing, connecting, testing and commissioning of mirror light luminaire with 1 x 13 watt complete with electronic ballast, lamp including connection etc. complete as required similar to Philips cat no. FWZ301 | 9 | Each | 521.7875 | 4696.0875
45 | Supply, installation, connecting, testing and commissioning of illuminated exit sign with 1 x 8 watt FTL lamp including providing maintenance free batteries & charger capable of working for 2 hr duration mounted on recessed/ ceiling/wall complete with the approved EXIT self adhesive labels as per site requirement as required similar to Prolite cat. PEM 108 E/M RM. | 3 | Each | 6145.1113 | 18435.3338
46 | Supply, installation, connecting, testing and commissioning of Motion sensor including all wiring in the existing conduits required similar to Philips cat no. OCCU Switch | 6 | Each | 9083.3 | 54499.8
47 | Supplying and fixing of round shaped fan box fabricated out of 16 SWG sheet steel and 12mm M.S. bar hook duly covered with 3mm thick hylam sheet in white colour of suitable size with C.P. brass screws and making the hole in centre of plate etc. as required. | 19 | Each | 60 | 1140
M.V. PANELS/ DISTRIBUTION BOARD
48 | Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor mounted totally enclosed , extensible on both sides, switch board suitable for use on 415 Volts 3-phase, 4 wire, 50 Hz system having required fault capacity, housed with incoming and outgoing, Aluminium bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. (for UPS)
INCOMER:-
1 Nos. 200 Amps. 4P MCCB(25 KA) with electronic releases.
1 Set phase indication lights (R, Y, B)
1 No. Volt Meter (digital type) with inbuilt VSS & control fuses.
1 No. 0-200 Amp. Ammeter (digital type) with inbuilt ASS
BUS BARS:-
200 Amps. 4P Aluminium bus bars (25 KA)
OUT GOINGS:-
| 10 Nos. 100/63 Amps. TPN MCCB(25 KA) with electronic releases. | 1 | Set | 130283.0643 | 130283.0643
49 | Design, supply at site, installation, testing & commissioning of 3-phase, 415 volt, 1500 RPM, 50 HZ, air-cooled, Diesel generator set of 160 KVA at 0.8 pf lagging diesel engine alternator set mounted on common base frame in outdoor type acoustic enclosure , day tank capacity of 990 liters,m with AMF Panel,battery, batter charger, return fuel cooler, anti vibration mounting pads including residential silencer, engine alternator, pcc based auto start & synchronization set, safeties with accessories as per specification complete as required. Diesel engine shall conform to IS:10000 and alternator shall be self excited complete with AVR to IS:4722. | 1 | Set. | 963349.2 | 963349.2
METERING PANEL
50 | Supply, Installation, testing and commissioning of 11 KV HT metering panel board suitable for indoor installation for use on 11 KV 50 C/S earthed system including CTs and PTs complete with connections etc as required.
a) | 3 - Nos. PT's 11KV /Rt.3 /110V/Rt 3 cast resin type.
b) | 3 - Nos. CTs – 200/5A class -1or as per state electricity board
c) | 2 sets of HRC fuses with fuse base (H.T. fuse - 1 A & LT fuse 2-6 A)
d) | Bus link Fuses with fuse base
e) | 2 Nos. indoor cable end box for 3C x 240 Sq.mm. 11 KV aluminium conductor XLPE cable (Incoming & outgoing Cables)
f) | 1 No. Electronic Digital trivector meter 200/5A accuracy class-1.0 or as per state electricity board | 1 | Set | 195000 | 195000
Note:
The supplier/ contractor shall get tested and get approvals of the metering panels as well as equipments including their sealing etc. from state electricity board as required.
TRANSFORMER
51 | Supply , Installation, testing & commissioning of outdoor type 160 KVA copper wound 11/0.433 KV, 50 C/S, Delta star connected VCC oil type outdoor type transformer with OFF load circuit tap changer, minus 10% to plus 5% on HT side in steps of 1.25% complete as required. | 1 | Each | 382846.7064 | 382846.7064
HT PANEL BOARD
52 | Supply Installation testing and commissioning of extendable type HT panel board suitable for indoor installation for use on 11 KV 50 C/S earthed system having a symmetrical breaking capacity of 350MVA for 1 Sec. at 11 KV comprising triple pole VCB. Panel shall be equipped with following accessories as per specifications and schematic drawing.
Panel shall be comprising of:
1- Metal Clad housing with track having 630A TP integral VCB with Electric operated draw out type mechanism (spring charged motor - 230 VAC).
1- Set of air insulated copper bus bar & chamber.
1- Set of isolating plug and receptacle.
1- Set of Automatic safety shutter.
1- Set of breaker control switch (TNC)
2- Sets of CT's
CT- I -100/5A class 5P-10(15 VA)
CT- II - 100/5A class -1(15 VA)
1 - Digital Ammeter, selector switch. (Built-in)
1 - H.T. Cable box for 3C x 240 sq.mm aluminium conductor XLPE cable (11 KV earthed system).
1 - No. Tripping coil & closing Coil 24V DC/110V A.C.
1 - Set of ON/OFF/Trip & circuit healthy and phase indicating lights.
1- 3 element O/C, EF & SC relay (IDMTL & Hi - set) with required setting.
1- set Auxiliary relay.
1- Master trip relay
1-set Trip circuit supervision
| 1-Restricted Earth fault relay | 1 | Set | 450000 | 450000
53 | Liaisoning for sanctioning of load from the state electricity board, including the cable laying from the nearest tap-off point, etc completely as required. | 1 | LS
54 | Supply, erection, testing & commissioning of 230 V, single phase, 2 wire, A.C. to 24V D.C. 180 AH sealed maintenance free batteries with semiconductor/ IGBT (half wave rectifier) with auto-manual trickle boost facility battery charging units complete including 1 No. Distribution board having 63 Amps DP MCB incomer and 12 No. 16/ 20 Amps DP MCBs (D.C. duty) as outgoing complete as required as per technical specifications. | 1 | Set | 140000 | 140000
55 | Supplying and fixing of non-skid rubber mat 20mm thick and 900mm width as required including cutting to required lengths of approved make with Test Certificates for H.T. 11 KV panels. | 4 | Metre | 1500 | 6000
56 | Supplying and fixing of non-skid rubber mat 16mm thick and 900mm width as required including cutting to required lengths of approved make with Test Certificates for L.T. panels. | 20 | Metre | 1200 | 24000
57 | Supplying and fixing of fire bucket painted red and duly filled with sand conforming to IS: 2546-1974. | 12 | Each | 250 | 3000
58 | Supplying and fixing of MS stand suitable for supporting two buckets (Pedestal type) | 2 | Each | 1000 | 2000
59 | Supplying and fixing of MS stand suitable for supporting four buckets (Pedestal type) | 2 | Each | 1500 | 3000
60 | Supplying and fixing of shock restoration chart written in English and Hindi duly framed in as required. | 4 | Each | 800 | 3200
61 | Supplying and fixing of carbon dioxide fire extinguisher type 4 kgs. Capacity of approved make with wall mounting bracket as required conforming to IS: 2878/1976 (Push type). | 4 | Each | 4250 | 17000
62 | Supplying and fixing of first aid box as approved complete with standard kit as prescribed by Indian Red Cross. | 1 | Each | 500 | 500
L.T. CABLES
63 | Supply, laying and testing of under noted sizes of Aluminium conductor XLPE insulated PVC sheathed & sleeved armoured and overall PVC sleeved 1.1 KV grade power distribution cables conforming to relevant IS code and as per specification in ground (in existing trenches) through pipe or on wall / racks cable trays including dressing and clamping the cable with MS zinc passivated clamps etc. as required.
a) | 3.5 x 185 sq.mm | 100 | Metre | 1376.7213 | 137672.1343
b) | 3.5x 150 sq.mm | 100 | Metre | 1148.3808 | 114838.0823
c) | 4 x 25 sq.mm | 360 | Metre | 333.9365 | 120217.1302
d) | 4 x 16 sq.mm | 300 | Metre | 262.456 | 78736.7887
e) | 4 x 10 sq.mm | RO | Metre | 242.6003
64 | Supply and laying of under noted sizes of hume pipe NP-2 grade under the road including 1:3:6 cement concrete bed at 750-1200 depth cutting and making good the same as required as per technical specifications.
a) | 100mm dia | 20 | Metre | 287 | 5740
b) | 250mm dia | 50 | Metre | 394 | 19700
65 | Supply and fixing of steel work in position including clamps, frame work of flats, angle iron, channel with fabrication work including cutting, bending, welding, drilling bolting etc. as per design as required. One coat of primer and 2 coats of enamel paint of approved shade shall be provided. | 500 | Kg. | 80 | 40000
EARTHING
66 | Supply and fixing of following sizes of copper/GI strip in GI pipe from earth electrode including cost of GI pipe 'B' class as required.
a) | 50mm x 6mm copper | 20 | Meter | 1075 | 21500
T.V. , TELEPHONE SYSTEM & LAN SYSTEM
67 | Providing, laying, connecting and testing of multi-core telephone armoured cable of conductor size 0.63mm dia annealed copper conductor PVC insulated PVC sheathed jelly filled (as per DOT specification) cable along wall or ceiling or through existing pipe.
a) | 20 Pair telephone cable | 200 | Metre | 224.9939 | 44998.7711
b) | 5 Pair telephone cable | 80 | Metre | 95.9245 | 7673.9574
68 | Providing, fixing connecting and testing of under noted size of solderless telephone tag block Krone make in surface/recess in wall required size of M.S. box with hinged lockable cover duly stove enamel painted.
a) | 5 pair tag block | 2 | Each | 1226.417 | 2452.834
b) | 30 pair tag block | 1 | Each | 1870.6843 | 1870.6843
c) | 200 pair tag block | RO | Each | 5966.448
69 | Providing and laying of 80mm dia medium class GI pipe including all fixing accessories concealed or surface as required. | 20 | Metre | 623.4739 | 12469.4772
70 | Supplying and fixing M.S. box with Phenolic laminate plate 4- way splitter box for TV antenna complete as required. | 1 | Each | 150 | 150
71 | Supplying and fixing M.S. box with modular type data/ computer (RJ-45) outlet complete as required. | 22 | Each | 354.318 | 7794.996
72 | Providing, laying, connecting and testing of data/ computer Cat-6 cable along wall or ceiling or through existing pipe, including penta scanning documentation etc as required. | 880 | Metre | 11 | 9680
73 | Supplying and fixing of 450 x 450 x 150 M.S. box with Phenolic laminate plate of 16 SWG M.S. Sheet with hinged door cover for mounting TV amplifier including wooden base plate complete as required. | 1 | Each | 500 | 500
EXTERNAL LIGHTING
74 | Supplying, installation, testing and commissioning of L.T. panel fully compartmentalized cubical type sheet clad floor mounted totally enclosed , extensible on both sides, switch board suitable for use on 415 Volts 3-phase, 4 wire, 50 Hz system having required fault capacity, housed with incoming and outgoing, Aluminium bus bars with current rating of 0.8 Amp/sq.mm, interconnection etc. with indication lamps, accessories etc, as required as per specification and schematic diagram as required. (Street lighting Panel)
INCOMER:-
1 Nos.100 Amps. TPN MCCB(25 KA) with electronic releases.
1 Set phase indication lights (R, Y, B)
1 No. Volt Meter (digital type) with inbuilt VSS & control fuses.
1 No. 0-200 Amp. Ammeter (digital type) with inbuilt ASS
BUS BARS:-
200 Amps. TP&N Aluminium bus bars (25 KA)
OUT GOINGS:-
8 Nos. 63A TPN, MCB (10KA).
4 Nos. 24 Hr Timer Switch
| 4 Nos. 63A TPN contactor | 1 | Set | 130143.769 | 130143.769
75 | Supply, fixing, testing & commissioning of the Gate Lighting Fixture equivalent to Philips Cat. No. Metronomis including 1 no. 70 watt SON-T lamp along with ballast, necessary brackets, including connections 3 m extruded aluminium column as required. | 2 | Each | 19926.0275 | 39852.055
76 | Supply, fixing, testing & commissioning of the Security Lighting Fixture wall mounted equivalent to Philips Cat. No. Halolie NG QVR 135 including 1 no. 500 watt Halogen lamp along with ballast, necessary brackets, including connections as required. | 19 | Each | 831.615 | 15800.685
77 | Supply, fixing, testing & commissioning of the Landscaping Lighting Fixture equivalent to Pierlite Cat. No. LED Bollard including 1 no. 3 watt LED lamp of approved shade along with ignitor, necessary brackets, including connections as required. | 25 | Each | 12044.6875 | 301117.1875
SPLIT UNIT AIRCONDITIONERS
78 | Hi Wall Unit
Providing, fixing, testing and commissioning high wall mounted split unit airconditioners with evaporator with fan with motor, cooling coil, filter, all enclosed in decorative plastic casing, condenser with hermatically sealed rotary compressor, condenser coil, propeller fan with motor, cordless remote control, as per standards, requirement and drawings.
a) | 2.0 Tons | 13 | Nos. | 37263.75 | 484428.75
79 | Refrigerant Piping
Providing and fixing of copper soft / hard refrigerant piping along (Circuit length) with cable control cabling and earthing shall be insulated with 9 mm thick pipe section of nitrile rubber and finished with nitrile tape, running all pipe as sloted channel, hanger at interval of 2 meters.
A. | 2.0 TR Hi-Wall Split unit. | 130 | Rm | 657.0993 | 85422.909
80 | Drain Piping
Supply and installation of PVC drain piping along with U-traps, sockets, hanging supports etc. insulation the same with 6 mm nitrile rubber of density 60 - 80 kg/m3 insulation and finally finished with nitrile tape as per standard and specifications.
a) | 32 mm dia | 60 | Rm | 176.9114 | 10614.681
b) | 25 mm dia | 120 | Rm | 151.6383 | 18196.596
MV CABLES
81 | Supplying, laying, of following sizes XLPE, 11 KV earthed cable in existing open structure/ hume pipe including in vertical formation as per technical specification and complete as required. (The payments of cable length shall only be made upto gland in panel on both sides not for loop and connection cables of approximate length upto 2 metres either sides.)
a. | 3Cx120 Sq.mm. | 100 | Metre | 1834.6133 | 183461.3282
82 | Providing and fixing UPVC pipes as per IS:13592 suitable for 6 Kg/ sq cm pressure, including all fittings with accessories i.e bends, junctions, cowls, offsets, PVC pipe clips/holders etc. and jointing with rubber rings and cement solvent complete as per manufacturer's specifications with excavation, refilling and disposal of surplus earth, including cutting holes in walls and floors ,wherever required and making good the same, complete as directed by the Engineer-in-Charge.
a. | 110 sq.mm outer dia | RO | Metre | 578
b. | 200 sq.mm outer dia | 100 | Metre | 1686 | 168600
| TOTAL (PART D - ELECTRICAL WORKS) |  |  |  | 6668586.7139