CONSTRUCTION OF 2 DOCTOR’S DISPENSARY FOR ESIC AT KULASEKARAPURAM, KOLLAM

TENDER  DOCUMENT

FOR

CONSTRUCTION OF 2-DOCTOR’S DISPENSARY AT KULASEKARAPURAM, KOLLAM, FOR ESIC

PART-III PRICE  BID

TENDER NO. HLL / ID / 13 / 55

JULY- 2013

HLL LIFECARE LIMITED. INFRASTRUCTURE DEVELOPMENT DIVISION

1

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

| INDEX |  |  |
| --- | --- | --- |
| SL.NO | DETAILS | PAGE |
| 1 | Specifications | 3 |
| 2 | List of Approved Make of materials | 19 |
|  | a) Civil Works b) Plumbing works c) Electrical works |  |
| 3 | Table For Weight (Kg/m) For Reinforcement Bars | 31 |
| 4 | Bill Of Quantities | 32 |
| 5 | Summary Sheet | 33 |

2

HLL LIFECARE Ltd

SPECIFICATIONS

GENERAL

The quoted rates for various items in the tender shall be inclusive of all the additional conditions  and particular specifications and for adherence  to all these conditions  and specifications,  no  extra  payment  shall  be  made  to  the  contractor.  Any  infringement and/or  breach of  these specification  and condition(s) etc.  shall render  the  contractor liable to action(s) under various clauses of the contract and such action stipulated  in conditions therein.

“A” 	SPECIFICATIONS

1.   The  Contractor  shall  maintain  safe  custody  of  materials  brought  to  the  site.  The Contractor shall also employ necessary watch and ward establishment for the work and other purposes as required at his own cost.

2.   For Cement and Steel and other materials, as prescribed, the quantities brought at site shall be entered  in the  respective material  at site  accounts  and  shall be treated  as issued for maintenance of daily consumption.

3.   The procurement of Cement and Reinforcement Steel, and, their issue and consumption shall be governed as per conditions laid down hereunder.

3.1. 	Cement

3.1.1.   The contractor shall procure 43 grade cement Conforming to IS: 8112 / IS: 1489, as required  in the work, from reputed manufactures  of cement such as A.C.C. Ultra   Tech,   India   Cements,   Malabar   Cement,   Ramco   Cement,   Cement Corporation of India or equivalent holding license to use ISI certification mark for their  product  whose  name  shall  be  got  approved  from  Engineer-in-Charge. Supply of cement shall be taken in 50 kg bags bearing manufacture’s name and ISI marking. Samples of cement arranged by the contractor shall be taken by the Engineer-in-Charge and got tested whenever felt necessary in accordance with provisions of the relevant BIS codes. In case test results indicate that the cement arranged by the contractor does not conform to the relevant BIS codes, the same shall stand rejected and shall be removed from the site by the contractor at his own cost within a week’s time of written order from the Engineer-in-Charge to do so.

3.1.2.   The Cement shall be brought at site in bulk supply of approximately 20 tonnes or as decided by the Engineer-in-Charge.

3.1.3.   The cement godown of the capacity to store about 500 bags of cement or as decided by the Engineer-in-Charge shall be constructed by the contractor at site of work for which no extra payment shall be made. Double lock provision shall be made to the door of the cement godown. The keys of one lock shall remain with the Engineer-in-Charge or his authorized representative and the key of other lock

3

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

shall remain with the contractor. The contractor shall facilitate the inspection of the cement godown by the Engineer-in-Charge or his authorized subordinate at any time.

3.1.4.   The contractor shall supply free of charge the cement required for testing. The cost of tests shall be borne by the contractor/ Department in the manner indicated below:

i. 	By  the  contractor,  if  the  results  show  that  the  cement  does  not conform to relevant BIS codes.

ii. 	By the Department, if the results show that the cement conforms to relevant BIS codes.

3.2. 	Steel

3.2.1.   The contractor shall procure steel reinforcement bars conforming to relevant BIS codes from main producers like SAIL, TISCO, VSP, IISCO etc. as approved by the Ministry of Steel. In cases when the contractor is required  to procure steel reinforcement  bars  conforming  to  relevant  BIS  codes  from  other  than  main producers such as secondary producers or re-rollers having BIS License, can be done with prior  approval  of the Engineer-in-Charge. The procurement of TMT Bars conforming to relevant BIS codes shall be made from main producers and secondary producers having BIS License with prior approval of the Engineer-in- Charge. The contractor shall have to obtain and furnish test certificates  to the Engineer-in-Charge.  The  contractor   shall  have  to  obtain   and   furnish   test certificates to the Engineer-in-Charge in respect of all supplies of steel brought by him  to  the  site  of  work.  Samples  shall  also  be  taken  and  got  tested  by  the Engineer-in-Charge as per the provisions in this regard in the relevant BIS codes. In case the test results indicate that the steel arranged by the contractor does not conform to BIS codes, the same shall stand rejected and shall be removed from the site of work within; a weeks’ time of written order from the Engineer-in-Charge to do so.

3.2.2.   The steel reinforcement shall be brought to the site in quantity of lots as approved by the Engineer-In-Charge.

3.2.3.   The steel reinforcements shall be stored by the contractor at site of work in such a way as to prevent distortion and corrosion and nothing extra shall be paid on this account. Bars of different sizes (diameters) and lengths shall be stored separately to facilitate easy counting and checking.

3.2.4.   For  steel  procured  from  main  producers,  for  checking  nominal  mass,  tensile strength,  bend  test, etc.  specimen of  sufficient  length  shall be cut from  each diameter of the bar at random at frequency not less than that specified below. In case of works costing more that 2 Crores and when the steel is procured from other  than  main  producers,  additional  tests  such  as,  retest,  re-bend  test, elongation test, proof stress may also be conducted

4

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

| Size (Diameter) of bar | For consignment |  |
| --- | --- | --- |
|  | Below 100 tonnes | Over 100 tonnes |
| Under 10mm dia | One sample for each 25 tonnes or part thereof | One sample for each 40 Tonnes or part thereof |
| 10mm to 16mm dia | One sample for each 35 tonnes or part thereof | One sample for each 45 Tonnes or part thereof. |
| Over 16mm dia | One sample for each 45 tonnes or part thereof. | One sample for each 50 Tonnes or part thereof. |

3.2.5.   The contractor shall supply free of charge the steel bars required for testing. The cost of tests shall be borne by the contractor/ Department in the manner indicated below:

1. 	By the contractor, if the results show that the steel does not conform to relevant BIS codes.

2. 	By the Department, if the results show that the steel conforms to relevant

BIS codes.

3.2.6.   Coefficient of weight i.e. the weight per unit length of the steel procured by the contractor  shall  be  ascertained  at  site  before  using  it  and  certified  by  the Engineer-In-Charge. In case weight per unit length is beyond the rolling margin as laid down in the BIS: 1786, the steel will be rejected and shall be removed from the site of work within; a weeks’ time from the date of written order from the Engineer-in-Charge to do so. In case weight per unit length  is more than the standard coefficient of weight for the diameter, but is within the rolling margin, then the payment shall be made as per the standard weight per unit length, and, where the weight per unit length is lesser than the standard coefficient of weight for the diameter, but is within the rolling margin, the payment shall be restricted with respect to the actual weight per unit length of the diameter.

3.3. 	The standard sectional weights referred to in standard  table under para 5.3.3., page 75 of the revised CPWD Specifications 2002 for Cement Mortar, Cement Concrete  and  RCC  works,  are  to  be  considered  for  conversion  of  length  of various sizes of  Steel Reinforcement  bars into weight and are reproduced below for ready reference.

| SIZE (mm) | WEIGHT (Kg/M) | SIZE (mm) | WEIGHT (Kg/M) |
| --- | --- | --- | --- |
| 6 | 0.222 | 20 | 2.467 |
| 8 | 0.395 | 22 | 2.985 |
| 10 | 0.617 | 25 | 3.856 |
| 12 | 0.888 | 28 | 4.836 |
| 16 | 1.579 | 32 | 6.316 |
| 18 | 1.999 | 36 | 7.986 |

3.4. 	Steel and Cement brought to site and remaining unused shall not be removed from site without the written permission of the Engineer-In-Charge.

5

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

3.5. 	Cement used in Ready Mix Concrete shall be evaluated based on the certification by the in-charge of the RMC Plant in accordance with design approved by the Engineer-In-Charge.

4.   Some restrictions  may be  imposed by the  security staff  etc.  on  the  working and/  or movement of labour, materials etc. and the contractor shall be bound to follow all such restrictions/ instructions and nothing extra shall be payable on this account.

5.   The contractor shall comply with proper and legal orders and directions of the local or public authority or municipality and abide by their rules and regulations and pay all fees and charges which he may be liable and nothing extra shall be payable on this account. The work shall be carried out without infringing on any of the local Municipal Bye-Laws.

6.   The contractors shall given a performance test of the entire installations as per standard specifications before the work is finally accepted and nothing extra what so ever shall be payable to the contractor for the tests.

7.   The contractor shall engage licensed plumber for sanitary, water supply, drainage work and also get all the materials and system (including the materials supplied if any, by the department)  tested  by  the  Municipal  Authority,  Whenever  required,  at  his  own  cost including testing fees, transport etc. according to Municipal by Laws. The contractor shall produce necessary certificate from the Municipal Authorities  after completion of work. Nothing extra will be paid on this account. The Contractor shall execute the guarantee for  removal  of  defects  after  completion  in  respect  of  water  supply  and  sanitary installation.

8.   The water supply sanitary installation and drainage work shall be carried out in a manner complying in all respects with the requirement of relevant by laws of the local municipal authority of the place at no extra cost of the department.

9.   The rate for every item of work to be done under this contract shall be for all heights, depths,  lengths  and widths of the structure (except where specially mentioned  in the item) and nothing extra will be paid on this account.

10. The contractor shall take all precautions to avoid all accidents by exhibiting necessary caution boards such as day and night boards, speed limit boards and flags, red lights and providing barriers etc. He shall be responsible for all damages and accidents caused due  to  negligence  on  his  part.  No  hindrance  shall  be  caused  to  traffic  during  the execution of work. Nothing extra shall be paid on this account.

11. The contractor will work in close liaison, during the works, with other contractors of water supply, sanitary, drainage arrangements, electrical installation and any other works and adjust his work plan accordingly.

12. Other Taxes and Royalties

12.1. 	Income  Tax  and  surcharges  over  Income  Tax  etc.  at  the  rates  fixed  by  the Ministry of finance, Government of India, shall be deducted from all the running and final bills of the contractor. Should there be any increase in rate of Income Tax and surcharge  during  execution  of  the  contract,  the  same  shall  be  payable  by  the contractor.

6

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

12.2. 	Works Contract Sales Tax as prevalent as per statutory orders of State/Central Government and  shall  be  charged  on  gross  value  of  all  the  bills  and  shall  be recovered from each bill of the contractor as ‘works contract sales tax’. Should there be  any  increase  in  rate  of  Works  Contract  Sales  Tax  during  execution  of  the contract, the same shall also be payable by the contractor.

12.3. 	Royalty shall have to be paid by the contractor  on all materials such as stone, bricks, boulders, metal, shingle, bajri, stone aggregate, coarse sand and fine sand etc. or any other materials used for the execution of the work direct to the Revenue Authority  of  the  District/State  Govt.  concerned.  The  contractor  shall  obtain  “No Demand” certificate from the District/State Govt. authority concerned before the final bill is paid, failing which necessary recovery will be effected at the applicable rates in the final bill.

13. Secured Advance:

13.1. 	Secured advance on bricks, stone, stone aggregate brought at site for use in the work shall be paid only after receipt of satisfactory test results from the laboratory and provisions under rules.

13.2. 	Secured advance on steel doors, steel windows, etc. shall be paid only after the

Engineer-in-Charge  has  personally  verified  that  the  materials  brought  at  site  of work, for use in work, conforms to the sample approved by him.

13.3. 	Secured  advance  whenever  admissible  on  water  supply,  sanitary  installation materials and fittings shall be allowed only after the Engineer-in-Charge has verified that  materials  brought  at site  have been  checked by him  personally and  are  in conformity with the samples approved by him.

13.4. 	Secured advance for terrazzo tiles shall be paid only after satisfactory results are

received from the laboratory.

*************

B.  ADDITIONAL SPECIFICATIONS

1.   GENERAL

1.1. 	The  Work  shall,  in  general,  conform  to  the  CPWD  Specifications.  The  CPWD specifications shall mean CPWD Specifications – 1996 Vol. 1 to VI with up-to-date correction slips and Revised CPWD Specifications 2002 for Cement Mortar, Cement Concrete and RCC works which supersede Chapter 3,4 & 5 of CPWD specifications

1996 Vol.II.

1.1.1.   Should there be any difference between the specifications mentioned above and  the  specifications  given  in  the  schedule  of  quantities,  the  later  shall prevail.

1.1.2.   If the specifications for any item are not available in the CPWD Specifications cited above, relevant BIS Specifications should be followed.

1.1.3.   In case BIS Specifications are also not available, the decision of Engineer-in- Charge given in writing based on acceptable sound engineering practice and local usage shall be final and binding on the contractor.

7

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

1.1.4 		Articles classified as first quality by the manufacturer shall be used unless otherwise specified.

1.2. 	The  work  will  be  carried  out  in  accordance  with  the  architectural  drawings  and structural drawings to be issued by the Engineer-in-Charge. The structural and architectural drawings shall have to be properly correlated before executing the work.

1.2.1.   Incase  of   any   difference   noticed   between   Architectural   and   Structural drawings, the contractor shall obtain final decision in writing of the Engineer- in-Charge.

1.2.2.   In case of any discrepancy in the item given in the schedule of quantities appended with the tender and architectural drawings relating to the relevant item, former shall prevail unless otherwise given in writing by the Engineer-in- Charge

1.3. 	For items where so desired, samples shall be prepared before starting the particular items of work for prior approval of the Engineer-in-Charge and nothing extra shall be payable on this account.

1.4. 	Materials  brought  at  site  of  work  shall  not  be  used  in  the  work  before  getting satisfactory  Mandatory  test  results.  For  details,  relevant  provisions  in the  CPWD specification shall be referred to.

1.4.1.   Wherever it is desired to procure factory-made materials, such factory-made materials  shall  be  procured  from  reputed  and  approved  manufacturers  or through  their  authorized  dealers.  The contractor  shall  obtain  the  approval from  the  Engineer-in-Charge  of  such  firms  prior  to  procurement  of  such factory-made materials. The Engineer-in-charge may, at any stage,  inspect such factories/ manufacturing units. The contractor shall have no claim if the factory made materials brought  to the site are rejected by the Engineer-in- charge in part or in full due to bad workmanship/ quality etc. even after the inspection of the manufacturing units.

1.4.2.   The manufactured materials brought at site of work shall, in general, conform to  the  relevant  specifications.  The source for  supply  of  the  manufactured materials shall be approved by the Engineer-in-charge. The contractor shall have no claim if the manufactured materials brought to the site are rejected by the Engineer-in-charge in part or in full due to bad workmanship/ quality etc.

1.4.3.   The preference amongst the various alternative materials available shall be as follows: -

(a) The materials shall be as per the Brand specified to be used in the work. (b)  If the Brand specified material is not available then the material shall be

ISI marked.

(c) If ISI marked item is not available then it should be from ISO certified

Company.

(d) If the ISI marked or ISO certified items are not available then the best available items in the market to be procured.

8

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S FOR ESIC AT KADAMBHANADU, KERALA

1.4.4.   Equivalents  for the  various materials  and  the materials  of  approved make shall be got approved from the Engineer-in-Charge of work in writing before using them on the work.

1.4.5.   The contractor shall maintain register for cement, paint and other registers as required by the Engineer-in –charge and those should be signed by the contractor or his authorized agents and the Asst. Project Engineer in charge of the work.

2.   The following modifications to the above specifications shall, however, apply.

2.1. 	Earth Work

2.1.1. 	During   excavation   and   trenching   work   etc.,   the   contractors   shall   ensure compliance to the guidelines in such matters laid down by the local body / bodies to ensure that there is minimum hazard to the operating personnels and users, minimum  inconvenience to  the  users, minimized  damage  to  the  underground plant/services of other utilities in a coordinated way, in the interest of public convenience and overall safety.

2.1.2. 	Any trenching and digging for laying sewer lines/ water lines/ cables etc. shall be commenced by the contractor only when all men, machinery’s and materials have been arranged and closing of the trench(s) thereafter shall be ensured within the least possible time.

2.1.3. 	Surplus excavated earth which is beyond the requirement of the H.L.L shall have to be disposed of by the contractor at his own cost beyond the municipal limits or at places identified by the local bodies or as directed by the Engineer-in-Charge after obtaining written permission of the Engineer-in-Charge and no payment will be made by the Department for such disposal of this surplus excavated earth.

2.1.4. 	The  contractor  shall,  at  his  own  expense  and  without  extra  charges,  make provision for all shoring, pumping, dredging or bailing out water,  if necessary, irrespective of the source of water. The foundation  trenches shall be kept free from water while all the works below Ground Level are in progress, without any extra payment.

2.2. 	Reinforced Cement Concrete Work & Plain Cement Concrete- General

2.2.1. 	Stone Aggregate.   Stone aggregate  to be used in the work shall be of hard broken stone to be obtained from source approved by Engineer-In-Charge and shall conform to the relevant provisions in the CPWD Specifications.

2.2.2. 	Fine Sand / Coarse Sand:  Fine sand / Coarse sand to be used in the work shall be obtained from sources approved by Engineer-In-Charge and shall conform to the relevant provisions in the CPWD Specifications.

2.2.2.1.   Where only one variety of sand is available, the sand will be sieved for use in finishing work to achieve the required particle size distribution as per CPWD Specifications in order to obtain smooth surface and nothing extra shall be paid to the contractor on this account.

9

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

2.2.3. 	Water: - It shall conform to requirements laid down in IS: 456-2000 and CPWD Specification

2.3. 	R. C. C. work (Design Mix Concrete) - Wherever the RCC work is specified to be done with  Design Mix Concrete,  the  particular  specifications,  as  applicable,  shall apply.

2.4. 	R.C.C.Work  (Nominal  mix  concrete)- Water-Cement  Ratio:  -  For  RCC Works, wherever nominal mix of concrete is stipulated in the items for work, for maintaining proper quality and durability requirements of the structure, maximum water-cement ratio shall be restricted to 0.55. If in normal course of work, the required workability is not  achieved;  suitable  plasticizers/  admixtures  may  be  used  for  improving  the workability of concrete with  the  approval  of Engineer-in-Charge for which nothing extra shall be paid.

2.5. 	Non-destructive  Testing  for  Concrete/R.C.C  Work:  -  The  Engineer-in-charge shall, at  his  discretion,  get the  non-destructive  testing  (Such as Ultrasonic  Pulse Velocity Test etc.) done and the Contractor shall make all necessary arrangements for getting such tests done and make good the same after the test, for which nothing extra shall be paid. The results of such tests shall be binding on the Contractor. In case of non-conformity of the test to the standards, the contractor shall be liable to re-do the concrete work at his cost including the cost of test, subject however, to the acceptability of the work as laid down in the mandatory test defined in the relevant CPWD specifications.

2.6. 	Cement slurry, if any, added over base surface (or) for continuation of concreting for better bond is deemed to have been in built in the items (Unless other wise explicitly stated)   and  nothing   extra  shall  be  payable  (or)  extra  cement  considered  in consumption on this account.

2.7. 	Centring and Shuttering For R.C.C Work:- The concrete surface shall be free from honey combing, offsets, superfluous mortar, cement slurry and foreign matter. The formwork shall be assembled in such a way as to facilitate removal of their parts in proper sequence without any damage to the exposed cement concrete surfaces and corners etc. The contractor shall keep skilled staff for special care and supervision to check the formwork and concreting so that every member is made true to its size, shape,  level  and  alignment  so  that  it  does  not  result  in  any  deformation,  snug, buldges etc. The contractor shall also take suitable precautionary measure to prevent breaking and chipping of corners and edges of completed work until the building is handed over. The size of shuttering plates for slabs shall not be less than 0.6mx0.9m in  general.  However,  contractor  has  to  provide  tape  or  wooden  fillets  or  rubber gaskets to seal the joint properly to get smooth surface. Further shuttering shall be of such quality that there are no undulations  and surfaces will be fairly even and no extra thick ceiling plaster shall be permitted to make the surface even. Any honey- combed or poorly formed concrete shall be repaired with polymer concrete of any suitable   design  by  the   Contractor   at  his  own  cost,  in  accordance  with   the specifications laid down in hand book of Repairs and Rehabilitation of RCC Buildings by CPWD.

2.8. 	BRICK WORK: - Bricks used in the work shall be of class designation specified  to be obtained from kilns approved by Engineer-In-Charge. In all other respects they shall conform to the provisions in CPWD specifications.

10

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S  ESIC AT KADAMBHANADU, KERALA

2.9. 	STONE WORK: Stone used for stone masonry work shall be hard granite/ basalt/ quartz  stone/sand  stone  to  be  obtained  from  quarries  approved  by  Engineer-In- Charge and shall conform to the relevant provision in the CPWD specifications.

2.10. 	All above materials  like stone  aggregates,  coarse sand, fine sand, Bricks, Surkhi, Stone etc. confirming to the CPWD specifications  to be brought  from the sources approved by Engineer-In-Charge. In case, at any stage during execution of work, the material from the approved source being not available or otherwise, and, is required to be arranged from other sources conforming to relevant CPWD specifications and duly approved of Engineer-in-charge, involving extra lead etc. nothing extra shall be paid on this account.

2.11. 	WOOD WORK: - Timber required  for manufacture  of chowkhats  and shutters for doors, windows, ventilators, and partitions etc. in the work shall be kiln seasoned and preservative treated. The Timber shall be kiln seasoned before applying preservative treatment. The rate quoted for various items shall be inclusive of kiln-seasoning and preservative treatment of wood. The wood used in the work shall conform to the provisions in the CPWD Specifications for works.

2.12. 	FACTORY MADE SHUTTERS etc.:- The shutters for doors, windows & ventilators, and, chowkhats etc. shall be factory made and obtained from suppliers approved by the Engineer-in-charge.

2.13. 	STEEL WORK:- All steel doors, steel windows, steel ventilators, wire gauge, steel glazing, steel grill shall be according to the Architect’s detailed drawings and factory made and obtained from approved suppliers.

2.13.1. 	In  the  case  of  composite  steel  windows  the  rates  shall  include  the  cost  of coupling mullion and transom etc. Where windows with inside openable shutters are  fixed  along-with   windows  with  shutters  openable   outside,  such  inside openable  windows  shall  be  fitted  with  suitable  friction  hinges  and  openable outside with  box  type hinges, lever handles  or otherwise  as approved by the Engineer-in-Charge of the work. For such windows, cement concrete blocks of size 15cmx 10cmx 10cm shall be provided. Nothing extra shall be paid on this account.

2.13.2. 	In  the  case  of  steel  windows  and  doors,  steel  glazing,  wire  gauge  steel ventilators,  rolling shutters, grills etc. an approved  quality-priming  coat of zinc chromate shall be applied over and above shop coat of primer. Nothing  extra shall be payable for providing shop-coat primer.

2.14. 	Sanitary and Water supply installations

The contractor shall engage  licensed plumber for sanitary, water supply, drainage work  and  shall  be  carried  out  in  a  manner  complying  in  all  respects  with  the requirement of relevant by laws of the local municipal authority. The Contractor shall give a guarantee to the effect that the work shall remain structurally stable and shall guarantee against faulty workmanship, finishing, manufacturing defects of materials and leakages etc. The Contractor shall furnish a Guarantee Bond, as per prescribed format. The Guarantee Period shall be for 10(Ten) years.

2.15. 	Approval of sample work of repetitive/ typical nature prior to general execution of work shall be as enumerated hereafter.

11

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

2.15.1.1. Samples of typical portion of the works of repetitive nature such as typical room, toilet room, or any other  work shall be prepared by the contractor under the directions and to the satisfaction of Engineer-in-Charge and got approved from him in writing before the commencement of these items for the entire work.

2.15.1.2. The work shall be so arranged to be carried out that the requirement for preparation of samples are observed and fulfilled without any detriment to the general progress of work. In other words, this will not be allowed to have any effect  on the general  progress  of  work or on any of  the terms and conditions of the contract. No claims of any kind whatsoever including the claim of extension of time will be entertained due to the incorporation of this requirement.

2.16. 	TEST RESULTS & RELATED ASPECTS

2.16.1. 	Normally, part-rate  payment shall be allowed in the running  account bills only if the materials conforming to the CPWD specifications for works as mentioned  in  the  work  are  used  and  test  results  are  awaited  by  the Engineer-in-Charge.

2.16.2. 	The  Engineer-in-Charge of  work  shall check  the  test  results  and  satisfy himself before allowing any payment in the running/final bill.

2.17. 	WATER PROOFING: -

2.17.1. 	Treatment for roof surfaces: - The treatment of Roof Surfaces, wherever done with integral cement based compound (Brick-coba), the particular specifications shall be applicable.

2.17.2. 	The Contractor shall associate himself with the specialized firm, to be approved by  the  Engineer-in-charge,  for  execution  of  water  proofing   treatment.   The contractor shall furnish a Guarantee Bond, as per prescribed format, from the specialized firm and duly counter-signed by the contractor as a token of overall responsibility. The Guarantee Period shall be for 10(Ten) years.

2.17.3. 	Ten percent of the cost of items of water proofing treatment for sunken floors and on roofs would be retained as guarantee to watch the performance of the work done. However half of the amount withheld would be released after (5) five years, if the performance of the work done is satisfactory. If any defect is noticed during the guarantee period, it should be rectified by the contractor within seven days, and if’ not attend to, the same will be got done from another agency at the risk and cost of the contractor. However this security deposit can be released in full, if bank guarantee of equivalent amount for 10(ten) years after completion of maintenance period is produced and deposited with the HLL.

C.  PARTICULAR SPECIFICATIONS

1.1. 	R. C. C. WORK (DESIGN MIX CONCRETE)

12

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

1.1.1. 	The  RCC  work  shall  be  done  with  Design  Mix  Concrete  unless  otherwise specified. In the nomenclature of items, wherever letter M has been indicated, the same shall imply for  the Design Mix Concrete.  For  the  nominal mix in RCC, CPWD specification shall be followed. The Design Mix Concrete will be designed based on the principles give in IS: 456, IS: 10262 and SP 23. The contractor shall design mixes for each class of concrete indicating that the concrete ingredients and proportions will result in concrete mix meeting requirements specified. The cement shall be actually weighed, as presumption of each bag having 50kg shall not be allowed. In case of use of admixture, the mix shall be designed with these ingredients as well. The specification mentioned therein below shall be followed for Design Mix Concrete.

1.1.2. 	Admixture: - Wherever required, admixtures of approved quality shall be mixed with concrete to achieve the desired workability within specified  water cement ratio.  The  admixture  shall  conform  to  IS:  9103.  The  chloride  contents  in  the admixture shall satisfy the requirement of BS: 5075. The total amount of chlorides in  the admixture mixed concrete shall also satisfy the requirements of IS: 456-

2000.

1.1.2.1. 	The  contractor  shall  not  be  paid  anything  extra  for  admixture  required  for achieving desired workability without any change in specified water cement ratio for RCC/CC work.

1.1.3. 	Grade of concrete: - The characteristic compressive strength of various grades of concrete shall be given as below: -

| Sl. No. | Grade / Designation | Compressive strength on 15cm cubes min 7days (N/mm2) | Specified characteristic compressive strength at 28 days (N/mm2) | Minimum cement content (kg per cum) | Maximum water cement ratio |
| --- | --- | --- | --- | --- | --- |
| (i) | M 25 | As per Design | 25 | 360 | 0.50 |
| (ii) | M 30 | As per Design | 30 | 400 | 0.45 |
| (iii) | M 35 | As per Design | 35 | 410 | 0.45 |

1.1.3.1. 	The Concrete mix will be designed for minimum workability as specified in para 7 of IS-456-2000. Workability of Concrete (Unless otherwise specified elsewhere or as decided by Engineer- in-charge.

| Placing Conditions | Degree of Workability | Slump (mm) |
| --- | --- | --- |
| (1) | (2) | (3) |
| Lightly reinforced sections in, slabs, beams, walls columns | Low | 25-75 |
| Heavily reinforced section in slabs, beams, walls, columns | Medium | 50-100 |
| Pumped concrete | Medium | 75-100 |

1.1.3.2. 	In the designation of concrete mix letter M refers to the mix and the number to the specified   characteristic   compressive   strength   of   15cm-Cube   at   28   days expressed in N/mm2.

13

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

1.1.3.3. 	It  is  specifically  highlighted  that  in  addition  to  the  above  requirements  the maximum cement content for any grade shall be limited to 450kg/ cubic metre.

1.1.3.4. 	The  Minimum  /  Maximum  cement  content  for  design  mix  concrete  shall  be maintained as per the quantity  mentioned  above. Even in the case where the quantity  of  cement  required  is  higher  than  the  minimum  specified  above  to achieve desired strength based on an approved mix design, nothing extra shall become payable to the contractor. In case of pile work, cement content will be as specified (Minimum 400kg/Cum of concrete).

1.1.3.5. 	The  concrete  design mix with  or  without  admixture  will be carried out by the contractor through laboratories/ Test houses of repute as decided by EE/SE.

1.1.3.6. 	The various ingredients for mix design/ laboratory tests shall be sent to the lab/ test houses through the Engineer in charge immediately after award of work and the samples of such aggregate sent shall be preserved at site by the department. The admixture if used by contractor shall be at his own cost without any extra payment.

1.1.4. 	The Contractor shall submit the mix design report from any of above approved laboratories for approval of Engineer in charge within 30 days from the date of issue of letter of acceptance of the tender. No concreting shall be done until the mix design is approved.

1.1.5. 	In case of change of source or characteristic properties of the ingredients used in the  concrete  mix  during  the  work,  a  revised  laboratory  mix  design  report conducted at laboratory established at site shall be submitted by the contractor as per the direction of Engineer in charge.

1.1.6. 	Approval of Design Mix:-

The mix design for a specified grade of concrete shall be done for a target mean compressive strength Tck = Fck +1.65s

Where Fck = Characteristic Compressive Strength at 28 day

s = Standard deviation which depends on degree of quality control.

The degree of quality control for this work is “good” for which the standard deviation (s) obtained for different grades of concrete shall be as follows:-

| GRADE OF CONCRETE | FOR ‘GOOD’ QUALITY OF CONTROL |
| --- | --- |
| M – 25 | 5.3 |
| M -30 | 6.0 |
| M –35 | 6.3 |

1.1.6.1.  Out of the six specimen of each set, three shall be tested at seven days and remaining three at 28days. The preliminary tests at seven days are intended only to indicate the strength to be attained at 28days.

14

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

1.1.6.2.  All  cost  of  mix  designing  and  testing  connected  therewith  including  charges payable to the laboratory shall be borne by the contractor.

1.1.7. 	Batching, Mixing, Transportation, Placing, and, Compaction:

1.1.7.1.  The Concrete shall be sourced from on site batching and mixing plant conforming to IS: 4925, it shall have the facilities of presetting the quantity to be weighed with automatic  cut  off  when  the  same  is  achieved.  Transportation  and  placing  of concrete shall be with transit mixes and concrete pump respectively or with tower cranes depending upon site condition and nothing extra shall be paid. In certain places/ location  placing  of  concrete  may be  permitted  manually.  Accuracy  of measurement shall be as specified is IS - 456-2000.

1.1.7.2.  All  other  operations  in  concreting  work  like mixing,  Slump,  Laying/Placing  of concrete, compaction, curing etc. not mentioned in this particular specification for Design Mix of Concrete shall be as per Revised CPWD Specification 2002 for CM, CC and RCC work, IS- 456-2000 and Additional/Special Condition forming part of this tender document.

1.1.8. 	Preparation 	of 	Mixes 	As 	Per 	Approved 	Design 	Mix 	Conducting

Confirmatory Test at Field Lab.

1.1.8.1.  The contractor shall make the cubes of trial mixes as per approved Mix design at site laboratory for all grades, in presence of Engineer in charge using sample of approved materials proposed to be used in the work prior to commencement of concreting and get them tested in his presence to this entire satisfaction for 7 days and 28 days. Test cubes shall be taken from trial mixes as follows.

1.1.8.2.  For each mix, a set of six cubes shall be made from each of three consecutive batches.  Three cubes from each set of six shall be tested at age of 7 days and remaining  three  cubes  at  age  of  28  days.  The  cubes  shall  be  made  cured transported  and  tested  strictly in accordance with  specifications.  The  average strength of nine cubes at age of 28 days shall exceed the specified target mean strength for which design mix has been approved; the evaluation of test result will be done as per IS-456-2000.

1.1.9. 	Work Strength Test- Test Specimen

1.1.9.1.  Work strength  test shall be conducted in accordance with IS: 516 on random sampling. Each test shall be conducted on six specimens, three of which shall be tested at 7 days and remaining three at 28 days. Additional samples shall be prepared if required, as per direction of Engineer in charge for testing samples cured by accelerated method as described in IS: 9103.

1.1.10. 	Test Result of Sample

1.1.10.1.  The  test  results  to  the  sample shall  be  the  average  of  the  strength  of  three specimens. The individual variation shall not be more than +/-15 percent of the average. If more the test results of the sample are invalid. 90% of the total tests shall be done at the laboratory established at site by the contractor and remaining

15

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

10%  in  the  laboratory  of  Central  Designs  Organization,  CPWD  or  any  other laboratory as directed by the Engineer in charge.

1.1.11. 	Standard For Acceptance

1.1.11.1.  Standard of acceptance shall be same as specified in clause 16 of IS-456-2000

1.1.11.2.  In  order  to keep the  floor finish  as per  architectural  drawings  and  to provide required thickness of the flooring as per specification, the level of top surface of RCC shall be  accordingly adjusted  at  the  time of  its  centring,  shuttering  and casting for which nothing extra shall be paid to the contractor.

1.1.12. 	Measurement:- As per CPWD specifications.

1.1.13. 	Tolerance:- As per CPWD specifications.

1.1.14. 	Rate:-  The rate  includes  the  cost  of  materials  and  labour  involved  in  all  the operations described above except for the cost of centring, shuttering and reinforcement, which will be paid separately.

1.1.14.1.  In  case  of  actual  average  compressive,  strength  being  less  than  specified strength which shall be governed by para ‘Standard of Acceptance’ as above, the rate payable shall be worked out accordingly on prorata basis.

1.1.14.2.  In  case  of  rejection  of  concrete  on  account  of  unacceptable  compressive strength,  governed  by  para  ‘Standard  of  Acceptance’  as  above,  the  work  for which samples have failed shall be redone at the cost of contractors. However the Engineer in charge may order for additional tests (like cutting cores, ultrasonic pulse velocity test, load test of structure or part of structure etc) to be carried out at the cost of contractor to ascertain if the portion of structure wherein concrete represented  by  the  sample  has  been  used,  can  be  retained  on  the  basis  of results  of  individual  or  combination  of  these  tests.  The  contractor  shall  take remedial measures necessary to retain the structure as approved by the Engineer in charge without any extra cost. However, for payment, the basis of rate payable to  contractor shall be governed by the 28 days cube tests results and reduced rates shall be regulated in accordance with para 5.14.13 of Revised CPWD specification 2002 for C.M., C.C. and R.C.C. works.

1.2. 	Treatment for roof surfaces: -

For treatment of Roof Surfaces with integral cement based compound (Brick-coba), following specifications shall be applicable. This item shall be got executed from specialized agency to be got approved from Engineer-in-charge: -

1.2.1.1. 	The bricks bats shall be from over burnt bricks. The proprietary water-proofing compound shall bear I.S.I. mark and shall conform to IS: 2645. Before execution of work water proofing  compound has to be brought to and a certificate of its conforming  to  IS  code  should  be  produced.  The  proprietary  water-proofing compound shall be added at the rate recommended by the specialist firm but not exceeding 3 percent by weight of cement. The Engineer in charge reserve the right to collect the random sample from material brought at site and get it tested

16

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

from laboratory of his choice. The material which does not conform to the specification shall have to be removed forthwith by the contractor.

1.2.1.2. 	The finished surface after water proofing treatment shall have minimum slope of 1 in  80. At no point shall the thickness of water proofing treatment be less than

65mm.

1.2.1.3. 	While treatment of roof surface is done, it shall be ensured that the outlet drain- pipes have been fixed and mouths at the entrance have been eased and round off properly for easy flow of water.

1.2.1.4. 	The surface where the water proofing is to be done shall be thoroughly cleaned with wire brushes. All loose scales mortar splashes etc. shall be removed and dusted off. The surface shall be treated  with neat cement slurry admixed with proprietary water proof compound to penetrate  into crevices and fill up all the pores in the surface. The cement slurry shall be applied at the junction of parapet and terrace slab including the vertical face of the parapet.

1.2.1.5. 	After the slurry coat is laid, layer of over burnt brick bats shall be laid in cement mortar  of mix as specified by specialist firm but not leaner  than  1:5(1cement:

5coarse sand) admixed with  proprietary  water  proofing  compound to required gradient and joints filled to half the depth. The bricks bat layer shall be rounded at the junctions with the parapet and tapered  towards top for a height of 300mm curing of this layer be done for 2 days.

1.2.1.6. 	After curing the surfaces shall be applied with a coat of cement slurry admixed with proprietary water proofing compound.

1.2.1.7 	Joints of bricks bat layer shall be filled fully with cement mortar of mix as specified by the specialist firm but not leaner than 1:5 (1cement:5 coarse sand)admixed with proprietary  water proofing compound and finally top finished with average

20mm thick layers of cement mortar:1 :4 (1cement:4 coarse sand) and finished smooth with cement slurry mixed with proprietary water proofing compound. The finished surface shall have marking of  300x300mm false squares  to  give the appearance of tiles.

1.2.1.8 	Curing of water proofing treatment shall be done for a minimum period of weeks by flooding the water by making kiaries etc.

1.2.2 	MEASUREMENTS: 	The measurement shall be taken for plan area of terrace only.

Length and breadth shall be measured correct to 1cm. And area shall be worked out to nearest 0.01sqm. No deduction in measurement shall be made for either opening or recesses for chimney, stacks roof lights and the like of area upto 0.01sqm not anything extra shall be paid for forming such openings. For similar areas exceeding

0.10 sqm, deduction will be made in measurements for full openings  and nothing extra shall be paid for making such opening.

17

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

1.2.3 	Rates: The rate shall include the cost of all labour and materials  involved the all operations described above.

1.3 	CHECK LIST FOR QUALITY ASSURANCE: For works with estimated cost Rs.10

Lakhs  and  above,  quality  Assurance  Check  list  for  Back  Filling,  Plain  Cement Concrete, Shuttering, Reinforced Cement Concrete and Structural Steel fabrication as annexed  shall  form  a  part  of  the  Tender  Document.  Compliance  of  this  Quality Assurance Check List shall be before release of the payment.

18

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

LIST OF APPROVED MAKE OF MATERIALS

1.0 	FOR CIVIL WORKS

| Sl. No. | Details of Material/ Products |  | Manufacturer’s Name |
| --- | --- | --- | --- |
| 1.1 | Plywood |  | Duroply (Green marked, BWR Grade) of Sarda Plywood Industries Ltd. Century Plywood Green Plywood Kitply |
| 1.2 | Blockboard |  | Duroboard (Green marked, BWR Grade) of Sarda Plywood Industries Ltd. Green Plywood, Ashwani Sarda, F4, Dhawandeep Building, 6 Jantar Mantar Lane, New Delhi, Ph. 011-23748424/25/26/27/28) Century Plywood, E-5, Kalkaji, Main Road, New Delhi-19, Ph. 011-26474434 Kitply Industries Ltd. |
| 1.3 | Veneers |  | Sarda Plywood Industries Ltd., Green Plywood, Century Plywood, Kitply Industries Ltd. |
| 1.4 | Adhesive |  | Pidilite, 93, New Rajdhani Enclave, Vikas Marg, Delhi-92, Ph. 011-2203118, 2430170 Araldite & equivalent |
| 1.5 | Flush Doors |  | Samrat, Kanchan Prima, Swastik (Kitply), Century |
| 1.6 | Plastic Laminates |  | Formica, Neoluxe, Greenlam Bakelite Hylam, 28-A, IInd Floor, Defence Colony Market, New Delhi –24, Ph. 4623393, 4625935 |
| 1.7 | Steel Door |  | Raymus Straucturals and Engineering Pvt. Ltd. Plot No. 406, 457, Phase-III, Udyog Vihar, |

19

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

| Sl. No. | Details of Material/ Products |  | Manufacturer’s Name |
| --- | --- | --- | --- |
|  |  |  | Gurgaon, Fax No. 0124-2346050 Shakti Met Door |
| 1.8 | Aluminium Sections |  | India Aluminium Co. / Hindustan Aluminium / Jindal, Bharuka |
| 1.9 | Powder Coatings |  | Berger / Nerocoat / Jenson & Nicholson |
| 1.10 | Tile Joint Filler |  | Bal Adhesives & Grouts / “Roff Rainbow Tile Mate” of Roff Construction Chemicals Pvt. Ltd. / Winsil 20 / Silicon Sealant of GE Bayer Silicon / “Zentrival FM” of MC – Bauchemie (India) Pvt. Ltd. |
| 1.11 | PVC Tile Spacers |  | Kajaria Ceramic Limited, J-1/B-1 (Ext.) Mohan Cooperative Industrial Estate, Mathura Road, Ph. 26946409, 26946411, 26949524 |
| 1.12 | Heavy Duty Chequered Tiles |  | NITCO, 2308, Behind Kali Masjid, Chowk Prajapat, Delhi 110006 – Phone : 2048473 Modern Tiles, Hindustan Tiles |
| 1.13 | Ceramic Tiles |  | Kajaria / Spartek Morbito, Orient Nittco, Euro Somany/Rustico/Azure |
| 1.14 | Vitrified Tiles |  | Asian, Naveen, Somany Nitco Aaren Industries, F-31, Hauz Khas, Main Road, Opp. Telephone Exchange Euro 208, Sangam Arcade,Vallabhai Road, Vile Parle (W), Mumbai – E-mail : eurovitrified.com Oracle Granito Ltd. 309, New Delhi House 27 Barakhamba Raod, New Delhi – 110001 Ph. 011-4151 3661, 3256 3503 Fax No. 011-4151 1792 |

20

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

| Sl. No. | Details of Material/ Products |  | Manufacturer’s Name |
| --- | --- | --- | --- |
|  |  |  | E-mail : delhi@marbito.co.in Morbito |
| 1.15 | Mineral Fibre Suspended Ceiling |  | Armstrong World Industries (I) PVt. Ltd. A-31, Naraina Indl. Area, Phase-I, New Delhi – 110028 - Phone : 25893262 AMF perforated ceilings Ecoflex Atek Mineral Fibre India Pvt. Ltd. 495 Double Storey, Kalkaji, New Delhi 19 Ph : 11-51604860 Everest Industries Limited HS-37, 2nd Floor, Kailash Colony Market, New Delhi 110048 – Phone : 41618660 |
| 1.16 | Calcium Silicate Suspended Ceiling |  | Aerolite Ceiling Systems Plot No.-2, Phase-V, IDA, Jeedimetla, Hyderabad – 500 055 Phone : 040-23449240 Promat International (Asia Pacific) Ltd. S-5, Second Floor B-87, Defence Colony, New Delhi – 110 024. Ph. : 011-2469 1594, Fax :011 -2469 2064 E-mail: raman@promat.com.my |
| 1.17 | Resin Bonded Glass Wool |  | U.P. Twiga Fibreglass Limited / Crown Fibreglass / Rockloyd |
| 1.18 | MS Tubes |  | Tata 917, International Trade Tower, Nehru Place, New Delhi 110019 Lloyd Metal & Engineering Co. / NSL Limited |
| 1.19 | Roof Waterproofing |  | RB Waterproofing, India Waterproofing, CICO, SIKA, Structural Waterproofing Co. Pvt. Ltd. |

21

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

| Sl. No. | Details of Material/ Products |  | Manufacturer’s Name |
| --- | --- | --- | --- |
| 1.20 | Expansion / Scismic Floor / Wall Joints Cover |  | “No Bump” Multipurpose floro systems Plot No. 4, Kehar Singh Estate, Westend Marg Saidulajab, MB Road, New Delhi – 110 030 Ph. : 011 4166 4480, 4166 4478, 2953 5899 Fax : 011-2953 3733, E-mail : info@tristarintech.com McCoy Silicones Ltd. (C/S Group) Giesse (Acovyn Wall Covers) 8, M.M. Road, Motia Khan, New Delhi-55, Ph: 011-23513003 Fax:011-23513007, E-mail: tekgroup@vsnl.com |
| 1.21 | Silicon Sealants |  | GE Bayer Silicone Cross Road, Off 132 Ft, Ring Road, Ahmedabad – Ph. : 079-26748476 Sika G-75, Kalkaji 110019, Ph. : 26464823 Dow Corning / Waclear |
| 1.22 | Paints |  | ICI / Berger / Jenson & Nicholson/Asian Paints |
| 1.23 | Textured Paints |  | Spectrum C-1/106, Lajpat Nagar, New Delhi Ph : 29816587, 29816791, 29818345 Unitile Texture Unitile House, 3/35, Punjabi Bagh, New Delhi 110026, Phone : 25221877, 6599981 |
| 1.24 | Wax Polish |  | Reckitt & Colman or equivalent |
| 1.25 | Modular Stainless Steel Railings |  | Dline India Pvt. Ltd. Oberoi Garden Estate, 3rd Floor, ‘A’ Wing, Chandivali Farms Road, Andheri (East) Cavallier Interior Craft, Ph : 26846809 Jindal Dormat India Pvt. Ltd. |

22

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

| Sl. No. | Details of Material/ Products |  | Manufacturer’s Name |
| --- | --- | --- | --- |
|  |  |  | International Division A-181, Vikaspuri, New Delhi – 110 018 9810012361 (M), Fax No. 011-2550 5617 Connect Architectural Product Pvt. Ltd. B-5, Sector-81, Phase-II, Noida Mobile : 9871481811 |
| 1.26 | Fire Check Steel Doors |  | Godrej 379-A, Chirag Delhi, Sheikh Sarai, New Delhi – Ph : 26444300 Sukri 380, Chirag Delhi, New Delhi – Ph : 29250694 Pacific Fire Controls Phone : 23674884 |
| 1.27 | Interlock Paving Tiles |  | Unistone Unitile House, 3/35, Punjabi Bagh, New Delhi 110026 Hindustan Tiles 601, 602, Suneja Tower, Janakpuri Dist. Centre, New Delhi – Phone : 25532481 Nimco Prefab 57/11, 1st Floor, Old Rajinder Nagar, New Delhi - Phones : 25781059, 25814818 |
| 1.28 | Non Metalic Hardner |  | STP, Fosroc or equivalent |
| 1.29 | Anchor Fastener |  | HILTI, BOSCH |
| 1.30 | Formwork Release Agent |  | FOSROC, MBT, MC Baucheme, CICO, Ado Conmat |
| 1.31 | Ready Mix Concrete (RMC) |  | ACC, Unitech Grasim Industries Ltd. 2nd Floor, DCM Bldg., 16, Barakhamba Road, New Delhi – Ph : 23356752 / 23356754 L&T, 5, Bikaji Cama Place, Somdatt Chamber-1, 3rd Floor, P.O. Box 5, R.K.Puram, New Delhi Ph : 26106639, 26170519 Or Equivalent |

23

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

| Sl. No. | Details of Material/ Products |  | Manufacturer’s Name |
| --- | --- | --- | --- |
| 1.32 | Non shrink grout |  | Fosroc Chemical (India) |
| 1.33 | Bonding Coat |  | CICO Bond EPO of CICO Nitibond EP pf M/s FOSROC OR Polyalk EP of Sunanda speciality coating Pvt. Ltd. |
| 1.34 | Welding Electrodes |  | ESAB Advani – Orlikon Weld Alloy |
| 1.35 | Horizontal Tie Bars / Shear |  | BB Bars System, ETIC system |
| 1.36 | Cement |  | L&T, ACC, GRASIM, Birla, Ambuja as approved by Engineer-in-Charge |
| 1.37 | Epoxy |  | FOSROC, SIKA QUALCRETE, Araldite, MBT |
| 1.38 | Admixtures |  | FOSROC, MBT, Asian Lab, MC Baucheme, CICO Plast Super, Chembond, Sika |
| 1.39 | Waterproofing System |  | FOSROC, SIKA, SUPREME, SILTECH Chemicals, Krypton Buildmat Co., Ado Conmat |
| 1.40 | Aluminium Fabricator | (a) (b) (c) | Windorz India (P) Ltd. 806, Shakuntala Building, 59, Nehru Place, New Delhi 110019 Phone : 26283456, 41624899 M/s Alkarma Pvt. Ltd. Phone No. 011-25938525, 9810030901 Hindustan Alcox Ltd. 101, Janak Cinema Complex, New Delhi – 110058 Ph. 011-5555277 Or equivalent approved by Engineer-in-Charge |
| 1.41 | Reinforcement Steel (TMT Bars) | (a) (b) (c) | Steel Authority of India Ltd. Rashtriya Ispat Nigam Ltd. Tata Iron and Steel Company Ltd. Ist Floor, Jeevan Tara Building, 5 Sansad Marg, New Delhi – Ph : 23542646 Or equivalent as approved by the Engineer- |

24

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

| Sl. No. | Details of Material/ Products |  | Manufacturer’s Name |
| --- | --- | --- | --- |
|  |  |  | in-Charge |
| 1.42 | Wooden Laminated Flooring |  | KRONO, Quick Step M/s M.R.Carpets Pvt. Ltd. Phone : 45401155 PERGO M/s Red Floor India UG-5, Ansal Chamber, Bhikaji Cama Place New Delhi 110066 – Phone : 41658558 |
| 1.43 | Tile Joint Filler, Tile Fixing Adhesive, Polysulphide Sealant and Primer for Polysulphide |  | M/s Pidilite Industries Ltd., or equivalent as approved by Engineer-in-Charge |
| 1.44 | Gypsum False ceiling |  | Gypsum India Ltd., 137, Sant Nagar, Delhi 110065 – Ph : 26236289 26236290 Beral Gypsum or equivalent as approved by the Engineer- in-Charge |
| 1.45 | Float Glass | (a) | Glaverbel, Saint Gobain, Modiguard, Floatglass India Ltd (Asahi), or equivalent as approved by the Engineer-in-Charge |
| 1.46 | Toughened Glass | (a) | GSC, Gold Plus Gold Plus House, G-192, Prashant Vihar, New Delhi 110085 – Ph : 27564007, 27565277 Sejal Gurind Toughened D-172, Okhla Industrial Area, Phase-I, New Delhi 110020 – Ph : 26819009 Or equivalent as approved by the Engineer- in-Charge |
| 1.47 | Aluminum Sections, angles etc. | (a) | Indalco, Hindalco, Jindal or equivalent |
| 1.48 | Ironmongery for Aluminium | (a) | Security Style/Alualpha, |

25

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

| Sl. No. | Details of Material/ Products |  | Manufacturer’s Name |
| --- | --- | --- | --- |
|  | Doors & Windows | (b) | Conne Xions, 205, Balram House, Karampura, Commercial Compelx, New Delhi-15 Ph: 011-25920226-7, Fax:011-25920228 E-mail: info@lgfsysma.com Giesse/ Welka Lock McCoy Silicones Ltd. (C/S Group) 8, M.M. Road, Motia Khan, New Delhi-55, Ph: 011-23513003, 9813800117(M) Fax:011-23513007, E-mail: tekgroup@vsnl.com |

26

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

LIST OF APPROVED MAKES OF SANITARY AND PLUMBING MATERIALS

-----------------------------------------------------------------------------------------------------------------------

SL. 	MATERIALS 	BRAND NAME NO.

-----------------------------------------------------------------------------------------------------------------------

1. 	INDIAN/EUROPEAN CLOSET/

WASH BASIN 	SOMANY/AQUAWARE/HINDWARE/ PARRYWARE/ORIENT (CORAL)

2. 	PLASTIC W.C. SEATS 	COMMANDER/ DIPLOMAT/ADMIRAL

3. 	STAINLESS STEEL SINKS 	PRESTIGE/JAYNA/KINGSTON NEELKANTH

4. 	C.P. FITTINGS & ACCESSORIES 	GEM/PARKO/JAQUAR/ KINGSTON

& FLUSH VALVES

5. 	C.P. WASTE, SPREADERS, 	ORIENT/PARKO/JAQUAR URINAL

6. 	SENSOR OPERATED AUTO 	PARRYWARE/HINDWARE/

SEABIRD/ORIENT (CORAL)

FLUSHING  SYSTEM URINALS

7. 	HAND DRIER 	KOPAL

8. 	SOIL, WASTE & RAIN WATER PIPES & FITTINGS

A) 	CAST IRON PIPES 	NECO/B.C./RIF (IS:3989)

B) 	CENTRIFUGALLY CAST SPUN 	ELECTROSTEEL/ CAST IRON PIPES (IS:1536) 	KESORAM/IISCO

27

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

| 9. | RCC PIPES |  | INDIAN HUME PIPE/ PRAGATI CONCRETE UDYOG |
| --- | --- | --- | --- |
| 10. | G.I. PIPES |  | TATA/ JINDAL HISSAR |
| 11. | G.I. FITTINGS MALLEABLE CAST IRON) |  | R/KS / UNIK |
| 12. 13. | GUN METAL VALVES (FULLWAY, CHECK AND GLOBE VALVES) C.I. VALVES |  | ZOLOTO / LEADER / SANT KIRLOSKAR / SANT |
|  | (FULLWAY, CHECK AND GLOBE VALVES) |  |  |
| 14. | WATER METERS |  | CAPSTAN/KRANTI/ANAND |
| 15. | BALL COCKS |  | GPA/SANT/L & K |
| 16. | STONEWARE PIPES & GULLY TRAPS |  | PERFECT/BURN/RK |
| 17. | C.I. MANHOLES COVERS AND FRAMES |  | NECO / R.I.F. / B.C. |
| 18. | HORIZONTAL CENTRIFUGAL PUMPS |  | KIRLOSKAR/BEACONS/ HBD-BOMBAY |
| 19. | SUBMERSIBLE DRAINAGE PUMPS |  | KSB/KISHORE |
| 20. | ELECTRIC MOTORS |  | KIRSLOSKAR/GEC/SIEMENS |
| 21. | ELECTRICAL SWITCHGEAR & STARTERS |  | SIEMENS/L&T/ENGLISH ELECTRIC |
| 22. | CABLES |  | (REFER TO ELECTRICAL SPECIFICATIONS) |
| 23. | LIQUID LEVEL CONTROLLERS LIQUID LEVEL INDICATORS |  | MINILEC |
| 24. | FILTRATION PLANT/ SOFTENING PLANT |  | ION EXCHANGE/THERMAX / PENTAIR |
|  |  | 28 |  |

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

| 25. | PIPECOAT | INTEGRATED WATER PROOFING |
| --- | --- | --- |
| 26. | SFRC MANHOLE COVERS | KK / S K PRECAST CONCRETE |
| 27. | UPVC PIPES/ FITTINGS | SUPREME/ PRINCE / FINOLEX |
| 28. | MIRROR | ATUL/ MODI FLOT/GOLDEN FISH |

LIST OF APPROVED MAKES FOR ELECTRICAL AND SUBSTATION

| S.No. | MATERIALS | MANUFACTUERS / AGENCIES |
| --- | --- | --- |
| 1. | H.T Panel | Crompton /ABB / Alsthom / Siemens |
| 2. | Transformer | Crompton /Kirloskar /Voltamp / Alsthom / (DRY, Cast Resin) / BHEL / Universal |
| 3. | Bus trunking / Rising mains | (Along with all accessories) L&T / Schneider / GE / Control & Switchgear |
| 4. | LT Panels | GE / ABB / L&T / Siemens/ Schneider |
| 5. | ACBs | Same as (4) |
| 6. | MCCBs | Same as (4) |
| 7. | MCBs with DBs | Legrand /Hager / Alsthom/ Merlin Gerin/ Havels / Standard / Indo-asian |
| 8. | Accessories of HT /LT Panels | As per manfacturer’s specified make |
| 9. | HT / LT UG cables | Cable corporation/Universal/Gloster/ Havells / NICCO /Polycab |
| 10. | Wiring cables | Polycab / Havells / RR Kables / Finolex |
| 11. | Switches (SFU) | GE / ABB / L&T / Siemens/ Schneider |
| 12. | Modular Switches or Boxes | Legrand / Carbtree / Ess Esskay (signature) / MK /clipsal / Northwest |

29

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

| 13. | Piano Type switches and Accessories | Anchor / Leader |
| --- | --- | --- |
| 14. | Cubicle Type Fuse Unit | Siemens / GE / L&T/ABB/ Schnider |
| 15. | SFUs/Isolators | Siemens / GE / L&T / ABB/ Schnider |
| 16. | Starters /Contractor /Bi metal Relay | Siemens / L&T / ABB |
| 17. | Push Button /Indicating Lamps (LED Type) | Siemens / L&T / ABB |
| 18. | CTs | Kappa |
| 19. | Control Fuse Base with HRC Fuse | GEC / Alsthom |
| 20. | Selector Switch | Salzer |
| 21. | Measuring Instruments | AE / IMP / Rishab |
| 22. | MS Conduit | Supreme / BEC / NIL / or any Other ISI marked |
| 23. | PVC Conduit | Precision / Avon Plast / Clipsal |
| 24. | Accessories for PVC conduit | Precision / Clipsal / Avon Plast |
| 25. | Capacitors | Universal / Siemens / L&T / GE |
| 26. | Relays | L&T / EE / GE |
| 27. | Digital Meters | Enercon / Alacirity / L&T |
| 28. | Jointing Kits | Rey Chem / 3M Birla |
| 29. | AC Units | Blue Star, Volts, Carrier |

NOTE:  In  all  cases  of  procurements,  the contractor  shall  submit  his  proposal  of procurement of materials in the form of a submittal with material specification and

product information brochures, samples etc and the final decision on a particular

30

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

make shall always vest with the engineer-in-charge. In case specific makes are not mentioned for a material, contractor shall submit his proposal for reputed makes of materials.  No procurement shall be made and no material shall be brought to site without the prior approval of the Engineer-in-charge and the Engineer-in-charge will have the right to ask the contractor to remove any such material brought to site and the contractor is bound to obey any such orders within 24 hours.

TABLE FOR WEIGHT (Kg/m) FOR REINFORCEMENT BARS

Steel reinforcement shall be measured and paid for on the basis of theoretical standard weight of different sizes of bars, irrespective of the actual weights as per table given below (up to 3 digits as per CPWD Table.)

Dia (mm)	Weight (kg/m)

| 6 |  | 0.222 |
| --- | --- | --- |
| 8 |  | 0.395 |
| 10 |  | 0.617 |
| 12 |  | 0.888 |
| 16 |  | 1.579 |
| 18 |  | 1.999 |
| 20 |  | 2.467 |
| 22 |  | 2.985 |
| 25 |  | 3.856 |
| 28 |  | 4.836 |
| 32 |  | 6.316 |
| 36 |  | 7.986 |
| 40 |  | 9.869 |
| 45 |  | 12.490 |
| 50 | 31 | 15.424 Contractor’s name |
| HLL LIFECARE Ltd |  |  |

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

BILL OF QUANTITIES

32

HLL LIFECARE Ltd

CONSTRUCTION OF 5 DOCTOR’S DISPENSARY FOR ESIC AT KADAMBHANADU, KERALA

Appendix - E

| SUMMARY |  |  |  |
| --- | --- | --- | --- |
| SL. NO. | DESCRIPTION | ESTIMATED AMOUNT |  |
|  |  | Schedule items | Non schedule items |
| 1 2 3 4 | CIVIL WORKS INTERNALPLUMBING EXTERNAL PLUMBING ELECTRICAL WORKS | 12159575.70 722596.35 538129.05 1739397.38 | - - - 4929189.34 |
|  | TOTAL | 15159698.48 4929189.34 |  |
| GRAND TOTAL 20088887.82 |  |  |  |
| Say Rs. 2,00,88,888/- (Rupees Two crores Eighty Eight Thousand Eight Hundred and Eighty Eight only) |  |  |  |
| I hereby agree to execute the work 1 Schedule items : Estimated cost Rs.15159699.00 (Rupees One crore Fifty One lakhs Fifty Nine Thousand Six hundred and Ninety Nine only) at *estimated cost or at percentage ………………... (……………………………………) *above/below. 2 Non schedule items : Estimated cost Rs.4929189.00 (Rupees Forty Nine Lakhs Twenty Nine Thousand One hundred and Eighty Nine only) at *estimated cost or at percentage ……………… (………………………………) *above/below. |  |  |  |

Note: * Strike the words whichever is

not applicable	Signature of Contractor.

33

HLL LIFECARE Ltd