## Civil works
Horizontal Extention of first floor over the existing ward of Taluk Hospital, Karunagapally
PART I- CIVIL WORKS
Sl.no | Description of Item | Quantity | Unit | Rate(Rupees in words & Figures) | Amount(Rupees in words)
SUB HEAD I : REINFORCED CEMENT CONCRETE
1 | Reinforced cement concrete work in walls including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, posts and struts, etc.upto floor five level including the cost of centring, shuttering finishing and excluding cost of reinforcement .1 : 1.5 : 3 ( 1 cement : 1.5 coarse sand :3 graded stone aggregate 20 mm nominal size). | 61.69 | cum
2 | Reinforced cement concrete work in beams, suspended floors,roofs,having slope upto 15O,landings,balconies, shelves,chajjas,lintels,bands,plain window sills,staircases and spiral staircases upto floor five level including the cost of centring, shuttering finishing and excluding cost of reinforcement with 1 : 1.5 : 3 ( 1 cement : 1.5 coarse sand : 3 graded stone aggregate 20 mm nominal size).. | 264.42 | cum
3 | Reinforced cement concrete work in walls (any thickness) including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc upto floor V level including cost of centering, shuttering, finishing and excluding cost of reinforcement in 1:3:6 (1 cement: 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) | 20.92 | cum
4 | Reinforcement for reinforced cement concrete works including straightening, cutting, bending, binding and placing in position all complete:- Thermo Mechanically Treated bars-Vizag/Tata/sail | 54263.27 | kg
5 | Extra for additional height in centering, shuttering where ever required with adequate bracing, propping etc., including cost of de-shuttering and decentering at all levels, over a height of 3.5 m, for every additional height of 1 metre or part thereof (Plan area to be measured). Suspended floors, roofs, landing, beams and balconies (Plan area to be measured) | 1079.22 | sqm
6 | Providing and fixing in position ,copper plate as per design for expansion joints | 50 | kg
7 | Providing and fixing in position ,blown bitumen expansion joints. | 49.4 | Rm
8 | Providing and fixing in position ,12 mm thick bitumen impergnated fibre board conforming to IS.1838 including cost of primer ,sealing compound in expansion joints. | 49.4 | Rm
9 | Providing and fixing sheet cover over expansion joints with iron screws as per design to match the colour/shade of wall treatment- Aluminium fluted strips 3.15 mm thick:150 mm wide | 80 | Rm
SUB HEAD II : BRICK WORK
10 | Brick work with country burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in :Cement mortar 1:6 (1 cement : 6 coarse sand) | 282.63 | cum
11 | Half brick masonry with country burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level. Cement mortar 1:4 (1 cement :4 coarse sand) | 429.97 | sqm
12 | Extra for providing and placing in position 2 Nos 6 mm dia M.S. bars at every third course of half brick masonary ( with F.P.S. bricks). | 429.97 | sqm
SUB HEAD :III GRANITE WORK
13 | Providing and fixing 18 mm thick mirror polished, machine cut for kitchen platforms, vanity counters facias and similar locations of required size of approved shade, colour and texture laid over 20 mm thick base cement mortar 1 : 4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing etc. complete at all levels :- Granite of any colour -- area of slab : | 20.06 | sqm
14 | Extra for providing edge moulding to 18mm thick marble counters, Vanities etc. including machine polishing to dege to give high gloss finish etc. complete as per design approved by Engineer-in-charge Granite work | 27 | Rm
SUB HEAD IV : WOOD WORK
15 | Providing and fixing 18mm thick marine plywood exsterior grade of approved make for cup board shelves including neccessary screws, nails,gum etc complete asper the direction of engineer-in - charge. Including painting to get an even shade. | 20 | sqm
16 | Providing and fixing cupboard shutters with 18mm thick marine plywood ISI marked exterior grade of approved make including IInd class teak wood lipping of 18mm wide x12 mm thick with necessary screws,75mm stainless steel handle and bright finished stainless steel piano hinges etc. complete asper direction of Engineer -in-charge | 12 | sqm
17 | Providing and fixing brass 6 lever locking mechanism of approved make like godrej etc. for cupboard including all neccessary fittings as directed by the engineer in charge | 15 | each
18 | Providing and fixing M.S. grills of required pattern in frames of windows etc with M.S flats, square or round bars etc all complete:- Fixed to openings / wooden frames with rawl plugs screws etc. | 2221.76 | Kg
19 | Providing and fixing fly proof galvanized M.S wire gauze to windows and clerestory windows using galvanized M.S wire gauge with average width of aperture 1.4 mm in both directions with wire of dia 0.63 mm. With 12 mm mild steel u beading | 21 | sqm
SUB HEAD V: STEEL WORK
20 | Providing and fixing M.S. fan clamp type I of 12 mm dia M.S. bar bent to shape with hooked ends in R.C.C. slabs during laying including painting the exposed portion of loop , all as per standard design complete . | 80 | each
SUB HEAD VI : FLOORING
21 | Providing and laying Ceramic glazed wall tiles conforming to IS:15622 of minimum 300x450 mm thickness 5MM of approved make NITCO, ORIENT, SOMANY, KAJARIA or equivalent make in all colours, shades except begundy,bottle green, black of any size as approved by Engineer in charge in skirting,risers of steps and dados over 12mm thick bed of Cement Mortar 1:3 (1Cement:3 Coarse sand) and joining with grey cement slurry @ 3.3kg per sqm including pointing in white cement mixed with pigment of matching shade complete. (Basic price not less than 400/m2) | 589 | sqm
22 | Providing and laying anti-skid ceramic floor tiles 300x300 mm or nearest size of not less than 7.5mm thick of 1st quality conforming to IS : 13755 of NITCO, ORIENT, KAJARIA or equivalent make in all colours, shades except White, Ivory, Grey, Fume Red Brown,laid on 20mm thick bed of Cement Mortar 1:4 (1 Cement : 4 Coarse sand) including pointing the joints with white cement and matching pigments etc., complete.(Basic price not less than 367/m2) | 83 | sqm
23 | Providing and laying virtified floor tiles of size 600x600 mm thickness 10mm of M/s Jonson or equivalent (Marbonite), Somany, Kajaria, or equivalent in light colours and shades , with water absorption's less than 0.08% and conforming to IS : 15622 of approved make in all colours and shades, laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand) including grouting the joints with white cement and matching pigments etc., complete.(Basic price not less than 865/m2) | 933 | sqm
SUB HEAD VII : ROOFING
24 | Providing and fixing on wall face unplasticised- Rigid PVC rain water pipes conforming to IS:13592 type A including jointing with seal ring conforming to IS:5382 leaving 10mm gap for thermal expansion (i) Single socketed pipes – 110mm diameter of 4Kg/m2 | 190 | Rm
25 | Providing and fixing unplasticised-P.V.C pipes clips of approved design to unplasticised-P.V.C rain water pipes by means of 50 x 50 x 50 mm hard wood plugs, screwed with M.S screws of required length including cutting brick work and fixing in cement mortar 1 : 4 ( 1 cement : 4 coarse sand ) and making good the walls etc. complete :- 110 mm diameter of 4Kg/m2. | 120 | each
26 | Providing and fixing to the inlet mouth of rain water pipe cast iron grating 15cm diameter and weighing not less than 440 grams. | 28 | each
27 | Providing and fixing on wall face unplasticised-PVC moulded fittings/accessories for unplasticised-Rigid PVC rain water pipes conforming to IS:13592 type A including jointing with seal ring conforming to IS:5382 leaving 10mm gap for thermal expansion bend 87.5 degree
a | 110 mm bend of 4Kg/m2. | 45 | each
b | Shoe( plain)
| 110 mm shoe of 4Kg/m2. | 38 | each
28 | Supplying and fixing Leaxan Polycarbonate sheet roofing 4.50mm multiwall bronze (Manufactured by GE Plastics India Private Ltd) over the framework using special MS extrusions of size 50x22.5mmwith rubber gasket applying silicon sealent and support whereever necessary(Rate is inclusive of framework including support, painting etc).Nothing etc shall be paid on pattern of framework. | 40 | SQM
29 | Providing and fixing semicircular 110mm PVC pipe of 4Kg/m2. for gutter with iron brackets 40 x 3 mm size, bolts , nuts and washers including making necessary connections with rain water pipes complete. | 60 | Rm
SUB HEAD VIII : FINISHING
30 | 15mm cement plaster on rough side of single or half brick wall of mix 1:6 ( 1 cement : 6 fine sand) | 236 | sqm
31 | 12 mm cement plaster of mix : 1:6 (1 cement: 6 fine sand) | 1807.11 | sqm
32 | Cement Plaster in two coats – 18mm cement plaster in two coats under layer 12mm thick cement plaster 1:5 (1 cement : 5 coarse sand) finished with a top layer 6mm thick cement plaster 1 : 6 (1 cement : 6 fine sand ) | 1202.32 | sqm
33 | Wall painting with plastic emulsion paint of approved brand and (asian,berger)manufacture to give an even shade. Two or more coats on new work, including priming coat . | 2043.114 | sqm
34 | Distempering with first quality acrylic distemper (ready mixed) of approved manufactures of required shade (asian,berger)and colour complete ,as per manufactures specification . New work ( three or more coats) . | 1285 | sqm
35 | Finishing walls with acrylic smooth exterior paint of required shade (asian,berger) : exterior walls. New work (Two or more coat applied @ 1.67 ltr/10 sqm over and including priming coat of exterior primer applied @ 2.20 kg/ 10 sqm). | 1202.32 | sqm
36 | Painting with synthetic enamel paint of approved brand (asian,berger) and manufacture to give an even shade :- Two or more coats on new work . | 139 | sqm
37 | Providing and applying plaster of paris putty of 2 mm thickness over plastered surface to prepare the surface even and smooth complete | 200 | sqm
SUB HEAD IX : MISCELLANEOUS
38 | Providing and fixing factory made PVC door frame made of PVC extruded section having overall dimension of 48 x 40 mm (tolerance + 1 mm ) with wall thickness 2.0 mm + 0.2 mm, corners of the door frame to be mitred and jointed by means of plastic/M.S. galvanised brackets and stainless steel screws. The hinge side vertical of the frames reinforced by galvanised M.S.tube of size 19 x 19 mm and 1mm + 0.1 mm wall thickness and 3 nos. stainless steel hinges fixed to the frame complete as per manufacturers specification and direction of Engineer - in - charge ( Sintex Plasopan or duroplast) | 106.5 | Rm
39 | Providing and fixing 30 mm thick factory made PVC rigid foam panelled door shutters manufactured by M/S. Rajshri or equivalent made from M.S.tube of 19 gauge thickness, size 19 x19 mm for styles and 15 x 15 mm for top and bottom rails, covered with heat moulded PVC "C" channel of 5 mm thick sheet and 30 x50 mm wide to form styles and 5 mm thick and 75 mm wide PVC sheets for top rail, lock rail and bottom rail on either side and 5 mm thick, 20 mm wide cross PVC sheet as gap insert for top rail ad bottom rail, panelling of 5 mm thick PVC sheet fitted in the M.S.frame welded/ sealed to the styles and rails with 5 x 30 mm PVC sheet beading on either side and joined together with solvent cement adhesive etc., complete as per manufacturers specification and direction of Engineer - in -charge fixed to frames with 4 Nos. M.S.powder coated butt hinges ( for W.C. and bathroom shutters) | 35.7 | sqm
SUB HEAD X : Dismantling & Demolishing
40 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge 1:3:6 or richer mix | 16.84 | CUM
41 | Demolishing R.C.C. work manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per direction of Engineer - in- charge. | 6.03 | CUM
42 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge. In cement mortar | 24.38 | CUM
43 | Taking out doors, windows and clerestory window shutters (steel or wood) including stacking within 50 metres lead: | 2 | EACH
44 | Removing and refixing carefully the existing polycarbonte sheet roofng with steel trusses frame work including necessary cutting removing cleats etc as required. | 192.5 | sqm
45 | Removing and refixing carefully the existing water tank to First floor roof slab. Include necessary fittings | 6000 | litre
46 | Removing and refixing carefully the existing supply and distribution water line over the terrace to the First floor of the building including necessary fittings. | 400 | RM
47 | Dismantling old plaster or skirting raking out joints and cleaning the surface for plaster including disposal of rubbish to the dumping ground within 50 metres lead | 1197 | SQM
SUB HEAD XI : SANITARY INSTALLATIONS& WATER SUPPLY
48 | Providing and fixing water closet squatting pan (Indian type WC pan ) with 100 mm sand cast iron P or S trap, 10 litres low level P.V.C flushing cistern manually controlled device ( handle lever ) conforming to IS: 7231, Parryware/Hindware/ Seabird/Orient ( Coral) with all fittings and fixtures complete including cutting and making good the walls and floors wherever required :- White Vitreous china Orissa pattern WC pan of size 580 x 440 mm with integral type foot rests . | 4 | each
49 | Providing and fixing white vitreous china pedestal type water closet (European type W.C.pan) with seat and lid, 10 litre low level P.V.C. flushing cistern with manually controlled device ( handle lever ), conforming to IS : 7231, Parryware / Hindware/ Seabrid / Orient ( Coral ) with all fittings and fixtures complete including cutting and making good the walls and flors wherever required :-W.C. pan with ISI marked white solid plastic seat and lid. | 8 | each
50 | Providing and fixing wash basin with C.I/M.S. brackets,15mm C.P. brass pillar taps, Kingston / Gem / Techno / Parko, 32mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls and floors wherever required :
| Wash basin size 550x400mm with single 15mm C.P.brass pillar tap | 10 | each
51 | White Vitreous China Surgeon type wash basin of size660x460 mm with single 15 mm C.P. brass pillar taps cera or equalent. elbow operated levers ISI marked.Elbow operated tap 20mm | 4 | each
52 | Providing and fixing 600 x 450 mm beveled edge mirror of superior glass of approved quality complete with 6 mm thick hard board ground fixed to wooden cleats with C.P brass scews and washers complete. | 12 | each
53 | Providing and fixing PTMT towel rail complete with brackets fixed to wooden cleats with C.P.brass screws with conceiled fittings arrangement of approved quality colour and make( Prayag or equivalent) 450mm long towel rail with total length of 495mm, width 78mm and effective height of 88mm, weighing not less than 170gms | 14 | each
54 | Providing and fixing P.V.C waste pipe for sink or wash basin, including P.V.C waste fittings complete :- Semi rigid pipe :-40 mm dia. | 12 | each
55 | Providing and fixing trap of self cleansing design with screwed down or hinged grating with or without vent arm complete, including cost of cutting and making good the walls and floors a)100mm inlet and 75mm outlet. | 25 | Each
56 | Providing and fixing PTMT soap Dish Holder having length 138mm,breadth 102mm,height of 75 mm with concealed fitting arrangement . weighing not less than 106gms | 18 | each
57 | Providing and fixing unplasticised rigid PVC pipes (pressure 6kg/cm2)confirming to IS specifications in rainwater pipe or in drainage lines including all fittings and fixtures complete
a | 75 mm diameter | 75 | Rm
b | 110 mm diameter | 190 | Rm
58 | Providing and jointing PVC pipes of (pressure10 Kg/cm2) confirming to IS specifications for water supply including testing of joints, concealing the pipes wherever required etc complete.
a | 20mm PVC pipe | 120 | Rm
b | 25 mm PVC pipe | 100 | Rm
c | 32mm PVC pipe | 20 | Rm
d | 40mm PVC pipe | 100 | Rm
e | 50mm PVC pipe | 50 | Rm
59 | Providing and fixing PTMT (an Engineering thermo plastic ) grating of approved quality colour and make 150 mm nominal size square, 18 mm high 100mm dia of the inner of hinged round grating domed shapped with 31 mm waste hole confirming to IS standards, weighing not less than 100 gms. | 25 | each
60 | Providing and fixing CP brass long body bib cock of approved quality confirming to IS standards weighing not less than 690gms (With long handle) 15mm nominal bore | 18 | each
61 | Providing and fixing,conforming to IS specification unplasticised rigid PVC pipes(pressure 6 kg/cm2) in drainage lines including cutting,trenching,filling but excluding the cost of fittings and fixtures etc complete
a | Providing and fixing 32mm PVC tank connector | 4 | each
b | Providing and fixing of 75mm pvc plain elbow | 24 | each
c | Providing and fixing of 75mm pvc door elbow | 14 | each
d | Providing and fixing of 75mm pvc door tee | 40 | each
e | Providing and fixing of 75mm pvc plain bend | 49 | each
f | Providing and fixing of 110mm pvc plain bend | 60 | each
g | Providing and fixing of 110mm pvc plain elbow | 50 | each
h | Providing and fixing of 110mm pvc door elbow | 12 | each
i | Providing and fixing of 110mm pvc door tee | 16 | each
j | Providing and fixing of 110mm pvc air cowl | 10 | each
62 | Providing and fixing C.P. brass bib cock of approved quality conforming to IS : 8931 :- | 4 | each
15 mm nominal bore
63 | Providing and fixing C.P. brass stop cock (concealed) of standard design and of approved make conforming to IS 8931 :- | 30 | each
15 mm nominal bore
64 | Providing and fixing C.P. brass shower hose with 15 or 20 mm inlet 100 mm dia. | 4 | each
65 | Providing and fixing unplasticised P.V.C connection pipe with brass unions :-
a | 15MM nominal bore | 22 | each
b | 20 mm nominal bore. | 5 | each
66 | Providing and fixing gun metal gate valve with CI wheel of approved quality(screwed end) –
| 25mm dia nominal bore | 5 | each
| 40 mm dia nominal bore | 10 | each
67 | Providing and fixing of 75 mm pvc air cowl | 12 | each
68 | Providing and fixing C.P. brass angle valve for basin mixer and geyser points of approved quality conforming to IS:8931 a) 15 mm nominal bore 15mm nominal bore | 20 | each
SUB HEAD XII : ALUMINIUM WORK
69.a | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular and other section of approved make conforming to IS : 733 and IS : 1285, fixed with rawl plugs and screws or with fixing clips, or with expansion hold fastners including necessary filling up of gaps at junctions, at top, bottom and sides with required P.V.C/neoprene felt etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically where ever required including cleat angle, Aluminium snap beading for glazing / panelling, C.P brass/ stainless steel screws, all complete as per Architectural drawings and the direction of Engineer-in-charge (glazing and panelling to be paid for separately) :- P/F aluminium work for doors, windows, ventilators and partitions etc as per architectural drawings and the directions of Engineer-in-charge. : For fixed portion with Powder coated aluminium of 50 micron. | 1251.69 | kg
b | b) For shutters of doors, windows and ventilators including providing and fixing hinges /pivots and making provision for fixing of fittings wherever required including the cost of P.V.C / neoprene gasket required (Fittings shall be paid for separately) . P/F aluminium work for doors, windows, ventilators and partitions as per architectural drawings - : For shutters of doors, windows & ventilators- with Powder coated aluminium of 50 micron | 870.44 | kg
70 | Extra for Providing and fixing 12 mm thick prelaminated three layer medium density (exterior grade) particle board Grade I, Type II conforming to IS : 12823 bonded with phenol formaldehyde synthetic resin, of approved brand and manufacture in panelling fixed in Aluminium doors, windows shutters and partition frames already fixed with C.P brass / stainless steel screws etc. complete as per architectural drawings and direction of Engineer-in-charge :- | 97 | sqm
Prelaminated particle board with decorative lamination in both sides.
71.a | Providing and fixing glazing in aluminium doors windows, ventilator shutters and partitions etc. with P.V.C / neoprene gasket etc. complete. as per the Architectural drawings and the directions of Engineer-in- charge. With glass panes of 5.5 mm thickness (weight not less than 10 Kg/Square metre . | 121.56 | sqm
b | With glass panes of 4 mm thickness (weight not less than 13.75 Kg/Square metre . | 81.45 | sqm
c | Providing and fixing glazing in aluminium doors windows, ventilator shutters and partitions etc. with P.V.C / neoprene gasket etc. complete. as per the Architectural drawings and the directions of Engineer-in- charge. With glass panes of 8 mm thickness . | 66.21 | sqm
72 | Providing and fixing aluminium sliding door bolts ISI marked anodised ( anodic coating not less than grade AC 10 as per IS: 1868) transparent or dyed to required colour or shade with nuts and screws etc 300x16mm. complete- | 8 | each
73 | Providing and fixing aluminium handles ISI marked anodised ( anodic coating not less than grade AC 10 as per IS: 1868) transparent or dyed to required colour or shade with nuts and screws etc. complete-
a | 125 mm | 8 | each
b | 100mm | 30 | each
74 | Providing and fixing aluminium tower bolts ISI marked anodised ( anodic coating not less than grade AC 10 as per IS: 1868) transparent or dyed to required colour or shade with nuts and screws etc. complete-
| 250 X 10 mm | 8 | each
| 150x10mm | 15 | each
75 | Providing and fixing IS : 3564 marked aluminium extruded section body tubular type universal hydraulic door closer with double speed adjustment with necessary accessories and screws etc. complete. | 20 | each
76 | Providing and fixing 100mm brass locks (best make of approved quality) for aluminium doors including necessary cutting and making good etc. complete. | 12 | each
77 | Providing fixing aluminium casement windows fastener of required length for aluminium windows with necessary screws etc. complete. Powder coated minimum thickness 50 micron aluminium | 92 | each
78 | Providing and fixing brass adjustable friction window stays of approved quality with necessary screws etc to the side hung window as per direction of engineer-in-charge complete. 250mm length | 184 | each
79 | Providing and fixing aluminium hanging floor door stopper, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) Transparent or dyed to required colour and shade, with necessary screws etc. complete. Twin rubber stopper | 20 | each
80 | Supplying and fixing hand rails with 304 grade and 16 gauge stainless steel pipe for stair cases with 1 No. polished stainless steel pipe of 50mm diameter at top and newel post and SS 304, 16 gauge ,25mm dia 2nos polished stain less steel pipe middle horizontal and 0.30m centre to centre vertical(approximately) welded together , including all neccessary fittings etc.. as per the drawing and direction of the Engineer – in – charge. Hand rails shall be fixed in the floor/steps with expansion hold fasters of required size including drilling etc.complete | 37 | RM
SUB HEAD : XIII WATER PROOFING
81 | Cleaning of RCC to remove dust and loosely adhering particles completely.Supply and application of 1st coat with Nitobond SBR Latex mixed with cement mortar, – the polymer modified high quality emulsion, as a coving at the corners of floor and the vertical surface in the sunken area, and between floor and walls in the remaining area..Supply and application of 2nd coat of Brushbond – acrylic Polymer modified cementitious waterproofing coating on the prepared surface in a continuous film on the floor of the sunken area, taking the coating over the vertical surfaces on to the floor and over the coving on to the wall (before tiling) to at least 600mm above the final finished floor level. The coating shall also be continued on to the inner surfaces of the pipe penetration holes. Two coats shall be applied. | 1185.91 | sqm
82 | 12mm cement plaster finished with a floating coat of neat cement of mix
| 1:3 (1 cement: 3 fine sand) | 1185.91 | sqm
Total (PART I -CIVIL WOKS)

## Civil Measurement (hidden)
DETAILED MEASUREMENT
Name of work: Construction of first floor over existing Ward at Taluk Hospital, Karunagapally
No | Description of Item | Number | Length | Width | Hight | Quantity | Unit
SUB HEAD I : REINFORCED CEMENT CONCRETE
1 | Reinforced cement concrete work in walls including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, posts and struts, etc.upto floor five level including the cost of centring, shuttering finishing and excluding cost of reinforcement .
1 : 1.5 : 3 ( 1 cement : 1.5 coarse sand :3 graded stone aggregate 20 mm nominal size).
| column | 37 | 0.6 | 0.6 | 4.08 | 54.346 | m3
|  | 4 | 0.3 | 0.6 | 4.08 | 2.938 | m3
| Sec.Flr column | 2 | 0.6 | 0.6 | 4.08 | 2.938 | m3
|  | 2 | 0.3 | 0.6 | 4.08 | 1.469 | m3
| Total |  |  |  |  | 61.691 | cum
2 | Reinforced cement concrete work in beams, suspended floors, roofs having slope upto 15degree, landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases upto floor V level including cost of centering, shuttering, finishing and excluding the cost of reinforcement in 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size)
| Primary beam | 2 | 7.9 | 0.3 | 0.6 | 2.844 | m3
|  | 15 | 5.18 | 0.3 | 0.6 | 13.986 | m3
|  | 19 | 6.36 | 0.3 | 0.6 | 21.751 | m3
|  | 30 | 6.35 | 0.3 | 0.6 | 34.29 | m3
Secondary Beam
|  | 9 | 6.36 | 0.3 | 0.6 | 10.303 | m3
|  | 15 | 5.18 | 0.3 | 0.6 | 13.986 | m3
| lift beam | 4 | 2.4 | 0.23 | 0.6 | 1.325 | m3
| Stair beam | 2 | 2.92 | 0.2 | 0.225 | 0.263 | m3
[6 empty] | 98.748 | m3
Slab
|  | 1 | 38.8 | 28.4 | 0.12 | 132.23 | m3
|  | 2 | 7.9 | 7.1 | 0.12 | 13.462 | m3
| Lift slab | 2 | 3 | 3.5 | 0.12 | 2.52 | m3
Stair
| Stair landing | 2 | 3.37 | 1.7 | 0.17 | 1.948 | m3
| Waist slab | 4 | 4.57 | 1.4 | 0.17 | 4.351 | m3
| Step | 52 | 0.3 | 1.4 | 0.165 | 3.604 | m3
[6 empty] | 158.115 | m3
| Lintel out side & Inside | 7 | 38.8 | 0.23 | 0.15 | 9.37 | m3
|  | 7 | 28.4 | 0.23 | 0.15 | 6.859 | m3
|  | 4 | 8.69 | 0.23 | 0.15 | 1.199 | m3
|  | 4 | 7.1 | 0.23 | 0.15 | 0.98 | m3
[6 empty] | 18.408 | m3
| Sunshade | 2 | 38.82 | 0.6 | 0.07 | 3.261 | m3
| Sunshade | 1 | 28.4 | 0.6 | 0.07 | 1.193 | m3
| Sunshade | 2 | 7.9 | 0.6 | 0.07 | 0.664 | m3
| Counter slab | 2 | 5 | 0.6 | 0.07 | 0.42 | m3
[6 empty] | 5.538 | m3
| Total |  |  |  |  | 280.809 | m3
Deduction
| Courtiyad | 1 | 13.3 | 6.65 | 0.12 | 10.613 | m3
| Stair | 2 | 2.95 | 5.43 | 0.12 | 3.844 | m3
| Lift | 2 | 2.4 | 3 | 0.12 | 1.728 | m3
| Duct | 1 | 0.62 | 1.43 | 0.12 | 0.106 | m3
| Duct | 1 | 0.62 | 1.37 | 0.12 | 0.102 | m3
[6 empty] | 16.393 | m3
| Less deduction |  |  |  |  | 264.416 | m3
3 | Reinforced cement concrete work in walls (any thickness) including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc upto floor V level including cost of centering, shuttering, finishing and excluding cost of reinforcement in 1:3:6 (1 cement: 3 coarse sand : 6 graded stone aggregate 20 mm nominal size)
| Dummy Coulmns | 37 | 0.6 | 0.6 | 1.5 | 19.98
|  | 4 | 0.6 | 0.3 | 1.3 | 0.936
| say |  |  |  |  | 20.916 | cum
4 | Reinforcement for reinforced cement concrete works including straightening, cutting, bending, binding and placing in position all complete:- Thermo Mechanically Treated bars-Vizag/Tata/sail
| slab |  | 158.115 | 125 |  | 19764.375
| Beams |  | 98.748 | 150 |  | 14812.2
| Column |  | 82.607 | 210 |  | 17347.47
51924.045
| sunshade |  | 5.538 | 90 |  | 498.42
| lintel |  | 18.408 | 100 |  | 1840.8
| Total |  |  |  |  | 54263.265 | kg
| say | 54263.265 | kg
5 | Extra for additional height in centering, shuttering where ever required with adequate bracing, propping etc., including cost of de-shuttering and decentering at all levels, over a height of 3.5 m, for every additional height of 1 metre or part thereof (Plan area to be measured). Suspended floors, roofs, landing, beams and balconies (Plan area to be measured)
|  | 1 | 38.8 | 28.4 |  | 1101.92 | m2
|  | 2 | 7.9 | 7.1 |  | 112.18 | m2
[6 empty] | 1214.1 | m2
Deduction
| Courtiyad | 1 | 13.3 | 6.65 |  | 88.445 | m2
| Stair | 2 | 2.95 | 5.43 |  | 32.037 | m2
| Lift | 2 | 2.4 | 3 |  | 14.4 | m2
[6 empty] | 134.882 | m2
| Less deduction |  |  |  |  | 1079.218 | m2
6 | Providing and fixing in position ,copper plate as per design for expansion joints |  |  |  |  | 50 | kg
7 | Providing and fixing in position ,blown bitumen expansion joints. |  |  |  |  | 10 | per cm depth per cm width per 100 m
| beams | 1 |  |  | 28.4 | 28.4
| Columns | 5 |  |  | 4.2 | 21
49.4
8 | Providing and fixing in position ,12 mm thick bitumen impergnated fibre board conforming to IS.1838 including cost of primer ,sealing compound in expansion joints. | [5 empty] | per cm depth per cm width per meter length.per100m
| beams | 1 |  |  | 28.4 | 28.4
| Columns | 5 |  |  | 4.2 | 21
49.4
9 | Providing and fixing sheet cover over expansion joints with iron screws as per design to match the colour/shade of wall treatment- Aluminium fluted strips 3.15 mm thick:150 mm wide |  |  |  |  | 80 | m
| SUB HEAD II : BRICK WORK | [7 empty] | 2.5
10 | Brick work in superstructure above plinth level upto floor V level. cement mortar 1 : 6 ( 1 cement : 6 coarse sand ).
| Outer walls | 2 | 38.8 | 0.23 | 3.8 | 67.8224
| Outer walls | 2 | 28.4 | 0.23 | 3.8 | 49.6432
| inside wall | 8 | 6.35 | 0.23 | 3.8 | 44.3992
| Electr.room | 2 | 4.5 | 0.23 | 3.8 | 7.866
| Electr.room & lift | 4 | 3 | 0.23 | 3.8 | 10.488
| inside wall | 8 | 5.5 | 0.23 | 3.8 | 38.456
| Courtiyad area | 4 | 6.36 | 0.23 | 3.8 | 22.2346
| Courtiyad area | 2 | 6.35 | 0.23 | 3.8 | 11.0998
| open area | 2 | 7.36 | 0.23 | 3.8 | 12.8653
| Stair head room | 4 | 6.35 | 0.23 | 2.4 | 14.0208
| Stair head room | 4 | 3.04 | 0.23 | 2.4 | 6.7123
| inside lift wall | 4 | 3.5 | 0.23 | 4.08 | 13.1376
| inside lift wall | 4 | 2.4 | 0.23 | 4.08 | 9.0086
| head room lift | 4 | 3.5 | 0.23 | 1 | 3.22
| head room lift | 4 | 2.4 | 0.23 | 1 | 2.208
| Pillar | 20 | 0.23 | 0.23 | 1 | 1.058
| Counter slab | 2 | 6.78 | 0.23 | 1.5 | 4.6782
318.918
Deductions
| Door ND | 7 | 1 | 0.23 | 2.1 | 3.381
| TD | 2 | 1 | 0.23 | 2.1 | 0.966
| Windows,NW | 38 | 1.25 | 0.23 | 1.5 | 16.3875 |  |  |  | 254
| Fixed window | 4 | 6.36 | 0.23 | 1.5 | 8.7768
| Fixed window | 2 | 6.35 | 0.23 | 1.5 | 4.3815
| TW | 16 | 0.65 | 0.23 | 1 | 2.392
| Total |  |  |  |  | 36.2848 |  | #VALUE!
| Total less deductions |  |  |  |  | 282.6332 | cum
| say | 282.6332 | cum |  |  |  |  | 47
11 | Half brick masonry with bricks of class designation 50 in super structure & above plinth up to floor V level in cement mortar 1 : 4 ( 1 cement : 4 coarse sand ).
| Toilet walls | 2 | 5.74 | 4.08 |  | 46.8384
| Toilet walls | 16 | 1.5 | 2.4 |  | 57.6
| Toilet walls | 2 | 0.87 | 4.08 |  | 7.0992
|  | 1 | 2.83 | 4.08 |  | 11.5464
|  | 2 | 1.46 | 1.5 |  | 4.38
|  | 2 | 0.8 | 0.8 |  | 1.28
|  | 2 | 1.99 | 4 |  | 15.92
| Parapet | 2 | 38.32 | 1.2 |  | 91.968
|  | 3 | 28.4 | 1.2 |  | 102.24
|  | 2 | 7.9 | 1.2 |  | 18.96
| courtiyad | 2 | 6.35 | 1.2 |  | 15.24
| courtiyad | 4 | 6.36 | 1.2 |  | 30.528
| Doctors toilet | 4 | 3 | 4.08 |  | 48.96
| counter slab pillar | 12 | 0.6 | 0.8 |  | 5.76
[6 empty] | 458.32 | sqm
Deduction for openings
| toilet door | 18 | 0.75 | 2.1 |  | 28.35
| Total deduction |  |  |  |  | 28.35 | sqm
| Total less deductions |  |  |  |  | 429.97 | sqm
| say | 429.97 | sqm
12 | Extra for providing and placing in position 2 Nos 6 mm dia M.S. bars at every third course of half brick masonary ( with F.P.S. bricks). |  |  |  |  | 429.97 | sqm
SUB HEAD :III GRANITE WORK
13 | Providing and fixing 18 mm thick mirror polished, machine cut for kitchen platforms, vanity counters facias and similar locations of required size of approved shade, colour and texture laid over 20 mm thick base cement mortar 1 : 4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing etc. complete at all levels :- Granite of any colour.
Over 1sqm but up to 2sqm
| NS | 2 | 3 | 0.6 |  | 3.6
| NS | 2 | 3.72 | 0.6 |  | 4.464
| Lift face | 2 | 2.4 | 2.5 |  | 12
| Total |  |  |  |  | 20.064 | sqm
14 | Extra for providing edge moulding to 18mm thick marble counters, Vanities etc. including machine polishing to dege to give high gloss finish etc. complete as per design approved by Engineer-in-charge Granite work
|  | 2 | 3 |  |  | 6
|  | 2 | 4.5 |  |  | 9
|  | 2 | 6 |  |  | 12
| Total |  |  |  |  | 27 | Rm
SUB HEAD IV : WOOD WORK
15 | Providing and fixing 18mm thick marine plywood exsterior grade of approved make for cup board shelves including neccessary screws, nails,gum etc complete asper the direction of engineer-in - charge |  |  |  |  | 20 | sqm
16 | Providing and fixing cupboard shutters with 18mm thick marine plywood ISI marked exterior grade of approved make including IInd class teak wood lipping of 18mm wide x12 mm thick with necessary screws,75mm stainless steel handle and bright finished stainless steel piano hinges etc. complete asper direction of Engineer -in-charge |  |  |  |  | 12 | sqm
17 | Providing and fixing 6 brass lever locking mechanism of approved make like godrej etc. for cupboard including all neccessary fittings as directed by the engineer in charge |  |  |  |  | 15 | Each
18 | Providing and fixing M.S. grills of required pattern in frames of windows etc with M.S flats, square or round bars etc all complete:-
Fixed to openings / wooden frames with rawl plugs screws etc.
| window(NW) | 38 | 1.25 | 1.5 |  | 71.25
| courtiyad | 4 | 6.36 | 1.5 |  | 38.16
|  | 2 | 6.35 | 1.5 |  | 19.05
| TW | 16 | 0.65 | 1 |  | 10.4
138.86
| In kg |  |  |  |  | 2221.76 | KG
19 | Providing and fixing fly proof galvanized M.S wire gauze to windows and clerestory windows using galvanized M.S wire gauge with average width of aperture 1.4 mm in both directions with wire of dia 0.63 mm. With 12 mm mild steel u beading
| Courtiyad | 1 | 42 | 0.3 |  | 12.6
| Courtiyad (Old area) | 1 | 28 | 0.3 |  | 8.4
[6 empty] | 21 | sqm
SUB HEAD V : STEEL WORK
20 | Providing and fixing M.S. fan clamp type I of 12 mm dia M.S. bar bent to shape with hooked ends in R.C.C. slabs during laying including painting the exposed portion of loop , all as per standard design complete .
| FF |  |  |  |  | 80
[6 empty] | 80 | Nos
SUB HEAD VI : FLOORING
21 | Providing and fixing 1st quality ceramic glazed tiles conforming to IS:13753 of minimum thickness 5 mm of approvedd make like NITCO, ORIENT, KAJARIA, or equivalent make in all colours, shades except begundy, bottle green, black or any size as approved by Engineer - in - Charge in skirting, risers of steps and dados over 12 mm thick bed of Cement Mortar 1: 3 ( 1 Cement : 3 Coarse sand ) and jointing with grey cement slurry @ 3.3 kg per sqm including pointing in white cement mixed with pigment of matching shade complete.
| wall | 28 | 5.18 |  | 1.5 | 217.56
| wall | 10 | 6.36 |  | 1.5 | 95.4
| wall | 2 | 7.3 |  | 1.5 | 21.9
| wall | 16 | 6.35 |  | 1.5 | 152.4
| Toilet | 4 | 3.5 |  | 1.5 | 21
| Toilet | 4 | 3 |  | 1.5 | 18
| Toilet | 20 | 1.5 |  | 1.5 | 45
| Toilet | 24 | 1.4 |  | 1.5 | 50.4
| Stair | 4 | 7.1 |  | 0.15 | 4.26
|  | 2 | 3.04 |  | 0.15 | 0.912
| Stair passage | 2 | 5.73 |  | 0.15 | 1.719
| Waiting area | 4 | 6.35 |  | 1.5 | 38.1
666.651
Deduction
| toilet door | 18 | 0.75 |  | 1.5 | 20.25 | (-)
| door | 2 | 1 |  | 1.5 | 3 | (-)
| door | 10 | 0.9 |  | 1.5 | 13.5 | (-)
| window | 38 | 1.2 |  | 0.9 | 41.04 | (-)
77.79
[6 empty] | 588.861 | sqm
| Say | 588.861 | sqm
22 | Providing and laying Ceramic glazed floor tiles 300 x 300 mm of not less than 7.5mm thick of 1st quality conforming to IS : 13755 of NITCO, ORIENT, KAJARIA or equivalent make in all colours, shades except White, Ivory, Grey, Fume Red Brown, laid on 20 mm thick Cement Mortar 1:4 ( 1 cement : 4 Coarse sand ) including pointing the joints with white cement and matching pigment etc., complete.
| Tilets | 2 | 5.55 | 6.49 |  | 72.039
| nurses. Toilet | 4 | 1.5 | 1.8 |  | 10.8
[6 empty] | 82.839 | sqm
| Say | 82.839 | sqm
23 | Providing and laying virtified floor tiles of size 60x60 cm thickness 10mm of M/s Jonson or equivalent (Marbonite), Somany, Kajaria, or equivalent in light colours and shades , laid on 3mm thick cemetious polymer based tile adhesive filling the joints with filler to match the colour of tiles complete as directed by the Engineer in Charge.
| Waiting area | 2 | 7.9 | 6.95 |  | 109.81
| passage | 4 | 5.78 | 3 |  | 69.36
| doctors room | 2 | 5.78 | 3 |  | 34.68
| nurses station | 2 | 5.78 | 3 |  | 34.68
| electrical room | 2 | 2.4 | 3.5 |  | 16.8
| electrical room | 2 | 3 | 4.4 |  | 26.4
| gynec ward | 1 | 9.45 | 4.48 |  | 42.336
| female ward | 1 | 13.7 | 4.48 |  | 61.376
| male ward | 1 | 20.3 | 4.84 |  | 98.252
| male ward | 1 | 20.3 | 6.6 |  | 133.98
| passage | 2 | 26.15 | 2 |  | 104.6
| passage | 1 | 6.95 | 5.18 |  | 36.001
| passage | 1 | 6.95 | 6.96 |  | 48.372
| passage | 2 | 3 | 11.13 |  | 66.78
| tread & riser | 52 | 1.4 | 0.45 |  | 32.76
| landng | 4 | 3 | 1.4 |  | 16.8
[6 empty] | 932.987 | sqm
| Say | 932.987 | sqm
SUB HEAD VII : ROOFING
24 | Providing and fixing on wall face unplasticised - Rigid P.V.C rain water pipes conforming to IS : 13592 Type - A including jointing with seal ring conforming to IS : 5382 leaving 10 mm gap for thermal expansion :-
110 mm diameter single socketed pipes .
| long side | 38 | 5 |  |  | 190
| Say |  |  |  |  | 190 | m |  | 84
25 | Providing and fixing unplasticised-P.V.C pipes clips of approved design to unplasticised-P.V.C rain water pipes by means of 50 x 50 x 50 mm hard wood plugs, screwed with M.S screws of required length including cutting brick work and fixing in cement mortar 1 : 4 ( 1 cement : 4 coarse sand ) and making good the walls etc. complete :- | [6 empty] | 420
| a. 110 mm . |  |  |  |  | 120 | nos
26 | Providing and fixing to the inlet mouth of rain water pipe cast iron grating 15 cm diameter and weighing not less than 440 grams. |  |  |  |  | 28 | each
27 | Providing and fixing on wall face unplasticised -P.V.C moulded fittings / accessories for unplasticised - Rigid P.V.C rain water pipes conforming to IS : 13592 Type A including jointing with seal ring conforming to IS 5382 leaving 10 mm gap for thermal expansion :-bend 87.5 degree
a | 110 mm bend. |  |  |  |  | 45 | each
b | Shoe( plain) 110mm |  |  |  |  | 38 | each
28 | Supplying and fixing Leaxan Polycarbonate sheet roofing 4.50mm multiwall bronze (Manufactured by GE Plastics India Private Ltd) over the framework using special MS extrusions of size 50x22.5mmwith rubber gasket applying silicon sealent and support whereever necessary(Rate is inclusive of framework including support, painting etc).Nothing etc shall be paid on pattern of framework.
|  | 2 | 5 | 4 |  | 40 | SQM
29 | Providing and fixing semicircular 110mm PVC pipe for gutter with iron brackets 40 x 3 mm size, bolts , nuts and washers including making necessary connections with rain water pipes complete. |  |  |  |  | 60 | m
SUB HEAD VIII : FINISHING
30 | 15mm cement plaster on rough side of single or half brick wall of mix 1:6 ( 1 cement : 6 fine sand)
1 : 5 ( 1 cement : 5 fine sand)
| Toilet walls | 24 | 1.5 | 2.4 |  | 86.4
| Toilet walls | 8 | 1.6 | 2.4 |  | 30.72
| Toilet walls | 4 | 2 | 2.4 |  | 19.2
| Toilet walls | 2 | 1.8 | 2.4 |  | 8.64
| Toilet walls | 12 | 1.4 | 2.4 |  | 40.32
| duct | 2 | 4.4 | 4.2 |  | 36.96
| Toilet walls | 4 | 3 | 4.08 |  | 48.96
[6 empty] | 271.2 | sqm
Deduction for openings
| toilet door | 18 | 0.75 | 2.1 |  | 28.35
| V | 16 | 0.8 | 0.6 |  | 7.68
| Total deduction |  |  |  |  | 36.03 | sqm
| Total less deductions |  |  |  |  | 235.17 | sqm
| say | 236 | sqm
31 | 12 mm cement plaster of mix : 1:6 (1 cement: 6 fine sand)
| Outer walls | 2 | 7.9 |  | 3.6 | 56.88
| inside walls | 28 | 6.95 |  | 3.6 | 700.56
| inside walls | 4 | 4.4 |  | 3.6 | 63.36
| inside walls | 22 | 5.78 |  | 3.6 | 457.776
| inside walls | 10 | 6.36 |  | 3.6 | 228.96
| inside walls | 2 | 6.35 |  | 3.6 | 45.72
| Lift | 8 | 3.46 |  | 2.1 | 58.128
|  | 8 | 2.4 |  | 2.1 | 40.32
| Stair room | 8 | 8 |  | 2.3 | 147.2
|  | 8 | 4.4 |  | 2.3 | 80.96
| Pillar | 20 | 0.23 |  | 1.5 | 6.9
| Total |  |  |  |  | 1886.764 | Sqm
Deductions
| Doors | 4 | 1 |  | 2.1 | 8.4
| W | 38 | 1.25 |  | 1.5 | 71.25
79.65
| Total less deductions |  |  |  |  | 1807.114 | Sqm
32 | 18 mm cement plaster in two coats under layer 12mm thick cement plaster 1:5 (1cement :5 Coarse sand) finished with a top layer 6mm thick cement plaster 1:6 (1 Cement : 6 Fine sand)
| Out side wall | 6 | 5.18 | 4.2 |  | 130.536
| Out side wall | 6 | 6.36 | 4.2 |  | 160.272
| Out side wall | 2 | 7.9 | 4.2 |  | 66.36
| vertical wall | 4 | 6.35 | 4.2 |  | 106.68
| Stair | 2 | 17 | 2.55 |  | 86.7
| Lift room | 2 | 10.8 | 4.2 |  | 90.72
| Lift room | 2 | 10.8 | 1 |  | 21.6
| parapet wall courtiyad | 4 | 6.36 | 2.5 |  | 63.6
| parapet wall courtiyad | 2 | 6.35 | 2.5 |  | 31.75
| parapet wall | 2 | 38.32 | 2.5 |  | 191.6
| parapet wall | 3 | 28.4 | 2.5 |  | 213
| parapet wall | 2 | 7.9 | 2.5 |  | 39.5
| Say |  |  |  |  | 1202.318 | Sqm
33 | Wall painting with plastic emulsion paint of approved brand and (asian,berger)manufacture to give an even shade. Two or more coats on new work .
[6 empty] | 2043.114 | sqm
34 | Distempering with first quality acrylic distemper (ready mixed) of approved manufactures of required shade (asian,berger)and colour complete ,as per manufactures specification . New work ( three or more coats) .
| sunshade | 1 | 122 | 0.6 |  | 73.2 |  | 33.7
| Ceiling Slab | 1 | 38.82 | 28.4 |  | 1102.488 |  | 29.6
| Ceiling Slab | 2 | 7.9 | 6.95 |  | 109.81
| Total |  |  |  |  | 1285.498
| say |  |  |  |  | 1285 | sqm
35 | Finishing walls with acrylic smooth exterior paint of required shade (asian,berger) : exterior walls |  |  |  |  | 1202.318 | sqm
36 | Painting with synthetic enamel paint of approved brand (asian,berger) and manufacture to give an even shade :- Two or more coats on new work .
Two or more coats on new work .
F Floor
| window(NW) | 38 | 1.25 | 1.5 |  | 71.25
| courtiyad | 4 | 6.36 | 1.5 |  | 38.16
|  | 2 | 6.35 | 1.5 |  | 19.05
| TW | 16 | 0.65 | 1 |  | 10.4
[6 empty] | 138.86 | sqm
| say |  |  |  |  | 138.86 | sqm
37 | Providing and applying plaster of paris putty of 2 mm thickness over plastered surface to prepare the surface even and smooth complete |  |  |  |  | 200 | sqm
SUB HEAD IX : MISCELLANEOUS
38 | Providing and fixing factory made PVC door frame made of PVC extruded section having overall dimension of 48 x 40 mm (tolerance + 1 mm ) with wall thickness 2.0 mm + 0.2 mm, corners of the door frame to be mitred and jointed by means of plastic/M.S. galvanised brackets and stainless steel screws. The hinge side vertical of the frames reinforced by galvanised M.S.tube of size 19 x 19 mm and 1mm + 0.1 mm wall thickness and 3 nos. stainless steel hinges fixed to the frame complete as per manufacturers specification and direction of Engineer - in - charge ( Sintex Plasopan or duroplast)
48 x 40 x 2.0 mm thick PVC frame
| Pvc door | 2 | 5.5 |  |  | 11
| Toilet door | 14 | 5 |  |  | 70
| Toilet door | 5 | 5.1 |  |  | 25.5
| say |  |  |  |  | 106.5 | Rm
39 | Providing and fixing 30 mm thick factory made PVC rigid foam panelled door shutters manufactured by M/S. Rajshri or equivalent made from M.S.tube of 19 gauge thickness, size 19 x19 mm for styles and 15 x 15 mm for top and bottom rails, covered with heat moulded PVC "C" channel of 5 mm thick sheet and 30 x50 mm wide to form styles and 5 mm thick and 75 mm wide PVC sheets for top rail, lock rail and bottom rail on either side and 5 mm thick, 20 mm wide cross PVC sheet as gap insert for top rail ad bottom rail, panelling of 5 mm thick PVC sheet fitted in the M.S.frame welded/ sealed to the styles and rails with 5 x 30 mm PVC sheet beading on either side and joined together with solvent cement adhesive etc., complete as per manufacturers specification and direction of Engineer - in -charge fixed to frames with 4 Nos. M.S.powder coated butt hinges ( for W.C. and bathroom shutters)
|  | 2 | 1 | 2.1 |  | 4.2
|  | 14 | 0.75 | 2.1 |  | 22.05
|  | 5 | 0.9 | 2.1 |  | 9.45
[6 empty] | 35.7 | Sqm
SUB HEAD X : Dismantling & Demolishing
40 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge 1:3:6 or richer mix
| Columns | 37 | 0.6 | 0.6 | 1 | 13.32
|  | 4 | 0.6 | 0.3 | 1 | 0.72
| Stair | 2 | 1.4 | 1 | 1 | 2.8
[6 empty] | 16.84 | CUM
41 | Demolishing R.C.C. work manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per direction of Engineer - in- charge.
| Lift slab | 2 | 4.5 | 3.5 | 0.13 | 4.095
| Duct slab | 2 | 2 | 2 | 0.1 | 0.8
| coping | 1 | 28.4 | 0.4 | 0.1 | 1.136
[6 empty] | 6.031 | CUM
42 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge. In cement mortar
| Parapet wall | 2 | 38.8 | 0.115 | 1 | 8.924
| Parapet wall | 2 | 28.4 | 0.115 | 1 | 6.532
| Courtiyad | 2 | 13.3 | 0.115 | 1 | 3.059
| Courtiyad | 2 | 6.65 | 0.115 | 1 | 1.5295
| Parapet wall pillar | 20 | 0.23 | 0.115 | 1 | 0.529
| lift opening | 2 | 1.8 | 0.23 | 1 | 0.828
| stair | 2 | 2.7 | 0.23 | 2.4 | 2.9808
[6 empty] | 24.3823 | CUM
43 | Taking out doors, windows and clerestory window shutters (steel or wood) including stacking within 50 metres lead: |  |  |  |  | 2 | each
44 | Removing and refixing carefully the existing polycarbonte sheet roofng with steel trusses frame work including necessary cutting removing cleats etc as required.
|  | 2 | 8.5 | 4.5 |  | 76.5
|  | 1 | 14.5 | 8 |  | 116
[6 empty] | 192.5 | sqm
45 | Removing and refixing carefully the existing water tank to First floor roof slab. Include necessary fittings
|  | 6000 lit |  |  |  | 6000 | lit
46 | Removing and refixing carefully the existing supply and distribution water line over the terrace to the First floor of the building including necessary fittings. |  |  |  |  | 400 | m
47 | Dismantling old plaster or skirting raking out joints and cleaning the surface for plaster including disposal of rubbish to the dumping ground within 50 metres lead
|  | 1 | 38.82 |  | 28 | 1086.96
|  | 2 | 7.9 |  | 6.95 | 109.81
[6 empty] | 1196.77 | sqm
SUB HEAD XI : SANITARY INSTALLATIONS& WATER SUPPLY
48 | Providing and fixing water closet squatting pan (Indian type WC pan ) with 100 mm sand cast iron P or S trap, 10 litres low level P.V.C flushing cistern manually controlled device ( handle lever ) conforming to IS: 7231, Parrywarw/Hindware/ Seabird/Orient ( Coral) with all fittings and fixtures complete including cutting and making good the walls and floors wherever required :- White Vitreous Orissa pan of size 580 x 440 mm with integral type foot rests . |  |  |  |  | 4 | each
49 | Providing and fixing white vitreous china pedestal type water closet (European type W.C.pan) with seat and lid, 10 litre low level P.V.C. flushing cistern with manually controlled device ( handle lever ), conforming to IS : 7231, Parryware / Hindware/ Seabrid / Orient ( Coral ) with all fittings and fixtures complete including cutting and making good the walls and flors wherever required :-W.C. pan with ISI marked white solid plastic seat and lid. |  |  |  |  | 8 | each
50 | Providing and fixing wash basin with C.I/M.S brackets painted white ,15 mm C.P brass pillar taps, Kingston / Gem / Techno / Parko, 32 mm C.P brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever required :-
a | Wash basin size 550x400mm with single 15mm C.P.brass pillar tap |  |  |  |  | 10 | each
51 | White Vitreous China Surgeon type wash basin of size660x460 mm with single 15 mm C.P. brass pillar taps cera or equalent. elbow operated levers ISI marked.Elbow operated tap 20mm |  |  |  |  | 4 | each
52 | Providing and fixing 600 x 450 mm beveled edge mirror of superior glass of approved quality complete with 6 mm thick hard board ground fixed to wooden cleats with C.P brass scews and washers complete. |  |  |  |  | 12 | each
53 | Providing and fixing PTMT towel rail complete with brackets fixed to wooden cleats with C.P.brass screws with conceiled fittings arrangement of approved quality colour and make( Prayag or equivalent) 450mm long towel rail with total length of 495mm, width 78mm and effective height of 88mm, weighing not less than 170gms |  |  |  |  | 14 | each
54 | Providing and fixing P.V.C waste pipe for sink or wash basin, including P.V.C waste fittings complete :- Semi rigid pipe :-40 mm dia. |  |  |  |  | 12 | each
55 | Providing and fixing PVC trap of self cleansingdesign withPVC screwed down or hinged grating with or without vent arm complete including cutting and making good the walls andfloors.
a | 100mm inlet and 75mm outlet. |  |  |  |  | 25 | Each
56 | Providing and PTMT Soap Dish Holder having length of 138 mm, breadth 102 mm, height of 75 mm with concealed fitting arrangements, weighing not less than 110 gms ( Prayag or equivalent) |  |  |  |  | 18 | each
57 | Providing and fixing on wall face unplasticised rigid PVC pipes6kg/cm2 confirmong to I.S 13592 Type A including jointing with Seal ring confirming to I.S 5382 leaving 10 mm gap for thermal expansion
Single soaked pipes
a | 75 mm diameter |  |  |  |  | 75 | m
b | 110 mm diameter |  |  |  |  | 190 | m
58 | Providing and jointing PVC pipes of (pressure10Kg/cm2) for water supply including testing of joints, concealing the pipes wherever required etc complete.
a | 20 mm pipe |  |  |  |  | 120 | m
b | 25 mm pipe |  |  |  |  | 100 | m
c | 32mm |  |  |  |  | 20 | m
d | 40mm pipe |  |  |  |  | 100 | m
e | 50mm |  |  |  |  | 50 | m
59 | Providing and fixing PTMT (an Engineering thermo plastic ) (prayag or equivalent) grating of approved quality colour and make 150 mm nominal size square, 18 mm high 100mm dia of the inner of hinged round grating domed shapped with 31 mm waste hole confirming to IS standards, |  |  |  |  | 25 | NOS
60 | Providing and fixing C.P. brass long body bib cock of approved quality conforming to IS : standards and weighing not less than 690 grams: 15mm nominal bore |  |  |  |  | 18 | NOS
61 | Providing and fixing,conforming to IS specification unplasticised rigid PVC pipes(pressure 6 kg/cm2) in drainage lines including cutting,trenching,filling but excluding the cost of fittings and fixtures etc complete
a | Providing and fixing 32mm PVC tank connector |  |  |  |  | 4 | nos
b | Providing and fixing of 75mm pvc plain elbow |  |  |  |  | 24 | nos
c | Providing and fixing of 75mm pvc door elbow |  |  |  |  | 14 | nos
d | Providing and fixing of 75mm pvc plain tee |  |  |  |  | 40 | nos
e | Providing and fixing of 75mm pvc plain bend |  |  |  |  | 49 | nos
f | Providing and fixing of 110mm pvc plain bend |  |  |  |  | 60 | nos
g | Providing and fixing of 110mm pvc plain elbow |  |  |  |  | 50 | nos
h | Providing and fixing of 110mm pvc door elbow |  |  |  |  | 12 | nos
i | Providing and fixing of 110mm pvc door tee |  |  |  |  | 16 | nos
j | Providing and fixing of 110mm pvc air cowl |  |  |  |  | 10 | nos
62 | Providing and fixing C.P. brass bib cock of approved quality conforming to IS : 8931 :- 15 mm nominal bore |  |  |  |  | 4 | each
63 | Providing and fixing C.P. brass stop cock (concealed) of standard design and of approved make conforming to IS 8931 :-15 mm nominal bore |  |  |  |  | 30 | each
64 | Providing and fixing C.P. brass shower hose with 15 or 20 mm inlet 100 mm dia. |  |  |  |  | 4 | each
65 | Providing and fixing unplasticised P.V.C connection pipe with brass unions :-
a | 15mm nominal bore |  |  |  |  | 22 | each
b | 20 mm nominal bore. |  |  |  |  | 5 | each
66 | Providing and fixing gun metal valve with C I wheel of approved quality (screwed end ):-
a | 25mm dia nominal bore |  |  |  |  | 5 | each
b | 40 mm dia nominal bore |  |  |  |  | 10 | each
67 | Providing and fixing of 75 mm pvc air cowl |  |  |  |  | 12 | each
68 | Providing and fixing C.P. brass angle valve for basin mixer and geyser points of approved quality conforming to IS:8931 a) 15 mm nominal bore 15mm nominal bore |  |  |  |  | 20 | Nos
SUB HEAD XII : ALUMINIUM WORK
69a | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular and other section of approved make conforming to IS : 733 and IS : 1285, fixed with rawl plugs and screws or with fixing clips, or with expansion hold fastners including necessary filling up of gaps at junctions, at top, bottom and sides with required P.V.C/neoprene felt etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically where ever required including cleat angle, Aluminium snap beading for glazing / panelling, C.P brass/ stainless steel screws, all complete as per Architectural drawings and the direction of Engineer-in-charge (glazing and panelling to be paid for separately) :- P/F aluminium work for doors, windows, ventilators and partitions etc as per architectural drawings and the directions of Engineer-in-charge. : For fixed portion Powder coated aluminium
| Fixed portion ND | 6 | 0.9 | 2.14 |  | 11.556
| partition ward | 1 | 9.45 | 2.4 |  | 22.68
| partition ward | 1 | 13.7 | 2.4 |  | 32.88
| partition ward | 2 | 20.3 | 2.4 |  | 97.44
| partition ward | 2 | 4.84 | 2.4 |  | 23.232
| partition ward | 2 | 6.6 | 2.4 |  | 31.68
| entrance | 2 | 3 | 3.6 |  | 21.6
| courtitiyad | 4 | 6.36 | 1.5 |  | 38.16
| courtitiyad | 4 | 6.35 | 1.5 |  | 38.1
| stair | 2 | 3 | 1.5 |  | 9
[6 empty] | 326.328 | Sqm
| SAYSQM326.33X2.71=884.35KG |  |  |  |  | 884.3489 | Kg
| window & ventilator NW | 39 | 1.25 | 1.5 |  | 73.125
| Tw | 14 | 0.65 | 0.75 |  | 6.825
|  | 6 | 0.5 | 0.5 |  | 1.5
[6 empty] | 81.45 | sqm
| SAY 81.45 X4.51=367.34KG |  |  |  |  | 367.3395 | Kg
| Total |  |  |  |  | 1251.6884 | Kg
b | b) For shutters of doors, windows and ventilators including providing and fixing hinges /pivots and making provision for fixing of fittings wherever required including the cost of P.V.C / neoprene gasket required (Fittings shall be paid for separately) . P/F aluminium work for doors, windows, ventilators and partitions as per architectural drawings - : For shutters of doors, windows & ventilators- Powder coated aluminium
| Shutter GD | 2 | 1.5 | 2.14 |  | 6.42
| ND2 | 6 | 1.2 | 2.14 |  | 15.408
|  | 6 | 0.9 | 2.14 |  | 11.556
[6 empty] | 33.384 | Sqm
| say 33.38SQMx5.75kg/sqm=191.96kg |  |  |  |  | 191.958 | kg
| WINDOW AND VENTILATOR | 39 | 1.25 | 1.5 |  | 73.125
| TW | 14 | 0.65 | 0.75 |  | 6.825
|  | 6 | 0.5 | 0.5 |  | 1.5
[6 empty] | 81.45 | sqm
| say 81.45SQMx8.33kg/sqm=678.48kg |  |  |  |  | 678.4785 | Kg
| Total |  |  |  |  | 870.4365 | Kg
| say | 870.4365 | kg
70 | Extra for providing and fixing 12 mm thick flat pressed decorative twin finished pre laminated board (both sides decorative super particle board exterior grade) approved variety of fire and moisture ressistant, quality as directed by Engineer - charge (The pre laminated particle board conform to IS:12823) for partition instead of 5mm sheet glass in ( Item No 1&2) above. Full area of panels will be measured for payments
| ward DOOR ND | 6 | 0.9 | 0.9 |  | 4.86
| Partitions ward | 1 | 9.45 | 0.9 |  | 8.505
| Partitions ward | 1 | 13.7 | 0.9 |  | 12.33
| Partitions ward | 2 | 20.3 | 0.9 |  | 36.54
| Partitions ward | 2 | 4.84 | 0.9 |  | 8.712
| Partitions ward | 2 | 6.6 | 0.9 |  | 11.88
| entrance door | 2 | 3 | 0.9 |  | 5.4
| entrance door | 2 | 3 | 1.46 |  | 8.76
[6 empty] | 96.987 | sqm
| say | 96.987 | sqm
71a | Providing and fixing glazing in aluminium doors windows, ventilator shutters and partitions etc. with P.V.C / neoprene gasket etc. complete. as per the Architectural drawings and the directions of Engineer-in- charge. (Cost of aluminium snap beading shall be paid in basic item.) . With glass panes of 5.5 mm thickness (weight not less than 13.75 Kg/Square metre .
| ward DOOR ND | 6 | 0.9 | 1.24 |  | 6.696
| Partitions ward | 1 | 9.45 | 1.24 |  | 11.718
| Partitions ward | 1 | 13.7 | 1.24 |  | 16.988
| Partitions ward | 2 | 20.3 | 1.24 |  | 50.344
| Partitions ward | 2 | 4.84 | 1.24 |  | 12.0032
| Partitions ward | 2 | 6.6 | 1.24 |  | 16.368
| entrance door | 2 | 3 | 1.24 |  | 7.44
[6 empty] | 121.5572 | sqm
b | With glass panes of 4 mm thickness (weight not less than 13.75 Kg/Square metre . | [6 empty] | 554.95
| WINDOW AND VENTILATOR NW | 39 | 1.25 | 1.5 |  | 73.125
| TW | 14 | 0.65 | 0.75 |  | 6.825
| V | 6 | 0.5 | 0.5 |  | 1.5
| Total |  |  |  |  | 81.45 | sqm
| say | 81.45 | sqm
c | Providing and fixing glazing in aluminium doors windows, ventilator shutters and partitions etc. with P.V.C / neoprene gasket etc. complete. as per the Architectural drawings and the directions of Engineer-in- charge. With glass panes of 8.0 mm thickness .
| courtitiyad | 4 | 6.36 | 1.5 |  | 38.16
| courtitiyad | 2 | 6.35 | 1.5 |  | 19.05 | sqm
| stair | 2 | 3 | 1.5 |  | 9 | sqm
[6 empty] | 66.21 | sqm
72 | Providing and fixing aluminium sliding door bolts ISI marked anodised ( anodic coating not less than grade AC 10 as per IS: 1868) transparent or dyed to required colour or shade with nuts and screws etc. complete-
| 300x16mm |  |  |  |  | 8 | each
73 | Providing and fixing aluminium handles ISI marked anodised ( anodic coating not less than grade AC 10 as per IS: 1868) transparent or dyed to required colour or shade with nuts and screws etc. complete-
a | 125 mm |  |  |  |  | 8 | each
b | 100mm |  |  |  |  | 30 | each
74 | Providing and fixing aluminium tower bolts ISI marked anodised ( anodic coating not less than grade AC 10 as per IS: 1868) transparent or dyed to required colour or shade with nuts and screws etc. complete-
a | 250 X 10 mm |  |  |  |  | 8 | each
b | 150x10mm |  |  |  |  | 15 | each
75 | Providing and fixing IS : 3564 marked aluminium extruded section body tubular type universal hydraulic door closer with double speed adjustment with necessary accessories and screws etc. complete. |  |  |  |  | 20 | each
76 | Providing and fixing 100mm brass locks (best make of approved quality) for aluminium doors including necessary cutting and making good etc. complete. |  |  |  |  | 12 | each
77 | Providing fixing aluminium casement windows fastener of required length for aluminium windows with necessary screws etc. complete. Powder coated minimum thickness 50 micron aluminium |  |  |  |  | 92 | each
78 | Providing and fixing brass adjustable friction window stays of approved quality with necessary screws etc to the side hung window as per direction of engineer-in-charge complete. 250mm length |  |  |  |  | 184 | each
79 | Providing and fixing aluminium hanging floor door stopper, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) Transparent or dyed to required colour and shade, with necessary screws etc. complete. Twin rubber stopper |  |  |  |  | 20 | each
80 | Supplying and fixing hand rails with 304 grade and 16 gauge stainless steel pipe for stair cases with 1 No. polished stainless steel pipe of 50mm diameter at top and newel post and SS 304, 16 gauge ,25mm dia 2nos polished stain less steel pipe middle horizontal and 0.30m centre to centre vertical(approximately) welded together , including all neccessary fittings etc.. as per the drawing and direction of the Engineer – in – charge. Hand rails shall be fixed in the floor/steps with expansion hold fasters of required size including drilling etc.complete |  |  |  |  | 37 | RM
SUB HEAD : XIII WATER PROOFING
81 | Cleaning of RCC to remove dust and loosely adhering particles completely.Supply and application of 1st coat with Nitobond SBR Latex mixed with cement mortar, – the polymer modified high quality emulsion, as a coving at the corners of floor and the vertical surface in the sunken area, and between floor and walls in the remaining area..Supply and application of 2nd coat of Brushbond – acrylic Polymer modified cementitious waterproofing coating on the prepared surface in a continuous film on the floor of the sunken area, taking the coating over the vertical surfaces on to the floor and over the coving on to the wall (before tiling) to at least 600mm above the final finished floor level. The coating shall also be continued on to the inner surfaces of the pipe penetration holes. Two coats shall be applied.
|  | 1 | 39 | 29 |  | 1131
|  | 1 | 7.9 | 6.95 |  | 54.905
[6 empty] | 1185.905 | sqm
82 | 12mm cement plaster finished with a floating coat of neat cement of mix
1:3 (1 cement: 3 fine sand)
| main roof | 1 | 39 | 29 |  | 1131
|  | 1 | 7.9 | 6.95 |  | 54.905
| say |  |  |  |  | 1185.905 | sqm

## Electrical &AC,FIRE
Horizontal Extension of First Floor over the existing ward of Taluk Hospital, Karunagapally
Sl. No. | Description of item | Unit | Qty | Rate (Rs in figures & words) | Amount (Rs) | M/s Indtech Rates |  | Remarks
[6 empty] | Rate in Rs | Amount in Rs
Part II A- ELECTRICAL WORKS
1 | Supply of 1x28 watts fluroscent tube fitting sleek with decorative end cap, powder coated CRCA steel channel complete with all electrical accessories like electronic ballast, lamp holder, 28W T5 lamp etc complete as required. (Philips TMS 540 HF / Wipro WRF 80128 SG / GE DMS 28 N N). | Each | 15 |  |  | 1158 | 17370
2 | Supply of ceiling fan 1200 mm sweep, double ball bearing, approved colour and quality with original down rod, suspension shackle, canopy etc with out regulator complete with all accessories as required. (Usha Sonata Max or equivalent) | Each | 70 |  |  | 2412.5 | 168875
3 | Supply of medium duty exhaust fan 300 mm sweep, metal blades of approved colour, for single phase 230 volt, 50Hz AC supply complete with motor, capacitor, metal grill cover and all accessories as required complete. (Usha Turbo Hi speed or equivalent) | Each | 15 |  |  | 2219.5 | 33292.5
4 | Supply of heavy duty type exhaust fan 450 mm sweep,1400 rpm, with metal blade, of approved colour, for single phase 230 volt, 50Hz AC supply complete with motor, capacitor all accessories as required complete. | Each | 2 |  |  | 6272.5 | 12545
5 | Supply and installation of 400 mm sweep, wall fan, swinging type with speed control, necessary adapter, of approved colour, for single phase 230 volt, 50Hz AC supply complete with motor, capacitor all accessories as required complete. (Usha Max Air or equivalent) | Each | 5 |  |  | 2412.5 | 12062.5
6 | Supply and fixing ISI marked Compact Fluroscent Lamp (CFL), 15 watts of approved quality. | Each | 20 |  |  | 241.25 | 4825
7 | Supply and fixing ISI marked Compact Fluroscent Lamp (CFL), 20 watts of approved quality. | Each | 5 |  |  | 241.25 | 1206.25
8 | Supply of 1x36 watts surface mounted luminaire, powder coated CRCA housing, opal acrylic diffuser, decorative end cap, complete with all accessories like electronic ballast, 36W FTL lamp etc complete as required.(Philips TCS019 IxTL-D36W EBE / Wipro WCF 51140 SGW). | Each | 10 |  |  | 3377.5 | 33775
9 | Supply & installation of 1x18 watts recess mounted down light fixture, with aluminium reflector, CRCA sheet housing, complete with all accessories like ballast, 18W CFL lamp etc complete as required. (Wipro WCP 32118 SGW / Philips FBH150 M IxPL-C/4P 18W HFM 240V / GE CFL 1x18 BDN LH R (H) HF) | Each | 10 |  |  | 1833.5 | 18335
10 | Supply of 1x28 watts surface mounting, CRCA powder coated housing, aluminium reflector, pre-wired complete with all accessories like electronic ballast, 28W T5 lamp etc complete as required. (Philips TMS 122 M IxTL5-28W EBE / Wipro WIF 30128 SG / GE GET CI 1x28 C/S HF). | Each | 110 |  |  | 2605.5 | 286605
11 | Supply and installation of 3x36 watts recess mounted, clean room fitiing, front openable, CRCA housing, stainless steel frame, glass cover, complete with all accessories like electronic ballast, 36W CFL lamp etc complete as required. (Philips FBS651 3XPL-L36W EB / Wipro WIP 43336 SGW). | Each | 6 |  |  | 9650 | 57900
12 | Supply and fixing 1x9W Bulk head luminaire with glass cover, powder coated MS wire guard, die-cast aluminium housing, etc complete with all accessories like 9W CFL lamp etc as required. (Philips FXC101 / GE GECPLI). | Each | 10 |  |  | 6755 | 67550
13 | Supply & fixing PVC straight / Angle batten holder with ISI marking including connection etc complete with all accessories as required. | Each | 25 |  |  | 144.75 | 3618.75
14 | Supply and fixing Polished aluminium reflector on the PVC straight / angle batten holder etc complete as required. | Each | 5 |  |  | 337.75 | 1688.75
15 | Supply of the following size 1.1kV grade XLPE insulated PVC sheathed, armoured Aluminium conductor power cable confirming to IS 7098 (part 1) ammended upto date.
15.1 | 4 x 10 Sq mm | Rm | 85 |  |  | 241.25 | 20506.25
15.2 | 4 x 16 Sq mm | Rm | 150 |  |  | 289.5 | 43425
15.3 | 3.5 x 35 Sq mm | Rm | 150 |  |  | 347.4 | 52110
15.4 | 3.5 x 70 Sq mm | Rm | 300 |  |  | 579 | 173700
15.5 | 3.5 x 150 Sq mm | Rm | 120 |  |  | 675.5 | 81060
16 | Supply & fixing modular type computer outlet (RJ-45) with modular base and cover plate, GI box complete with all accessories, connection etc. complete as required. | Each | 4 |  |  | 579 | 2316
17 | Supply and laying CAT 6 cable in the exisitng surface / recessed steel / PVC conduit as required. | Rm | 80 |  |  | 86.85 | 6948
18 | Supply, Installation, Testing & Commissioning of LT panel, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP42, free standing, floor mounting, dust and vermin proof, powder coated, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system with busbars extendable on both sides, including internal wiring with suitable size wires, rotary handle, spreaders, 3mm thick gland plate, hinged type door with neoprene gasket etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification.
INCOMER
1 no. 400A, TPN, 415V, 50Hz microprocessor based MCCB with adjustable overload, shortcircuit protection.
BUSBARS
1 Set of 500A TPN busbars of high conductivity electrolytic quality Aluminium alloy.
1 Set of 32 x 6mm copper busbars of high conductivity electrolytic quality shall be provided throught out the panel for its earthing.
INSTRUMENTS
1 No 3 phase Digital Multi function meter to read V, A, F, Acc class 1.
1 Set of phase indicating lamps, LED type, RYB.
1 Set of 2A 10kA C curve SP control MCB
1 Set of 400/5A, Class 1.0, 10VA, Cast Resin CT
OUTGOING
1no 200A, TPN, AC23A, 415V, 50Hz switch disconnector fuse unit with suitable size Din type HRC fuse as per load.
1no 160A, TPN, AC23A, 415V, 50Hz switch disconnector fuse unit with suitable size Din type HRC fuse as per load.
| 5nos 125A, TPN, AC23A, 415V, 50Hz switch disconnector fuse unit with suitable size Din type HRC fuse as per load. | Each | 1 |  |  | 0 | 0 | Extra Item
19 | Supply, Installation, Testing & Commissioning of Utility panel, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP42, free standing, floor mounting, dust and vermin proof, powder coated, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system, including internal wiring with suitable size wires, rotary handle, spreaders, 3mm thick gland plate, hinged type door with neoprene gasket etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification.
INCOMER
1 no. 200A, FP, AC23, 415V, 50Hz switch disconnector unit (Isolator) complete with handle assembly and door interlock.
BUSBARS
1 Set of 250A TPN busbars of high conductivity electrolytic quality Aluminium alloy.
1 Set of 25 x 3 mm copper busbars of high conductivity electrolytic quality shall be provided throught out the panel for its earthing.
INSTRUMENTS
1 No 3 phase Digital Multi function meter to read V, A, F, Acc class 1.
1 Set of phase indicating lamps, LED type, RYB.
1 Set of 2A 10kA C curve SP control MCB
1 Set of 200/5A, Class 1.0, 10VA, Cast Resin CT
OUTGOING
4nos 63A, TPN, C curve, MCB.
| 4nos 40A, TPN, C curve, MCB. | Each | 1 |  |  | 0 | 0 | Extra Item
20 | Supply, Installation, Testing & Commissioning of LT floor panel, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP42, free standing, floor mounting, dust and vermin proof, powder coated, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system, including internal wiring with suitable size wires, rotary handle, spreaders, 3mm thick gland plate, hinged type door with neoprene gasket etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification.
Incomer
1 no. 125A, FP, AC23, 415V, 50Hz switch disconnector unit (Isolator) complete with handle assembly and door interlock.
Busbar
1 Set of 150A TPN busbars of high conductivity electrolytic quality Aluminium alloy.
1 Set of 25 x 3 mm copper busbars of high conductivity electrolytic quality shall be provided throught out the panel for its earthing.
Instruments
1 No 3 phase Digital Multi function meter to read V, A, F, Acc class 1.
1 Set of phase indicating lamps, LED type, RYB.
1 Set of 2A 10kA C curve SP control MCB
1 Set of 100/5A, Class 1.0, 10VA, Cast Resin CT
Outgoing
3 nos. 63A, TPN, C curve, MCB.
| 4 nos. 32A, TPN, C curve, MCB. | Each | 1 |  |  | 65000 | 65000 | Extra Item
21 | Supply, installation testing and commissioning of 400 A Four pole On load change over switch, AC 23A, confirms to relavant IS code, in powder coated CRCA sheet steel enclosure, with extended type rotary handle with all mounting accessories etc complete as required. | Set | 1 |  |  | 35000 | 35000 | Extra Item
22 | Supply and installation of RYB LED type indication lamp in powder coated CRCA sheet with 2A C curve control MCB and all required mounting accessories etc complete. | Each | 2 |  |  | 434.25 | 868.5
23 | Supply, installation, testing and commissioning of Three phase 2.2 kW / 3 HP pump with motor having suction and delivery pipe, Impeller, motor body of cast Iron and stainless steel shaft. Conform to IS 14220-1994 of Kirloskar Model No: KAS -31.The capacity shall be 19 lps with 8 m head. The starter shall be of DOL Type in CRCA powder coated housing, IP54, with suitable rating 3 phase contactor, overload relay, single phase, under and over voltage protection etc with all mounting accessories as required. | Set | 1 |  |  | 22195 | 22195
24 | Wiring for light point/exhaust fan point/ wall fan point /call bell point with 1.5 sq:mm FR PVC insulated copper conductor single core cable cable in surface/ recessed PVC conduit, with modular switch, modular plate, suitable size G.I. box and earthing the point with 1.5 sq:mm FR PVC insulated copper conductor single core cable etc as required.
24.1 | Gruop B | Point | 80 |  |  | 675.5 | 54040
24.2 | Group C | Point | 200 |  |  | 675.5 | 135100
25 | Wiring for twin control light point with 1.5 sq:mm FR PVC insulated copper conductor single core cable in surface/recessed steel conduit, 2 way modular type switch, modular plate, suitable GI box and earthing the point with 1.5 sq mm. FR PVC insulated copper conductor single core cable etc as required. | Point | 4 |  |  | 965 | 3860
26 | Wiring for light/ power plug with 2x4 sq.mm FR PVC insulated copper conductor single core cable in surface/ recessed PVC coduit along with 1 No 4 sq mm FR PVC insulated copper conductor single core cable for loop earthing as required. | Rm | 200 |  |  | 144.75 | 28950
27 | Wiring for circuit sub main wiring alongwith earthwire with the following sizes of PVC insulated copper conductor, single core cable in surface/ recessed PVC conduit as required.
27.1 | 2x1.5 sq mm +1x1.5 sq. mm earth wire | Rm | 1500 |  |  | 96.5 | 144750
27.2 | 2x2.5 sq mm +1x 2. 5 sq.mm earth wire | Rm | 500 |  |  | 96.5 | 48250
27.3 | 4x6 sq mm + 2x6 sq mm earth wire. | Rm | 150 |  |  | 405.3 | 60795
27.4 | 4x10 sq mm + 2x10 sq mm earth wire. | Rm | 150 |  |  | 579 | 86850
28 | Supplying and drawing following pair, 0.5 sq mm FR PVC insulated copper conductor, un armoured telephone cable in the existing surface/recessed steel/ PVC conduit.
| 2 Pair | Rm | 200 |  |  | 48.25 | 9650
29 | Supplying and drawing co - axial TV cable RG-6 grade, 0.7 mm solid copper conductor PE insulated, shielded with fine tinned copper braid and protected with PVC sheath in the existing surface/recessed steel/ PVC conduit as required. | Rm | 80 |  |  | 86.85 | 6948
30 | Supplying and fixing of following sizes of PVC conduit along with accessaries in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
30.1 | 20 mm | Rm | 1100 |  |  | 57.9 | 63690
30.2 | 25 mm | Rm | 50 |  |  | 77.2 | 3860
31 | Supplying and fixing metal box of following sizes ( Nominal size ) on surface or recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
| 200 mmx 300 mmx 60mm deep | Each | 5 |  |  | 3377.5 | 16887.5
32 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc as required.
32.1 | Telephone socket outlet | Each | 10 |  |  | 579 | 5790
32.2 | TV antena socket outlet | Each | 2 |  |  | 579 | 1158
33 | Supplying and fixing stepped type electronic fan regulator on the existing modular plate and switch box excluding modular plate but including connections etc as required. | Each | 70 |  |  | 482.5 | 33775
34 | Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | Each | 50 |  |  | 57.9 | 2895
35 | Supplying and fixing following size/ modules,GI box along with modular base, cover plate for modular switches in recess etc as required.
| 1 or 2 module( 75 mmx75 mm) | Each | 75 |  |  | 183.35 | 13751.25
36 | Supplying and fixing suitable size G. I box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc as required, | Each | 110 |  |  | 482.5 | 53075
37 | Supplying and fixing suitable size G. I box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 15/16& 5/6 amps modular socket outlet and 15/16 amps modular switch, connection,painting etc as required. | Each | 35 |  |  | 579 | 20265
38 | Supplying and fixing 3 pin , 5 amps ceiling rose on the existing junction box / wooden block including connection etc as required. | Each | 120 |  |  | 57.9 | 6948
39 | Supplying and fixing call bell / buzer suitable for D.C / A.C single phase, 230 volts, complete as required. | Each | 6 |  |  | 386 | 2316
40 | Installation testing and commissioning of pre- wired, fluroscent fitting / compact fluroscent fitting of all types, complete with all accessories and tube etc. directly on ceiling / wall, including connection with 1.5 sq mm FR PVC insulated,copper conductor, single core cable and earthing etc as required. | Each | 145 |  |  | 173.7 | 25186.5
41 | Installation and testing commissioning of prewired, fluorescent fitting/compact fluorescent fitting of all types, complete with all accessories and tube etc, including supplying and fixing ball and socket arrangement, 2 Nos down rods of 20 mm dia x 1.6 mm thick steel conduit up to 30 cm length, painting and wiring the down rods and connection with 1.5 sq mm FR PVC insulated, copper conductor single core cable and earthing etc as required. | Each | 65 |  |  | 646.55 | 42025.75
42 | Providing and fixing extra conduit down rod of 20 mm dia, 2 x 10 cm length wiring with2 x 1.5 sq mm FR PVC insulated, copper conductor, single core cable including painting etc as required. ( Note: More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | Each | 85 |  |  | 386 | 32810
43 | Installation ,testing and commissioning of ceiling fan, including wiring the down rods of standard length { Up to 30 Cm } with 1.5 sq mm FR PVC insulated, copper conductor, single core cable as reqjired. | Each | 70 |  |  | 193 | 13510
44 | Supplying and fixing extra down rod of 10 Cm length G. I pipe, 15 mm dia, heavy guage including painting etc. as required ( Note: More than 5 Cm length shall be rounded to the nearest 10 Cm and 5 Cm or less shall be ignored) | Each | 140 |  |  | 144.75 | 20265
45 | Installation of exhaust fan up to 450 mm sweep in the existing opening, including, making the hole to suit the size of the above fan, making good the damage, connection, testing , commissioning etc as required. | Each | 20 |  |  | 241.25 | 4825
46 | Providing and fixing following capacity TP&N disconnector fuse switch unit inside the existing panel board with ISI marked HRC fuses including drilling holes in cubicle panel, making connections, etc. as required.
46.1 | 63 Amp TP&N | Each | 1 |  |  | 772 | 772
46.2 | 125 Amp TP&N | Each | 1 |  |  | 12545 | 12545
47 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc as required.
| 100 Amp, 16 KA | Each | 2 |  |  | 0 | 0
48 | Supplying and fixing following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, with provision of 100 amps TP 16 KA MCCB as incomer, interconnection between incomer MCCB and bus bars (but without MCB's/ MCCB) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.)
| 8 Way TP | Each | 2 |  |  | 0 | 0
49 | Supplying and fixing following way, three pole and neutral, sheet steel,MCB distributon board consumer unit, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, detachable gland plate, inter connections, phosphatized and powder painted including earthing etc as required.(But with out MCB/RCCB/Isolator)
49.1 | 4 way, Double door | Each | 2 |  |  | 5790 | 11580
49.2 | 6 way, Double door | Each | 2 |  |  | 6755 | 13510
49.3 | 8 way, Double door | Each | 2 |  |  | 0 | 0
50 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's (but without MCB's and incomer ) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.)
| 8 way, Double door | Each | 2 |  |  | 7720 | 15440
51 | Supplying and fixing 5 amps to 32 amps rating, 240 Volts ' C ' series, miniature circuit breaker suitable for inductive load of the following poles in the existing MCB DB complete with connections, testing and commissioning etc as required.
51.1 | Single pole | Each | 100 |  |  | 241.25 | 24125
51.2 | Tripple pole | Each | 16 |  |  | 1737 | 27792
52 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc as required. | Each | 30 |  |  | 38.6 | 1158
53 | Supplying and fixing following rating,four pole,415 volts, residual current circuit breaker { RCCB }, having a sensitivity current up to 300 milli amperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
53.1 | 25 amps | Each | 2 |  |  | 2895 | 5790
53.2 | 40 amps | Each | 4 |  |  | 3184.5 | 12738
53.3 | 63 amps | Each | 4 |  |  | 0 | 0
54 | Supplying and fixing following rating, double pole, 240 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
| 40 amps | Each | 5 |  |  | 1254.5 | 6272.5
55 | Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
55.1 | 40 amps | Each | 6 |  |  | 1254.5 | 7527
55.2 | 63 amps | Each | 4 |  |  | 1254.5 | 5018
56 | Supplying and installing following size of perforated GI cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with GI suspenders including bolts & nuts, suspenders, bends, tees etc as required.
| 300 mm width X 50 mm depth X 1.6 mm thickness | Rm | 50 |  |  | 935.7494 | 46787.47
57 | Supplying and fixing 20 amps, 240 Volts, SPN industril type, socket outlet, with 2 pole and earth, metal enclosed plug top along with 20 amps 'C' series, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket outlet and complete with connections, testing and commissioning etc. as required. | Each | 6 |  |  | 2895 | 17370
58 | Providing and fixing M.V. danger notice plate of 200 mm x 150 mm, made out of mild steel, at least 2 mm thick, and vitreous enamelled white on both sides, and with inscription in single red colour on front side as required. | Each | 2 |  |  | 627.25 | 1254.5
59 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | Set | 4 |  |  | 12062.5 | 48250
60 | Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including connection/ termination with GI thimble etc. as required. | Rm | 80 |  |  | 115.8 | 9264
61 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | Rm | 60 |  |  | 134.0734 | 8044.404 | Extra Item
62 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | Rm | 40 |  |  | 165.864 | 6634.56 | Extra Item
63 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | Rm | 200 |  |  | 41.466 | 8293.2 | Extra Item
64 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
| Above 95 sq. mm and upto 185 sq. mm | Rm | 50 |  |  | 0 | 0
65 | Laying of one number additional PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground in the same trench in one tier horizontal formation including excavation, sand cushioning, protective covering and refilling the trench etc as required.
| Above 95 sq. mm and upto 185 sq. mm | Rm | 50 |  |  | 0 | 0
66 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
66.1 | Upto 35 sq. mm (clamped with 1mm thick saddle) | Rm | 385 |  |  | 67.55 | 26006.75
66.2 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | Rm | 300 |  |  | 0 | 0
66.3 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | Rm | 20 |  |  | 0 | 0
67 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
67.1 | 4 X 10 sq. mm (25mm) | Each | 10 |  |  | 579 | 5790
67.2 | 4 X 16 sq. mm (28mm) | Each | 10 |  |  | 579 | 5790
67.3 | 3½ X 35 sq. mm (32mm) | Each | 8 |  |  | 598.3 | 4786.4
67.4 | 3½ X 70 sq. mm (38mm) | Each | 2 |  |  | 646.55 | 1293.1
67.5 | 3½ X 150 sq. mm (50mm) | Each | 6 |  |  | 0 | 0
Total -(Part II A -Electrical works)
Part II - B - Air Conditioning Works
1 | Supply, installation, testing and commissioning of High Wall mounted Split Air Conditioner of 2TR capacity consisting of high wall mounted type room unit (fan coil) with cordless remote control and one number outdoor condensing unit comprising of enegy efficient suitable rotary compressor for operation on single phase, 230 V, 50Hz supply, fixing the outdoor unit on a raised platform as per manufacturers recommendation and fixing of room (fan coil) unit on wall, upto 10 m distance refrigerant copper piping with 13mm nitrile rubber insulation, providing and making interconnection between room & condenser as per site conditions, comprising of 1" dia drain PVC pipe with insulation 10m, canvas connections, full electrical cabling from power plug near indoor unit and to outdoor unit, vibration isolators, first charge refrigarant gas, min 4star rated as per BEE suitable stabilizer etc complete as required. Make: Carrier /Hitachi/Panasonic/LG/Samsung/ Blue star / Voltas | Set | 2 |  |  | 67550 | 135100
2 | Supply and laying of electrical cabling for 2 TR split unit (between indoor & outdoor unit) | Rm | 50 |  |  | 96.5 | 4825
3 | Supply laying and fixing of additional length suitable dia copper refrigerant piping between indoor and out door unit for 2TR machine with suitable dia ntrile runer insulation. | Rm | 10 |  |  | 700 | 7000
Total -(Part II B -Air conditioning works)
Part II - C - Fire Detection & Alarm System
Fire Alarm System
1.1 | Supply, installation, testing and commissioning of Addressable type Manual Call Point (break glass type) complete with push button, enclosed in box with provision for cable or conduit coupling. The unit to be painted fire red outside, white inside and written 'In case of fire break glass'. | Each | 5 |  |  | 1254.5 | 6272.5
1.2 | Supply, installation, testing and commissioning of Hooter cum Speaker at different locations complete with all fixing accessories, etc. under false ceiling, roof, wall, etc, with a time delay of max 30sec, interconnecting lo loop cable complete as required. | Each | 5 |  |  | 1737 | 8685
1.3 | Supply, Installation, Testing & Commissioning of 16 bit intelligent Addressable Fire Alarm Panel with 1loop ( each loop accessing at least 120 detectors ) including battery backup. The panel shall be microprocessor based with its own micro controller, memory, communication module and fire device loop
interface cards for intelligent initiating and indicating devices and should also be networkable in peer-to-peer basis with other Addressable Fire Alarm Panels. The Panel shall be able to give pin point location of all Fire/Fault conditions of addressable units via the address codes for each unit. The Panel shall also be able to automatically switch off all Control Switches when ever any Alarm is triggered.
The panel shall have 54 Ah SMF Battery, Keypad operation, L C D unit to indicate Fire / Fault Signal of individual unit, in built printer to log all incoming data etc complete in all respects. operation of speakers. Panel shall have :
The Panel shall also have Logic hardware and software built into it for initiating specific AHU tripping, time delay operation of hooter and others as follows :
(a) programming software for the system
(b) automatic system test activates
(c) detector sensitivity adjustments
(d) alarm verification
(e) Alpha/numerical display
(f) provision to connect to PCs and external printers
| (g) Support modbus and bacnet protocol. | Set | 1 |  |  | 115800 | 115800
1.4 | Supply, installation, testing and commissioning of Analogue Addressable type Optical Smoke Detector (photoelectric type) complete with all accessories like base. base box, etc. to be installed under/above false ceiling, roof and concealed space, etc. interconnecting to loop cable complete as required. | Each | 60 |  |  | 3088 | 277920
1.5 | Supply, installation, testing and commissioning of Analogue Addressable type Heat Detector (photoelectric type, Fixed cum-rate of rise type) with range unto 60 deg C complete with all fixing accessories like base, base box, etc. to be installed under/above false ceiling, roof and concealed space, etc. interconnecting to loop cable complete as required. | Each | 5 |  |  | 482.5 | 7237.5
1.6 | Supply, installation, testing and commissioning of addressable Loop Isolators to protect one area or a number of devices with complete set to be installed under/above false ceiling, roof, concealed space, wall, etc. interconnecting to loop cable complete as required. | Each | 1 |  |  | 14475 | 14475
1.7 | Supply, installation, testing, and commissioning of Response Indicators | Each | 25 |  |  | 482.5 | 12062.5
1.8 | Supply and laying of 2x 1.5sq.mm copper armoured FRLS cable ISI marked with proper clamping, supports and terminations. | Rm | 950 |  |  | 173.7 | 165015
Total - Part II C - Fire Detection & Alarm System
| GRAND TOTAL (PART 1A+PART II A+ PART II B+PART II C) | [5 empty] | 607467.5