## Civil Abstract
NAME OF WORK ;- CONSTRUCTION OF WAITING AREA FOR THE EXISTING OP BLOCK FOR THQH TIRURANGADI, MALAPPURAM DISTRICT
PARTA - CIVIL WORKS
SL No | Schedule item no | Description | Unit | Rate Rs(in figures&words) | Amount
DEMOLISHING ANG DISMANTLING
1 | 15.3 | Demolishing R.C.C. work manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per direction of Engineer - in- charge. | Cum
2 | 15.5 | Extra for cutting reinforcement bars manually/ by mechanical means in R.C.C. or R.B. work (Payment shall be made on the cross sectional area of R.C.C. or R.B. work) as per direction of Engineer - in -charge | Sqm
3 | 15.7.4 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge- in cement mortar | Cum
4 | 15.13.1 | Taking out doors, windows and clerestory window shutters (steel or wood) including stacking within 50 metres lead: Of area 3 sq. metres and below | Each
5 | 14.1.2 | Repairs to plaster of thickness 12mm to 20mm in patches of area 2.5 sq. meters and under including cutting the patch in proper shape, raking out joints and preparing and plastering the surface of the walls complete including disposal of rubbish to the dumping ground within 50metres lead With cement mortar 1:4 (1cement: 4 coarse sand). | Sqm
6 | 14.46 | Removing dry or oil bound distemper, water proofing cement paint and the like by scrapping, sand papering and preparing the surface smooth including necessary repairs to scratches etc. complete. | Sqm
EARTH WORK
7 | 2.8.1 | Earth work in excavation by mechanical means (Hydraulic Excavator )/ manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan) including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All kinds of soil. | Cum
8 | 2.25 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. | Cum
9 | 2.35.3.1 | Treatment of soil under floors using chemical emulsion @ one litre per hole, 300 mm apart including drilling 12 mm diameter holes and plugging with cement mortar 1:2 (1 cement : 2 coarse sand) to match the existing floor: With Chlorpyriphos/Lindane E.C. 20% with 1 % concentration | Sqm
PLAIN CEMENT CONCRETE
10 | 4.1.10 | Cement concrete(Cast-in-situ) Providing and laying in position cement concrete of specified grade excluding the cost of centring and shuttering- All work upto plinth level 1:5:10 (1 cement : 5 coarse sand : 10 graded stone aggregate 40mm nominal size) | Cum
11 | 4.11 | Providing and laying damp proof coarse with cement concrete 1:2:4 (1 cement : 2 coarse sand: 4 graded stone aggregate 20mm nominal size) including and applying a coat of residual petroleum bitumen of penetration of penetration 80/100 of approved quality using 1.7 kg per square metre on damp proof coarse after cleaning the surface with brushes and finally with a piece of cloth lightly soaked in kerosene oil 50mm thick | Sqm
REINFORCED CEMENT CONCRETE
12 | 5.1.2 | Providing and laying in position specified grade of reinforced cement concrete,excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level.1:1.5:3 (1 cement : 1.5 coarse sand : 3 graded stone aggregate 20 mm nominal size). | Cum
12a | 5.9.1 | Centering and shuttering including strutting, propping etc. and removal of form for. Foundations, footings, bases of columns, etc. forma ss concrete. | Sqm
13 | Derived Rate from DSR-2013 | Reinforced cement concrete work in beams, suspended floors, roofs having slope upto 15degree, landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases upto floor V level including cost of centering, shuttering, finishing and excluding the cost of reinforcement in 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size) | Cum
13a | 5.9.3 | Centering and shuttering including strutting, propping etc. and removal of form for. Suspended floors, roofs, landings, balconies and access platform. | Sqm
14 | 5.22.6 | Reinforcement for RCC works including straightening, cutting, bending, placing in position and binding all complete. Thermo - Mechanically treated bars (Using Vizac, Tata or SAIL) | Kg
BRICK WORK / LATERITE WORK
15 | 7.1.1 | Random rubble masonry with hard stone in foundation and plinth including levelling up with cement concrete 1:6:12 (1 cement : 6 coarse sand : 12 graded stone aggregate 20mm nominal size) at plinth level with: Cement mortar 1:6 (1 cement : 6 coarse sand) | Cum
16 | LMR | Stone work with neatly dressed selected hard laterite stones of of good quality size 30X20X19 cm in foundation and plinth cement mortar 1:6 (1 cement : 6 course sand) including extra for super structure above plinth level and upto floor V level | Cum
17 | 6.4.1 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in :Cement mortar 1:4 (1 cement : 4 coarse sand | Cum
18 | 6.13.2 | Half Brick masonry with FPS bricks of class designation 75 in superstructure above plinth level upto floor V level in cement mortar 1:4 (1 cement: 4 coarse sand) | Sqm
19 | 6.15 | Extra providing and placing in position 2 nos.6mm dia MS bars at every third course of half brick masonry (with F P S Bricks) | Sqm
STEEL WORK
20 | 9.48.2 | Providing and fixing M.S grills of required pattern in frames of windows etc with M.S.flats,square or round bars etc all complete:- Fixed to openings/wooden frames with rawl plugs screws etc | Kg
21 | 10.16.1 | Steel work in built up tubular ( round, square or rectangular hollow tubes etc.) trusses etc. including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer, including welding and bolted with special shaped washers etc. complete.Hot finished welded type tubes | Kg
ALUMINIUM WORKS
22 | 21.1.1.2 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixed with rawl plugs and screws or with fixing clips, or with expansion hold fasteners including necessary filling up of gaps at junctions, at top, bottom and sides with required PVC/ neoprene felt etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing/panelling. C.P. brass/ stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing and panelling to be paid for separately): For fixed portion Powdercoated Aluminium (Minimum thickness of powdwe coating 50 micron) | Kg
23 | 21.1.2.2 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixed with rawl plugs and screws or with fixing clips, or with expansion hold fasteners including necessary filling up of gaps at junctions, at top, bottom and sides with required PVC/ neoprene felt etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing/panelling. C.P. brass/ stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing and panelling to be paid for separately):For shutters of doors, windows & ventilators including providing and fixing hinges / pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately).Powder coated aluminium (minimum thickness of powder coating 50 micron | Kg
24 | 21.13 | Providing and fixing 100mm brass locks (best make of approved quality) for aluminium doors including necessary cutting and making good etc. complete. | Each
25 | 21.3.2 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with PVC/neoprene gasket etc. complete as per the architectural drawings and directions of engineer-in-charge. (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.5 mm thickness | Sqm
26 | 21.3.1 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with PVC/neoprene gasket etc. complete as per the architectural drawings and directions of engineer-in-charge. (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 4.0 mm thickness | Sqm
27 | 21.2.2 | Providing and fixing12mm thick prelaminated particle board flat pressed three layer or graded wood particle board conforming to IS12823 Grade 1 type II, in panelling fixed in aluminium doors, windows shutters and partition frames with C.P brass/ stainless steel screws etc. complete as per architectural drawings and directions of engineer in charge Pre laminated particle board with decorative lamination on both sides | Sqm
28 | 21.4.1 | Providing and fixing double action hydraulic floor spring of approved brand andmanufacture IS : 6315 marked, for doors including cost of cutting floors as required,embedding in floors and cover plates with brass pivot and single piece M.S. sheetouter box with slide plate etc. complete as per the direction of Engineer-in-chargse With stainless steel cover plate. minimum 1.25 mm thickness | Each
29 | 9.83 | Providing and fixing IS : 3564 marked Aluminium die cast body tubular type universal hydraulic door closer with necessary accessories and screws etc. complete | Each
30 | 9.101.1 | Providing nad fixing aluminium hanging floor door stopper ISImarked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparant or dyed to required colour and shade with necessary screws etc. complete. Single rubber stopper | Each
31 | 9.97.2 | providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent od dyed to required colour or shade with necessary screws etc. complete: 250 x 10 mm | Each
32 | LMR | Providing and fixing aluminium handles for windows, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade, with necessary screws etc. complete | Each
FLOORING WORKS
33 | 11.41.2 | Providing and laying polished vitrified floor tiles of minimum size 600x600mm of thickness 10mm or nearest size of M/s. JOHNSON, KAJARIA, NITCO, SOMANY or equivalent in light colours and shades, with water absorption's less than 0.08% and conforming to IS:15622, laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand) including grouting the joints with cement and matching pigments etc, complete as directed by the Engineer-in-charge. (Basic price of tile not less than 865/m2) | Sqm
34 | 11.36 | Providing and fixing Ist quality ceramic glazed wall tiles conforming to IS: 15622 of minimum 350x250 mm size and thickness 5MM of JOHNSON, NITCO, ORIENT, , KAJARIA ,or approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados,over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand)and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete. (Basic price of tile not less than 400/m2) | Sqm
ROOFING WORKS
35 | LMR | Providing and fixing at all heights false ceiling of 8mm thick PVC hollow sheet including providing and fixing of frame work made of special section power pressed from MS sheet and galvanazied in accordance with zinc coating as per IS :277 and consisting of angle cleat of size 25mm wide x 1.6mm thick with flanges of 22mm and 37mm at1200mm c/c one flange fixed to the ceiling with dash fastner 12.5mm dia x 40mm long with 6mm dia bolts to the angle hangers of (25x25x0.50)mm of required length and other end of the angle hanger being fixed with nuts &bolts to GI channels (45 x 15 x 0.90 )mm running at the rate of 1200mm c/c to which the ceiling section 0.5mm thick bottom wedge of 80mm with tapered flanges of 26mm each having clips of 10.5mm at 450mm c/c shall be fixed in a direction perpendicular to GI chanel with connecting clips made out of 2.64mm dia x 230mm long with GI wire at every junction including fixing the PVC sheet with ceiling section and perimeter chanel 0.50mm thick 27mm high having flanges of 20mm | Sqm
and 30mm long, the perimeter of ceiling fixed to25mm long drive-all screws @ 230mm interval including jointing and fixing to a flush finish of square edges of the board with recommended filler, jointing tapes, finisher and two coats of primer suitable for board as per manufactures specification and also including the cost of making openings for light fittings, grills, diffusers, cutouts made with frame of perimeter channels suitably fixed all complete as per drawing and specification and direction of the Engineer in Charge but excluding the cost of painting
36 | LMR | Providing corrugated G.S. sheet (powder coated) roofing including vertical/curved surface fixed with polymer coated J or L hooks, bolts and nuts 8 mm diameter with bitumen and G.I. limpet washers or with G.I. limpet washers filled with white lead and including a coat of approved steel primer and two coats of approved paint on overlapping of sheets complete (up to any pitch in horizontal/ vertical or curved surfaces) excluding the cost of purlins, rafters and trusses and including cutting to size and shape wherever required. 0.63 mm thick with zinc coating not less than 275 gm/ m² | Sqm
FINISHING WORKS
37 | 13.16.1 | 6mm cement plaster to ceiling of mix 1 : 3 (1 cement : 3 fine sand ) | Sqm
38 | 13.23.2 | Extra for plastering on circular work not exceeding 6 m in radius:In two coats | Sqm
39 | 13.1.1 | 12mm cement plaster on rough side of single or half brick wall of mix 1:4 (1 cement : 4 fine sand) | Sqm
40 | 13.5.1 | 15 mm cement plaster on rough side of single or half brick wall of mix:1:4 (1 cement : 4 coarse sand) | Sqm
41 | 13.60.1 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade. | Sqm
41.a | 13.43.1 | Applying one coat of water thinnable cement primer of approved brand and Water thinnable cement primer. | Sqm
42 | 13.46.1 | Finishing walls with Acrylic Smooth exterior paint of required shade: —New work (Two or more coat applied @ 1.67 ltr/10 sqm over and including basecoat of water proofing cement paint applied @ 2.20 kg/ 10 sqm) | Sqm
43 | 13.26 | Providing and applying plaster of paris putty of 2 mm thickness over plastered surface to prepare the surface even and smooth complete | Sqm
44 | 13.43.1 | Applying one coat of water thinnable cement primer of approved brand and manufacture on wall surface : | Sqm
45 | 13.61.1 | Steel Work painting- Painting with synthetic enamel paint of approved brand and manufacture to give an even shade. Two or more coats on new work | Sqm
INTERNAL WATER SUPPLY & SANITORY INSTALLATIONS
46 | 17.7.3 | Providing and fixing wash basin with C.I/ M.S brackets, 15mm C.P. brass pillar taps Kingston/ Gem/ Techno/ Parko, 32mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls and floors wherever require: White Vitreous China Wash basin size 550x400 mm with a pair of 15 mm C.P. brass pillar taps | Each
47 | 18.21.1.1 | Providing and fixing unplasticised PVC connection pipes with brass unions 30 cm length 15mm nominal bore | Each
48 | 17.28.1.1 | Providing and fixing waste pipe for sink, wash basin or urinals including PVC waste fittings complete:Semi Rigid Pipe-32mm diameter | Each
49 | 17.31 | Providing and fixing 600x450mm bevelled edge mirror 5mm thick of superior glass(of approved quality) complete with 6mm thick hard board ground fixed to wooden cleats with C.P.brass screws and washers complete. | Each
50 | 17.73.2 | Providing and fixing PTMT towel rail complete with brackets fixed to wooden cleats with CP brass screws with concealed fitting arrangement of approved quality and colour. 600 mm long towel rail with total length of 645 mm, width 78 mm and effective height of 88mm, weighing not less than 190 gms. | Each
51 | 18.65 | Providing and fixing PTMT Soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements. Weighing not less than 106 gms. | Each
52 | LMR | Providing and fixing wall face PVC pipe complete including cutting,chasing in walls and making good the walls etc complete.
a |  | 25mm PVC pipe (10kg/sqcm) | RM
b |  | 32mm PVC pipe (10kg/sqcm) | RM
b |  | 32mm PVC pipe (10kg/sqcm) | RM
53 | LMR | Providing and jointing PVC 63mm PVC pipes of (pressure 6 kg/cm2) for drainage line including testing of joints etc complete. (Sullage Down pipe) 63mm diameter (OD) | RM
54 | LMR | Providing and jointing PVC 75mm PVC pipes of (pressure 6 kg/cm2) for drainage line including testing of joints etc complete. (Sullage Down pipe) 75mm diameter (OD) | RM
55 | LMR | Providing and fixingpvc 10 kg bend of specified diamenter including cutting and finishing etc.complete
a |  | 63mm PVC pipe (10kg/sqcm) | Each
b |  | 75mm PVC pipe (10kg/sqcm) | Each
56 | LMR | Providing and fixingpvc 10 kg bend with access door of specified diamenter including cutting and finishing etc.complete
a |  | 63mm PVC pipe (10kg/sqcm)
b |  | 75mm PVC pipe (10kg/sqcm)
57 | LMR | Providing and fixingpvc 10 kg TEE of specified diamenter including cutting and finishing etc.complete
a |  | 63mm PVC pipe (10kg/sqcm) | Each
b |  | 75mm PVC pipe (10kg/sqcm) | Each
58 | LMR | Providing and jointing PVC110mm PVC pipes of (pressure 4 kg/cm2) for drainage line including testing of joints etc complete. (Rain water Down pipe) 110mm diameter (OD) | RM
59 | LMR | Providing and jointing PVC110mm PVC bend of (pressure 4 kg/cm2) for drainage line including testing of joints etc complete. (Rain water Down pipe) 110mm diameter (OD) | Each
60 | LMR | Providing and jointing PVC110mm PVC bend with access door of (pressure 4 kg/cm2) for drainage line including testing of joints etc complete. (Rain water Down pipe) 110mm diameter (OD) | Each
61 | LMR | Providing and jointing PVC110mm PVC TEE of (pressure 4 kg/cm2) for drainage line including testing of joints etc complete. (Rain water Down pipe) | Each
62 | 12.43.2 | Providing and fixing unplasticised-P.V.C pipes clips of approved design to unplasticised-P.V.C rain water pipes by means of 50 x 50 x 50 mm hard wood plugs, screwed with M.S screws of required length including cutting brick work and fixing in cement mortar 1 : 4 (1 cement : 4 coarse sand) and making good the walls etc. complete 110mm | Each
63 | 17.60.1 | Providing and fixing trap of self cleansing design with screwed down or hinged grating with or without vent arm complete, including cost of cutting and making good the walls and floors: 110mm inlet and 110mm outlet pvc. Sand cast iron S&S as per IS: 3989 | Each
64 | 18.58.2.1 | Providing and fixing PTMT (an Engineering thermo plastic ) grating of approved quality colour and make 150 mm nominal size square,100mm diameter of the inner hinged round grating.Rectangular type with circular round lid. 50 mm nominal size square 100 mm dia of the inner hinged round grating. | Each
65 | 18.52.1 | Providing and fixing C.P brass stop cock (concealed) of standard design of approved make conforming to IS 8931. conforming to IS standards 15 mm nominal bore | Each
66 | 18.48 | Providing and placing on terrace (at all floor levels) poly ethlyne water storage tank ISI: 12701 marked with cover and suitable locking arrangement and making necessary holes for inlet, outlet and over flow pipes but with out fittings and the base support for tank | Litres
DRAINAGE WORKS
67 | 19.33 | Constructing soak pit 1.20x1.20x1.20m filled with brickbats including S.W. drain pipe 100 mm diameter and 1.20 m long complete as per standard design. | Each
68 | 19.18.1 | Supplying and fixing C.I. cover without frame for manholes 455x610 mm rectangular C.I. cover (light duty) the weight of the cover to be not less than 23 kg. | Each
69 | 18.17.2 | Providing and fixing gun metal gate valve with CI wheel of approved quality(screwed end) – 32mm nominal bore | Each
TOTAL - PART A CIVIL WORKS

## TOTAL QTY (hidden)
Name of work : RENNOVATION OF GENERAL HOSPITAL AT KALPETTA IN WAYANAD DISTRICT
GENERAL HOSPITAL - KALPETTA
DETAILED ESTIMATE--TOTAL QUANTITY
S.N | Description | Unit | NO | Length | Width | Depth | Quantity
DEMOLISHING ANG DISMANTLING
Demolishing R.C.C. work manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per direction of Engineer - in- charge.
| ground floor | [5 empty] | 0.4
| first floor | [5 empty] | 1
| first floor-kitchen | [5 empty] | 3.5
| second floor | [5 empty] | 1.5
| third floor | [5 empty] | 5
| total | cum |  |  |  |  | 11.4
Extra for cutting reinforcement bars manually/ by mechanical means in R.C.C. or R.B. work (Payment shall be made on the cross sectional area of R.C.C. or R.B. work) as per direction of Engineer - in -charge
| ground floor | [5 empty] | 4
| total | kg |  |  |  |  | 4
Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge
| ground floor | [5 empty] | 5
| first floor-kitchen | [5 empty] | 8
| second floor | [5 empty] | 6
| third floor | [5 empty] | 10
| total | cum |  |  |  |  | 29
Dismantling tile work in floors and roofs laid in cement mortar including stacking material within 50 metres lead.For thickness of tiles 10 mm to 25 mm
| ground floor | [5 empty] | 12
| second floor | [5 empty] | 235
| third floor | [5 empty] | 3
| total | sqm |  |  |  |  | 250
Dismantling aluminium/ Gypsum partitions, doors, windows, fixed glazing and false ceiling including disposal of unserviceable surplus material and stacking of serviceable material with in 50 meters lead as directed by Engineer-in-charge
| ground floor | [5 empty] | 7
| second floor | [5 empty] | 40
| total | sqm |  |  |  |  | 47
Dismantling doors, windows and clerestory windows (steel or wood) shutter including chowkhats, architrave, holdfasts etc. complete and stacking within 50 metres lead :Of area beyond 3 sq. metres
| second floor | [5 empty] | 12
| third floor | [5 empty] | 12
| total | sqm |  |  |  |  | 24
Dismantling steel work in built up sections in angles, tees, flats and channels including all gusset plates, bolts, nuts, cutting rivets, welding etc. including dismembering and stacking within 50metres lead.
| first floor-kitchen | [5 empty] | 550
| second floor | [5 empty] | 1050
| total | kg |  |  |  |  | 1600
Dismantling roofing including ridges, hips, valleys and gutters etc., and stacking the material within 50 metres lead of:G.S. Sheet
| first floor-kitchen | [5 empty] | 28
| second floor | [5 empty] | 55
| total | sqm |  |  |  |  | 83
EARTH WORK
2.31 | Clearing jungle including uprooting of rank vegetation, grass, brus wood, trees and saplings of girth upto 30 cm measured at a height of 1 m above ground level and removal of rubbish upto a distance of 50 m outside the periphery of the area cleared.
| In yard work | [5 empty] | 500
| total | sqm |  |  |  |  | 500
|  | 1OOsqm |  |  |  |  | 5
Surface dressing of the ground including removing vegetation and in-equalities not exceeding 15 cm deep and disposal of rubbish, lead upto 50 m and lift upto 1.5 m.For all kinds of soil
| yard | [5 empty] | 500
| total | sqm |  |  |  |  | 500
|  | 1OOsqm |  |  |  |  | 5
3 | Earth work in excavation by mechanical means (Hydraulic Excavator )/ manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan) including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All kinds of soil.
| yard work | [5 empty] | 80
| total | cum |  |  |  |  | 80
Earth work in excavation by mechanical means (Hydraulic excavator)/ manual means over areas (exceeding 30cm in depth. 1.5m in width as well as 10 sqm on plan) including disposal of excavated earth, with all lead and lift as per the direction of engineer -in -charge
| yard work | [5 empty] | 190
| total | cum |  |  |  |  | 190
4 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m.
| Yard work | [5 empty] | 35
| total | cum |  |  |  |  | 35
5 | Supplying and filling in plinth with quarry dust under floors including watering, ramming, consolidating and dressing complete.
| Yard work | [5 empty] | 12.5
| total | [5 empty] | 12.5
PLAIN CEMENT CONCRETE
Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering1:3:6 (1 Cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size).
| second floor | [5 empty] | 1
| third floor | [5 empty] | 1.5
| total | cum |  |  |  |  | 2.5
6 | Cement concrete(Cast-in-situ) Providing and laying in position cement concrete of specified grade excluding the cost of centring and shuttering- All work upto plinth level 1:5:10 (1 cement : 5 coarse sand : 10 graded stone aggregate 40mm nominal size)
| Yard work | [5 empty] | 19
| total | cum |  |  |  |  | 19
Providing and laying cement concrete in retaining walls, return walls, walls (any thickness) including attached pilasters, columns, piers, abutments, pillars, posts, struts, buttresses, string or lacing courses, parapets, coping, bed blocks, anchor blocks, plain window sills, fillets, sunken floor,etc., up to floor five level, excluding the cost of centering, shuttering and finishing 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size)
| yard work | [5 empty] | 4
| first floor -kitchen | [5 empty] | 2
| third floor | [5 empty] | 3.5
| total | cum |  |  |  |  | 9.5
REINFORCED CEMENT CONCRETE
Providing and laying cement Concrte in retaining walls, return walls (any thickness) including attached pilasters, columns, piers, abutmets, pillars, posts, struts, buttresses,string or lacing courses, parapets, coping bed blocks, anchor blocks, plain window sills, fillets etc upto floor five level, excluding the cost of centring, shuttering and finishing 1:2:4 (1 cement: 2coarse sand : 4 graded stone aggregate 20 mm nominal size)
| yard work | [5 empty] | 8
| total | cum |  |  |  |  | 8
Providing and laying in position specified grade of reinforced cement concrete including the cost of centering,shuttering,finishing and excluding cost of reinforcment -All work upto plinth level. 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size
| yard work | [5 empty] | 60
| total | cum |  |  |  |  | 60
Reinforced cement concrete work in walls (any thickness) including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc upto floor V level including cost of centering, shuttering, finishing and excluding cost of reinforcement in 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20 mm nominal size)
| Yard work | [5 empty] | 8
| first floor -kitchen | [5 empty] | 11
| second floor | [5 empty] | 10
| third floor | [5 empty] | 20
| total | cum |  |  |  |  | 49
Reinforced cement concrete work in beams, suspended floors, roofs having slope upto 15degree, landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases upto floor V level including cost of centering, shuttering, finishing and excluding the cost of reinforcement in 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size)
| yard work-lintels | [5 empty] | 17
| ground floor | [5 empty] | 2
| first floor | [5 empty] | 1
| first floor -kitchen | [5 empty] | 38
| second floor | [5 empty] | 47
| third floor | [5 empty] | 57
| total | cum |  |  |  |  | 162
Reinforcement for RCC works including straightening, cutting, bending, placing in position and binding all complete. Thermo - Mechanically treated bars (Using Vizac, Tata or SAIL)
| yard work | kg |  |  |  |  | 11650
| ground floor | [5 empty] | 200
| first floor | [5 empty] | 100
| first floor -kitchen | [5 empty] | 7200
| second floor | [5 empty] | 8000
| third floor | [5 empty] | 11150
| total | cum |  |  |  |  | 38300
#REF!
Random rubble masonry with hard stone in foundation and plinth including levelling up with cement concrete 1:6:12 (1 cement : 6 coarse sand : 12 graded stone aggregate 20mm nominal size) at plinth level with: Cement mortar 1:6 (1 cement : 6 coarse sand)
| yard work | [5 empty] | 30
| total | cum |  |  |  |  | 30
BRICK WORK / LATERITE WORK
Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in :Cement mortar 1:4 (1 cement : 4 coarse sand
| yard work | [5 empty] | 47
| ground floor | [5 empty] | 4
| first floor -kitchen | [5 empty] | 35
| second floor | [5 empty] | 55
| third floor | [5 empty] | 65
| total | cum |  |  |  |  | 206
Half brick masonry with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level.Cement mortar 1:4 (1 cement :4 coarse sand)
| ground floor | [5 empty] | 20
| first floor | [5 empty] | 20
| first floor -kitchen | [5 empty] | 43
| second floor | [5 empty] | 45
| third floor | [5 empty] | 82
| total | sqm |  |  |  |  | 210
Extra for providing and placing in position 2 Nos. 6mm dia. M.S. bars at every third course of half brick masonry
| ground floor | [5 empty] | 20
| first floor | [5 empty] | 20
| first floor -kitchen | [5 empty] | 43
| second floor | [5 empty] | 45
| third floor | [5 empty] | 82
| total | sqm |  |  |  |  | 210
ALUMINIUM WORKS
Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixed with rawl plugs and screws or with fixing clips, or with expansion hold fasteners including necessary filling up of gaps at junctions, at top, bottom and sides with required PVC/ neoprene felt etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing/panelling. C.P. brass/ stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing and panelling to be paid for separately): For fixed portion Anodised aluminium (anodised transparent or dyed required shade according to IS: 1868, Minimum anodic coating of grade AC 15)
| ground floor | [5 empty] | 400
| first floor | [5 empty] | 250
| first floor -kitchen | [5 empty] | 100
| second floor | [5 empty] | 500
| third floor | [5 empty] | 420
| total | kg |  |  |  |  | 1670
For shutters of doors, windows & ventilators including providing and fixing hinges / pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately).Powder coated aluminium (minimum thickness of powder coating 50 micron
| ground floor | [5 empty] | 300
| first floor | [5 empty] | 100
| first floor -kitchen | [5 empty] | 190
| second floor | [5 empty] | 425
| third floor | [5 empty] | 315
| total | kg |  |  |  |  | 1330
Providing and fixing 100mm brass locks (best make of approved quality) for aluminium doors including necessary cutting and making good etc. complete.
| ground floor | [5 empty] | 16
| first floor | [5 empty] | 5
| first floor -kitchen | [5 empty] | 5
| second floor | [5 empty] | 15
| third floor | [5 empty] | 10
| total | nos |  |  |  |  | 51
Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with PVC/neoprene gasket etc. complete as per the architectural drawings and directions of engineer-in-charge. (Cost of aluminium snap beading shall be paid in basic item): With OPAC glass panes of 4.0 mm thickness
| ground floor | [5 empty] | 3
| second floor | [5 empty] | 31
| total | sqm |  |  |  |  | 34
Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with PVC/neoprene gasket etc. complete as per the architectural drawings and directions of engineer-in-charge. (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.5 mm thickness
| ground floor | [5 empty] | 48
| first floor | [5 empty] | 25
| first floor -kitchen | [5 empty] | 7
| second floor | [5 empty] | 55
| third floor | [5 empty] | 40
| total | sqm |  |  |  |  | 175
Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with PVC/neoprene gasket etc. complete as per the architectural drawings and directions of engineer-in-charge. (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 4.0 mm thickness
| first floor -kitchen | [5 empty] | 25
| second floor | [5 empty] | 28
| third floor | [5 empty] | 33
| total | sqm |  |  |  |  | 86
Providing and fixing 12 mm thick frameless toughened glass door shutter of approved brand and manufacture, including providing and fixing top & bottom pivot & spring type fixing arrangement and making necessary holes etc. for fixing required door fittings, all complete as per direction of Engineer-in-charge (Door handle, lock and stopper etc.to be paid separately).
| GROUND FLOOR | [5 empty] | 4
| total | sqm |  |  |  |  | 4
Providing and fixing12mm thick prelaminated particle board flat pressed three layer or graded wood particle board conforming to IS12823 Grade 1 type II, in panelling fixed in aluminium doors, windows shutters and partition frames with C.P brass/ stainless steel screws etc. complete as per architectural drawings and directions of engineer in charge Pre laminated particle board with decorative lamination on both sides
| ground floor | [5 empty] | 70
| first floor | [5 empty] | 36
| first floor -kitchen | [5 empty] | 6
| second floor | [5 empty] | 55
| third floor | [5 empty] | 43
| total | sqm |  |  |  |  | 210
Providing and fixing double action hydraulic floor spring of approved brand andmanufacture IS : 6315 marked, for doors including cost of cutting floors as required,embedding in floors and cover plates with brass pivot and single piece M.S. sheetouter box with slide plate etc. complete as per the direction of Engineer-in-chargse With stainless steel cover plate
| ground floor | [5 empty] | 20
| first floor | [5 empty] | 4
| first floor -kitchen | [5 empty] | 4
| second floor | [5 empty] | 18
| third floor | [5 empty] | 6
| total | nos |  |  |  |  | 52
Providing and fixing IS : 3564 marked Aluminium die cast body tubular type universal hydraulic door closer with necessary accessories and screws etc. complete
| ground floor | [5 empty] | 18
| first floor | [5 empty] | 15
| first floor -kitchen | [5 empty] | 2
| second floor | [5 empty] | 5
| third floor | [5 empty] | 7
| total | nos |  |  |  |  | 47
Providing nad fixing aluminium hanging floor door stopper ISImarked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparant or dyed to required colour and shade with necessary screws etc. complete. Single rubber stopper
| ground floor | [5 empty] | 18
| first floor | [5 empty] | 15
| first floor -kitchen | [5 empty] | 2
| second floor | [5 empty] | 5
| third floor | [5 empty] | 7
| total | nos |  |  |  |  | 47
providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent od dyed to required colour or shade with necessary screws etc. complete: 250 x 10 mm
| ground floor | [5 empty] | 18
| first floor | [5 empty] | 7
| first floor -kitchen | [5 empty] | 11
| second floor | [5 empty] | 23
| third floor | [5 empty] | 13
| total | nos |  |  |  |  | 72
Providing and fixing window handles with necessary screws etc. complete-
| first floor -kitchen | [5 empty] | 33
| second floor | [5 empty] | 40
| third floor | [5 empty] | 45
| total | nos |  |  |  |  | 118
Providing and fixing aluminium tubular handle bar 32 mm outer dia, 3.0 mm thick & 2100 mm long with SS screws etc .complete as per direction of Engineer-in-Charge.Powder coated minimum thickness 50 micron aluminium tubular handle bar.
| ground floor | [5 empty] | 2
| first floor | [5 empty] | 2
| first floor -kitchen | [5 empty] | 2
| second floor | [5 empty] | 8
| third floor | [5 empty] | 2
| total | nos |  |  |  |  | 16
STEEL WORK
Providing and fixing G.I. chain link fabric fencing of required width in mesh size 25x25 mm made of G.I. wire of dia. 3mm including strengthening with 2mm dia. wire or nuts, bolts and washers as required complete as per the direction of Engineer-in-charge
yard work
| total | [5 empty] | 60
Providing and fixing stainless steel 12mm dia bar bent to shape with hooked ends in R.C.C. slabs during laying including, all as per standard design complete.
| first floor -kitchen | [5 empty] | 15
| second floor | [5 empty] | 15
| third floor | [5 empty] | 15
| total | nos |  |  |  |  | 45
Providing and fixing M.S grills of required pattern in frames of windows etc with M.S.flats,square or round bars etc all complete:- Fixed to openings/wooden frames with rawl plugs screws etc
| yard work | [5 empty] | 90
| first floor -kitchen | [5 empty] | 380
| second floor | [5 empty] | 420
| third floor | [5 empty] | 425
| total | kg |  |  |  |  | 1315
Supplying and fixing 1.10m height hand rails for stair cases with 2 Nos. polished stainless steel tube of outer diameter 50mm at top and bottom with wall thickness not less than 1.60mm as per SS 304 vertical members of 50mm diameter pipe 1.00m length(approximately) welded together at 1.50m center to center and providing and fixing 2 nos 32 mm outer diameter stainless steel tube horizontally between the top and bottom tubes including fixing with steel nuts and bolts as per the direction of the Engineer – in – charge. Hand rails shall be fixed in the floor/steps with expansion hold fasters of required size including drilling etc. complete.
| first floor -kitchen | [5 empty] | 90
| second floor | [5 empty] | 115
| third floor | [5 empty] | 115
| total | kg |  |  |  |  | 320
Steel work welded in built up section / framed work including cutting ,hoisting, fixing I position and applying a priming coat of approved steel primer using structural steel etc. as required.In grating ,frames,guard bar, ladder, railings, brackets, gates and similar works.
| yard work | [5 empty] | 500
| total | kg |  |  |  |  | 500
Steel work in built up tubular ( round, square or rectangular hollow tubes etc.) trusses etc. including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer, including welding and bolted with special shaped washers etc. complete.Hot finished welded type tubes
| yard work | [5 empty] | 4500
| total | kg |  |  |  |  | 4500
Supplying and fixing rolling shutters of approved make, made of required size M.S. laths, interlocked together through their entire length and jointed together at the end by end locks, mounted on specially designed pipe shaft with brackets, side guides and arrangements for inside and outside locking with push and pull operation complete, including the cost of providing and fixing necessary 27.5 cm long wire springs manufactured from high tensile steel wire of adequate strength conforming to IS: 4454 – part 1 and M.S. top cover of required thickness for rolling shutters:80x1.25 mm M.S. laths with 1.25 mm thick top cover
| yard work | [5 empty] | 8
| total | sqm |  |  |  |  | 8
Providing and fixing ball bearing for rolling shutters.
| yard work | nos |  |  |  |  | 1
| total | [5 empty] | 1
Extra for providing grilled rolling shutters manufactured out of 8 mm dia. M.S. bar instead of laths as per design approved by Engineer-in-charge.(area of grill to be measured).
| yard work | [5 empty] | 2
| total | nos |  |  |  |  | 2
ROOFING WORKS
Providing and laying water proofing treatment in sunken portion of WCs, bathroom etc., by applying cement slurry mixed with water proofing cement compound consisting of applying : (a) First layer of slurry of cement @ 0.488 kg/sqm mixed with water proofing cement compound @ 0.253 kg/sqm. This layer will be allowed to air cure for 4 hours (b) Second layer of slurry of cement @ 0.242 kg/sqm mixed with water proofing cement compound @ 0.126 kg/sqm. This layer will be allowed to air cure for 4 hours followed with water curing for 48 hours The rate includes preparation of surface, treatment and sealing of all joints,corners, junctions of pipes and masonry with polymer mixed slurry.
| second floor | [5 empty] | 8
| third floor | [5 empty] | 12
| total | sqm |  |  |  |  | 20
Extra for providing and mixing water proofing material in cement plaster work in proportion recommended by the manufacturers.
yard work
ground floor
first floor
| first floor -kitchen | [5 empty] | 16
| third floor | [5 empty] | 22
| total | BAGS |  |  |  |  | 38
Providing and fixing at all height false ceiling of 12.5 mm thick tapered edge gypsum board conforming to IS : 2095/calcium silicate boards, including providing and fixing of frame work made of special sections power pressed from M.S. sheet and galvanised in accordance with zinc coating 600 as per IS : 277 and consisting of angle cleats of size 25mm wide x 1.6mm thick with flanges of 22mm and 37mm at 1200mm centre to centre one flange fixed to the ceiling with dash fastner 12.5mm diax40mm long with 6mm dia bolts to the angle hangers of 25x25x5mm of required length, and other end of angle hanger being fixed with nut and bolts to G.I. channels 45x15x0.9mm running at the rate of 1200mm centre to centre to which the ceiling section 0.5mm thick botton wedge of 80mm with tapered flanges of 26mm each having clips of 10.5mm at 450mm centre to centre shall be fixed in a direction perpendicular to G.I. channel with connecting clips made out of 2.64mm diax230mm long G.I. wire at every junction including fixing the gypsum board with ceiling section and perimeter channels 0.5mm thick 27mm and as per detail specificationPartition Gypsum board
| second floor | [5 empty] | 800
| TOTAL | sqm |  |  |  |  | 800
Providing and fixing 15cm wide &45 cm overall semi circular plain GS sheet gutter with iron bracket 40x3 size washers including making nessassary connections with rain water pipe complete. 0.63mm thick zink coating not less than 275kg/m2
| yard work | rm |  |  |  |  | 60
total
Providing corrugated G.S. sheet roofing including vertical/curved surface fixed with polymer coated J or L hooks, bolts and nuts 8 mm diameter with bitumen and G.I. limpet washers or with G.I. limpet washers filled with white lead and including a coat of approved steel primer and two coats of approved paint on overlapping of sheets complete (up to any pitch in horizontal/ vertical or curved surfaces) excluding the cost of purlins, rafters and trusses and including cutting to size and shape wherever required.0.63 mm thick with zinc coating not less than 275gm/ m²
| yard work | [5 empty] | 220
| total | sqm |  |  |  |  | 220
FINISHING WORKS
12mm cement plaster on rough side of single or half brick wall finished with a floating coat of neat cement of mix 1:4 ( 1 cement : 4 fine sand)
| yard work | [5 empty] | 390
| ground floor | [5 empty] | 77
| first floor | [5 empty] | 28
| first floor -kitchen | [5 empty] | 485
| second floor | [5 empty] | 945
| third floor | [5 empty] | 450
| total | sqm |  |  |  |  | 2375
6mm cement plaster to ceiling of mix 1 : 3 (1 cement : 3 fine sand )
| first floor -kitchen | [5 empty] | 210
| second floor | [5 empty] | 260
| third floor | [5 empty] | 270
| total | sqm |  |  |  |  | 740
Extra for plastering on circular work not exceeding 6 m in radius:In two coats
| second floor | [5 empty] | 45
| total | sqm |  |  |  |  | 45
15mm cement plaster on rough side of single or half brick wall finished with a floating coat of neat cement of mix 1:5 ( 1 cement :5 fine sand)
| yard work | [5 empty] | 380
| first floor -kitchen | [5 empty] | 226
| second floor | [5 empty] | 320
| third floor | [5 empty] | 450
| total | sqm |  |  |  |  | 1376
Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade in two or more coats on new work, including finishing walls with Deluxe Multi surface paint system for interiors and exteriors using Primer as per manufacturers specifications: Two or more coats applied on walls @ 1.25 ltr/10 sqm over and including one coat of Special primer applied @ 0.75 ltr / 10 sqm
| yard work | [5 empty] | 390
| ground floor | [5 empty] | 77
| first floor | [5 empty] | 28
| first floor -kitchen | [5 empty] | 550
| second floor | [5 empty] | 2720
| third floor | [5 empty] | 720
| total | sqm |  |  |  |  | 4485
Finishing walls with Acrylic Smooth exterior paint of required shade: —New work (Two or more coat applied @ 1.67 ltr/10 sqm over and including basecoat of water proofing cement paint applied @ 2.20 kg/ 10 sqm)
| yard work | [5 empty] | 380
| first floor -kitchen | [5 empty] | 226
| second floor | [5 empty] | 320
| third floor | [5 empty] | 450
| total | sqm |  |  |  |  | 1376
Providing and applying plaster of paris putty of 2 mm thickness over plastered surface to prepare the surface even and smooth complete
| second floor | [5 empty] | 1510
| total | sqm |  |  |  |  | 1510
Applying one coat of water thinnable cement primer of approved brand and manufacture on wall surface :
| second floor | [5 empty] | 330
| Third floor | [5 empty] | 270
| total | sqm |  |  |  |  | 600
Finishing with Epoxy paint (two or more coats) at all locations prepared and applied as per manufacturer's specifications including appropriate priming coat, preparation of surface, etc. complete.On concrete work
| second floor | [5 empty] | 830
| total | sqm |  |  |  |  | 830
Steel Work painting- Painting with synthetic enamel paint of approved brand and manufacture to give an even shade. Two or more coats on new work
| yard work | [5 empty] | 5100
| first floor -kitchen | [5 empty] | 25
| second floor | [5 empty] | 28
| third floor | [5 empty] | 30
| total | sqm |  |  |  |  | 5183
FLOORING WORKS
Providing and laying polished vitrified floor tiles of minimum size 600x600mm of thickness 10mm or nearest size of M/s. JOHNSON, KAJARIA, NITCO, SOMANY or equivalent in light colours and shades, with water absorption's less than 0.08% and conforming to IS:15622, laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand) including grouting the joints with cement and matching pigments etc, complete as directed by the Engineer-in-charge.
| first floor -kitchen | [5 empty] | 146
| second floor | [5 empty] | 251
| third floor | [5 empty] | 145
| total | sqm |  |  |  |  | 542
Providing and laying anti skid ceramic floor tiles of minimum 400x400 mm size for toilets (7.5mm thickness or nearest size) M/s. JOHNSON, KAJARIA, NITCO, SOMANY or equivalent of 1st quality conforming to IS: 15622 of approved make in all colours, shades, except white, ivory, grey, fume red brown laid on 20mm thick bed of cement mortar 1:4 (1 cement : 4 coarse sand) including pointing the joints with white cement and matching pigments etc complete.
| yard work | [5 empty] | 15
| ground floor | [5 empty] | 6
| first floor | [5 empty] | 6
| second floor | [5 empty] | 4
| third floor | [5 empty] | 13
| total | sqm |  |  |  |  | 44
Providing and fixing Ist quality ceramic glazed wall tiles conforming to IS: 15622 of minimum 350x250 mm size and thickness 5MM of JOHNSON, NITCO, ORIENT, , KAJARIA ,or approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados,over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand)and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete
| yard work | [5 empty] | 55
| ground floor | [5 empty] | 20
| first floor | [5 empty] | 21
| first floor -kitchen | [5 empty] | 110
| second floor | [5 empty] | 180
| third floor | [5 empty] | 255
| total | sqm |  |  |  |  | 641
Providing and fixing 18mm thick gang saw cut mirror polished (premoulded and prepolished) machine cut for kitchen platforms, vanity counters, window sills, facias and similar locations of required size of approved shade, colour and texture laidover 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing moulding and polishing to edge to give high gloss finish etc. complete at all levels. Granite of any colour & Shade
| ground floor | [5 empty] | 26
| first floor | [5 empty] | 20
| first floor -kitchen | [5 empty] | 7.5
| second floor | [5 empty] | 18
| third floor | [5 empty] | 20
| total | sqm |  |  |  |  | 91.5
Providing edge moulding to 18mm thick marble stone counters, Vanities etc. including machine polishing to edge to give high gloss finish etc. complete as per design approved by Engineer-in-Charge.
| ground floor | [5 empty] | 40
| first floor | [5 empty] | 20
| first floor -kitchen | [5 empty] | 11
| second floor | [5 empty] | 30
| third floor | [5 empty] | 38
| total | rm |  |  |  |  | 139
Providing and laying 60mm thick factory made cement concrete interlocking paver blocks of M - 30 grade made by block making machine with strong vibratory compaction and of approved size and design/ shape laid in required colour and pattern over and including 50mm thick compacted bed of coarse sand, filling the joints with coarse sand etc all complete as per the direction of Engineer in charge.
| yard work | [5 empty] | 725
| total | sqm |  |  |  |  | 725
Providing and laying at or near ground level factory made kerb stone of M-25 grade cement concrete in position to the required line, level and curvature, jointed with cement mortar 1:3 (1 cement: 3 coarse sand) including making joints with or without grooves (thickness of joints except at sharp curve shall not to more than 5mm), including making drainage opening wherever required complete etc. as per direction of Engineer-in-charge (length of finished kerb edging shall be measured for payment). (Precast C.C. kerb stone shall be approved by Engineer-in-charge
| yard work | cum |  |  |  |  | 60
| total | [5 empty] | 60
#REF!
Providing and fixing factory made UPVC door frame of Rajashri or equivalent make made of UPVC extruded section having an overall dimension as. Below(tolerance+1mm) with wall thickness 2.0mm+/;0.2mm, corners of the door frame to be jointed with galvanized brackets and stainless steel screws, joint mitred plastic wilded. the hinge side vertical of the frames reinforced by galvanized M.S. tube of size 19x19mm and 1mm +/- 0.1mm wall thickness and 3 nos. stainless steel hinges fixed to the frame complete as per manufacturers specification and direction of Engineer-in-charge:Extruded section Profile size 42x50mm.
| yard work | [5 empty] | 21
| ground floor | [5 empty] | 21
| second floor | [5 empty] | 41
| third floor | [5 empty] | 47
| total | rm |  |  |  |  | 130
Providing and fixing to existing door frames.30mm thick factory made Rajashri or equivalent make Polyvinyl Chloride(PVC) door shutter and rails of a UPVC profile section of size 30mmx60mm and wall thickness 2mm+/-0.2mm with inbuilt decorative moulding edging on one side. The styles and rails with plastic brackets of size 75x220mm mitre and welded at the corners. The-stiles of the shutter reinforced by inserting galvanized M.S. tube of size 25x20mm and 1mm+/-0.1mm wall thickness. The lock rail made up of 'H' section, a UPVC profile section of size 30mmx100mm and 2mm+/-0.2mm wall thickness welded to the shutter style with a UPVC profile section single panel of size not less than 620mm,having overall thickness of 20mm and 1mm+/-0.1mm wall thickness with 20mm panel beading of suitable size, as per manufactures specification and direction of Engineer-in-charge.
| yard work | [5 empty] | 10
| ground floor | [5 empty] | 8
| second floor | [5 empty] | 7
| third floor | [5 empty] | 18
| total | sqm |  |  |  |  | 43
INTERNAL WATER SUPPLY & SANITORY INSTALLATIONS
Providing and fixing water closet squatting pan (Indian type W.C. pan ) with 100mm sand cast Iron P or S trap, 10 litre low level white P.V.C. flushing cistern, including flush pipe, with manually controlled device (handle lever) conforming to IS : 7231, with all fittings and fixtures complete including cutting and making good the walls and floors wherever required :White Vitreous china Orissa pattern W.C. pan of size 580x440mm with integral type foot rests.
| yard work | [5 empty] | 4
| third floor | [5 empty] | 4
| total | nos |  |  |  |  | 8
Providing and fixing white vitreous china pedestal type water closet (European type W.C. pan) with seat and lid, 10 litre low level white P.V.C. flushing cistern, including flush pipe, with manually controlled device (handle lever), conforming to IS : 7231, with all fittings and fixtures complete including cutting and making good the walls and floors wherever required :W.C. pan with ISI marked white solid plastic seat and lid
| second floor | [5 empty] | 2
| third floor | [5 empty] | 3
| total | nos |  |  |  |  | 5
Providing and fixing white vitreous china flat back half stall urinal of size 580x380x350mm with white PVC automatic flushing cistern, with fittings, standard size C.P. brass flush pipe, spreaders with unions and clamps (all in C.P. brass) with waste fitting as per IS : 2556, C.I. trap with outlet grating and other couplings in C.P. brass including painting of fittings and cutting and making good the walls and floors wherever required Single half stall urinal with 5 litre P.V.C. automatic flushing cistern
| yard work | [5 empty] | 2
| total | nos |  |  |  |  | 2
Providing and fixing wash basin with C.I/ M.S brackets, 15mm C.P. brass pillar taps Kingston/ Gem/ Techno/ Parko, 32mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls and floors wherever require: White Vitreous China Wash basin size 550x400 mm with a pair of 15 mm C.P. brass pillar taps
| yard work | nos |  |  |  |  | 4
| first floor | [5 empty] | 6
| first floor -kitchen | [5 empty] | 4
| second floor | [5 empty] | 2
| third floor | [5 empty] | 4
| total | nos |  |  |  |  | 20
Providing and fixing unplasticised PVC connection pipes with brass unions 30 cm length 15mm nominal bore
| yard work | nos |  |  |  |  | 10
| first floor | [5 empty] | 8
| first floor -kitchen | [5 empty] | 5
| second floor | [5 empty] | 5
| third floor | [5 empty] | 4
| total | nos |  |  |  |  | 32
Providing and fixing waste pipe for sink, wash basin or urinals including PVC waste fittings complete:Semi Rigid Pipe-32mm diameter
| yard work | nos |  |  |  |  | 6
| first floor | [5 empty] | 8
| first floor -kitchen | [5 empty] | 5
| second floor | [5 empty] | 2
| third floor | [5 empty] | 4
| total | nos |  |  |  |  | 25
Providing and fixing stainless steel scurb 2500x600x800mm with C.I brackets and stainless steel plug 40mm including painting of fittings and brackets ,cutting and making good the walls wherever required a)Scub with drain board
| first floor | [5 empty] | 2
| total | nos |  |  |  |  | 2
Providing and fixing Salem stainless steel A ISI 304 (18/8) kitchen sink as per IS 13983 with C.I brackets and stainless steel plug 40mm including painting of fittings and brackets, cutting and making good the walls wherever required a) Kitchen sink without drain board
| first floor -kitchen | [5 empty] | 2
| total | nos |  |  |  |  | 2
Providing and fixing 600x450mm bevelled edge mirror 5mm thick of superior glass(of approved quality) complete with 6mm thick hard board ground fixed to wooden cleats with C.P.brass screws and washers complete.
| yard work | nos |  |  |  |  | 4
| first floor | [5 empty] | 7
| first floor -kitchen | [5 empty] | 4
| second floor | [5 empty] | 2
| third floor | [5 empty] | 15
| total | nos |  |  |  |  | 32
Providing and fixing C.P towel rail complete with brackets fixed to wooden cleats with C.P.brass screws with conceiled fittings arrangement of approved quality ,size and make
| first floor | [5 empty] | 15
| first floor -kitchen | [5 empty] | 2
| second floor | [5 empty] | 4
| third floor | [5 empty] | 6
| total | nos |  |  |  |  | 27
Providing and fixing S.S soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements. Weighing not less than 106 gms.
| yard work | nos |  |  |  |  | 2
| first floor | [5 empty] | 15
| first floor -kitchen | [5 empty] | 4
| second floor | [5 empty] | 10
| third floor | [5 empty] | 15
| total | [5 empty] | 46
nos
Providing and jointing PVC 63mm PVC pipes of (pressure 6 kg/cm2) for drainage line including testing of joints etc complete. (Sullage Down pipe) 63mm diameter (OD)
| yard work | [5 empty] | 70
| first floor | [5 empty] | 15
| first floor -kitchen | [5 empty] | 70
| second floor | [5 empty] | 30
| third floor | [5 empty] | 120
| total | rm |  |  |  |  | 305
Providing and fixing unplasticised-P.V.C pipes clips of approved design to unplasticised-P.V.C rain water pipes by means of 50 x 50 x 50 mm hard wood plugs, screwed with M.S screws of required length including cutting brick work and fixing in cement mortar 1 : 4 (1 cement : 4 coarse sand) and making good the walls etc. complete 110mm
| first floor | [5 empty] | 15
| first floor -kitchen | [5 empty] | 50
| second floor | [5 empty] | 30
| third floor | [5 empty] | 60
| total | nos |  |  |  |  | 155
Providing and fixing on wall face unplasticised- Rigid PVC rain water pipes conforming to IS:13592 type A including jointing with seal ring conforming to IS:5382 leaving 10mm gap for thermal expansion (i) Single socketed pipes – 110mm diameter OD
| second floor | [5 empty] | 30
| third floor | [5 empty] | 125
| total | rm |  |  |  |  | 155
Providing and fixing on wall face unplasticised - PVC moulded fittings/ accessories for unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion: Bend 87.5°. 110 mm bend
| second floor | [5 empty] | 3
| third floor | [5 empty] | 25
| total | nos |  |  |  |  | 28
Providing and fixing on wall face unplasticised - PVC moulded fittings/ accessories for unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion. Single tee without door:110x110x110mm
| second floor | [5 empty] | 3
| third floor | [5 empty] | 12
| total | nos |  |  |  |  | 15
Providing and fixing wall face PVC pipe complete including cutting,chasing in walls and making good the walls etc complete.
25mm PVC pipe (10kg/sqcm)
| yard work | [5 empty] | 25
| first floor | [5 empty] | 25
| first floor -kitchen | [5 empty] | 25
| second floor | [5 empty] | 20
| third floor | [5 empty] | 110
| total | rm |  |  |  |  | 205
32mm PVC pipe (10kg/sqcm)
| yard work | [5 empty] | 100
| first floor | [5 empty] | 32
| first floor -kitchen | [5 empty] | 40
| third floor | [5 empty] | 125
| total | rm |  |  |  |  | 297
50mm PVC pipe (10kg/sqcm)
| yard work | [5 empty] | 75
| first floor -kitchen | [5 empty] | 50
| third floor | [5 empty] | 250
| total | rm |  |  |  |  | 375
Providing and fixing trap of self cleansing design with screwed down or hinged grating with or without vent arm complete, including cost of cutting and making good the walls and floors: 110mm inlet and 110mm outlet pvc
| yard work | [5 empty] | 7
| first floor -kitchen | [5 empty] | 6
| second floor | [5 empty] | 6
| third floor | [5 empty] | 4
| total | nos |  |  |  |  | 23
Providing and fixing PTMT (an Engineering thermo plastic ) grating of approved quality colour and make 150 mm nominal size square,100mm diameter of the inner hinged round grating. Rectangular type with circular round lid
| yard work | nos |  |  |  |  | 7
| first floor -kitchen | [5 empty] | 6
| third floor | [5 empty] | 6
| total | nos |  |  |  |  | 19
Providing and fixing CP brass long body bib cock of approved quality confirming to IS standards weighing not less than 690gms 15mm nominal bore
| first floor | [5 empty] | 2
| second floor | [5 empty] | 10
| third floor | [5 empty] | 10
| total | nos |  |  |  |  | 22
Providing and fixing brass Bib cock of approved quality - 15mm nominal bore
| second floor | [5 empty] | 5
| third floor | [5 empty] | 5
| total | nos |  |  |  |  | 10
Providing and fixing C.P. brass shower rose with 15 to 20 mm inlet 100mm diameter
| third floor | [5 empty] | 5
| total | nos |  |  |  |  | 5
Providing and fixing C.P brass stop cock (concealed) of standard design of approved make conforming to IS 8931. conforming to IS standards 15 mm nominal bore
| third floor | [5 empty] | 5
| total | nos |  |  |  |  | 5
Supplying & Erecting pump set of suitable capacity coupled to a electric motor to run on 3 phase electric supply capable of discharging of 7 LPS against a total head of 20m including starter with bronze impeller, stainless steel shaft etc incl. cost of panel Board, voltmeter, ameter etc.
| third floor | nos |  |  |  |  | 1
| total | nos |  |  |  |  | 1
Providing and placing on terrace (at all floor levels) poly ethlyne water storage tank ISI: 12701 marked with cover and suitable locking arrangement and making necessary holes for inlet, outlet and over flow pipes but with out fittings and the base support for tank
| third floor | [5 empty] | 2000
| total | litres |  |  |  |  | 2000
DRAINAGE WORKS
Constructing brick masonry manhole in cement mortar 1:4 (1 cement: 4 coarse sand) RCC top slab with 1:2:4 mix (1 cement:2 coarse sand:4 graded stone aggregate 20mm nominal size), foundation concrete 1:4:8 mix (1 cement:4 coarse sand:8 graded stone aggregate 40mm nominal size) inside plastering 12mm thick with cement mortar 1:3 (1 cement: 3 fine sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 20mm nominal size) finished with a floating coat of neat cement complete as per standard design: Inside size 90x80cm and 45cm deep including CI cover with frame (light duty) 455x610mm internal dimensions total weight of cover and frame to be not less than 38kg(weight of cover 23kg and weight of frame 15kg) with Class 75 F P S bricks.
| yard work | nos |  |  |  |  | 10
total
Making soak pit 2.5 m diameter 3.0 meter deep with 45 x 45 cm dry brick honey comb shaft with bricks of class designation 75 and SW drain pipe 100 mm diameter, 1.8 m long complete as per standard design :-
| yard work | nos |  |  |  |  | 1
total
Constructing soak pit 1.20x1.20x1.20m filled with brickbats including S.W. drain pipe 100 mm diameter and 1.20 m long complete as per standard design.
| yard work | nos |  |  |  |  | 4
total
Providing and jointing PVC 150mm PVC pipes of (pressure 6 kg/cm2) for drainage line including testing of joints etc complete. For sewage connection & Rain water collection & disposal 150mm diameter (Nominal)
| yard work | rm |  |  |  |  | 150
total
Construction of rain water collection chamber of size 45x45cm inside ,60cm depth,with 10cm thick floor slab of RCC 1:2:4, 23 cm thick Brick masonry side wall in 1:5 CM, Top cover of RCC 1:2:4 of 7cm thick, Plastering inside and outside with CM 1:4
| yard work | nos |  |  |  |  | 10
total
Supplying and fixing C.I. cover without frame for manholes 455x610 mm rectangular C.I. cover (light duty) the weight of the cover to be not less than 23 kg.
| yard work | nos |  |  |  |  | 21
total
15 | Providing and fixing gun metal gate valve with CI wheel of approved quality(screwed end) –
25mm PVC pipe (10kg/sqcm)
| yard work | [5 empty] | 4
| third floor | [5 empty] | 4
| total | rm |  |  |  |  | 8
32mm PVC pipe (10kg/sqcm)
| yard work | [5 empty] | 5
| third floor | [5 empty] | 2
| total | rm |  |  |  |  | 7
50mm PVC pipe (10kg/sqcm)
| yard work | [5 empty] | 4
| third floor | [5 empty] | 2
| total | rm |  |  |  |  | 6
16 | Providing and fixingpvc 10 kg bend of specified diamenter including cutting and finishing etc.complete
| yard work | nos |  |  |  |  | 45
| total | [5 empty] | 45
17 | Providing and fixingpvc 10 kg 90 degerr bend of specified diamenter including cutting and finishing etc.complete
yard work
| 63mm PVC pipe (10kg/sqcm) | [5 empty] | 22
| total | rm |  |  |  |  | 22
| 110mm PVC pipe (10kg/sqcm) | [5 empty] | 40
| total | [5 empty] | 40
18 | Providing and fixingpvc 10 kg PVC TEE of specified diamenter including cutting and finishing etc.complete
yard work
| 63mm PVC pipe (10kg/sqcm) | nos |  |  |  |  | 35
| total | [5 empty] | 35
Providing M.S. foot rests including fixing in manholes with 20x20x10 cm cement concrete blocks 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) as per standard design: With 20x20 mm square bar
yard work
| total | [5 empty] | 25

## YARD WORK (hidden)
Name of work : RENNOVATION OF GENERAL HOSPITAL AT KALPETTA IN WAYANAD DISTRICT
DETAILED ESTIMATE
S.N | Description | Unit | NO | Length | Width | Depth | Quantity
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
YARD WORK
1 | Clearing jungle including uprooting of rank vegetation, grass, brus wood, trees and saplings of girth upto 30 cm measured at a height of 1 m above ground level and removal of rubbish upto a distance of 50 m outside the periphery of the area cleared.
| yard |  | 1 | 45 | 2.8 |  | 126
|  |  | 1 | 55 | 3.25 |  | 178.75
|  |  | 1 | 68 | 2.75 |  | 187
| Total | [5 empty] | 491.75
| Say | [5 empty] | 500
Surface dressing of the ground including removing vegetation and in-equalities not exceeding 15 cm deep and disposal of rubbish, lead upto 50 m and lift upto 1.5 m.For all kinds of soil
| yard |  | 1 | 45 | 2.8 |  | 126
|  |  | 1 | 55 | 3.25 |  | 178.75
|  |  | 1 | 68 | 2.75 |  | 187
| Total | [5 empty] | 491.75
| Say | [5 empty] | 500
3 | Earth work in excavation by mechanical means (Hydraulic Excavator )/ manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan) including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All kinds of soil.
Toilet
|  |  | 3 | 5.5 | 0.7 | 0.7 | 8.085
|  |  | 3 | 3 | 0.7 | 0.7 | 4.41
|  |  | 2 | 1.5 | 0.7 | 0.7 | 1.47
Ele room
| column |  | 6 | 1.5 | 1.5 | 1.5 | 20.25
| Plinth beam |  | 2 | 7.6 | 0.3 | 0.7 | 3.192
|  |  | 3 | 3.5 | 0.3 | 0.7 | 2.205
Poarch foundationn
|  |  | 14 | 1.2 | 1.2 | 0.8 | 16.128
Compound wall
|  |  | 2 | 10 | 0.7 | 0.7 | 9.8
| gate |  | 2 | 2.3 | 2.3 | 1 | 10.58
| Total | [5 empty] | 76.12
| Say | [5 empty] | 80
Earth work in excavation by mechanical means (Hydraulic excavator)/ manual means over areas (exceeding 30cm in depth. 1.5m in width as well as 10 sqm on plan) including disposal of excavated earth, with all lead and lift as per the direction of engineer -in -charge
| rain water sump |  | 1 | 9 | 7 | 3 | 189
| total | [5 empty] | 189
| say | [5 empty] | 190
4 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m.
| Ele room |  | 1 | 7 | 3.5 | 0.1 | 2.45
|  |  | 6 | 1.5 | 1.5 | 1 | 13.5
| toilet |  | 1 | 5.2 | 3 | 0.1 | 1.56
| Poarch foundationn |  | 14 | 1.2 | 1.2 | 0.7 | 14.112
| Total | [5 empty] | 31.622
| Say | [5 empty] | 35
5 | Supplying and filling in plinth with quarry dust under floors including watering, ramming, consolidating and dressing complete.
| Poarch |  | 1 | 6.5 | 5.8 | 0.15 | 5.655
|  |  | 1 | 5.2 | 3.5 | 0.15 | 2.73
| Ele room |  | 1 | 7 | 3.5 | 0.1 | 2.45
| Toilet |  | 1 | 5.2 | 3 | 0.1 | 1.56
| Total | [5 empty] | 12.395
| Say | [5 empty] | 12.5
6 | Cement concrete(Cast-in-situ) Providing and laying in position cement concrete of specified grade excluding the cost of centring and shuttering- All work upto plinth level 1:5:10 (1 cement : 5 coarse sand : 10 graded stone aggregate 40mm nominal size)
Ele room
| coulmn |  | 6 | 1.4 | 1.4 | 0.1 | 1.176
| plinth beam |  | 2 | 7.6 | 0.3 | 0.1 | 0.456
|  |  | 3 | 3.5 | 0.3 | 0.1 | 0.315
| floor |  | 1 | 7.4 | 3.5 | 0.1 | 2.59
| sump foundation |  | 1 | 9 | 7 | 0.1 | 6.3
toilet
| foundation |  | 3 | 5.5 | 0.7 | 0.1 | 1.155
|  |  | 3 | 3 | 0.7 | 0.1 | 0.63
|  |  | 2 | 1.5 | 0.7 | 0.1 | 0.21
| floor |  | 1 | 5.2 | 3 | 0.1 | 1.56
| Poarch foundationn |  | 14 | 1.2 | 1.2 | 0.1 | 2.016
| gate |  | 2 | 2.2 | 2.2 | 0.1 | 0.968
| compound wall |  | 2 | 10 | 0.7 | 0.1 | 1.4
| Total | [5 empty] | 18.776
| Say | [5 empty] | 19
Providing and laying cement concrete in retaining walls, return walls, walls (any thickness) including attached pilasters, columns, piers, abutments, pillars, posts, struts, buttresses, string or lacing courses, parapets, coping, bed blocks, anchor blocks, plain window sills, fillets, sunken floor,etc., up to floor five level, excluding the cost of centering, shuttering and finishing 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size)
Dummy columns -- existing
|  |  | 10 | 0.45 | 0.6 | 1.2 | 3.24
| Say | [5 empty] | 4
Providing and laying cement Concrte in retaining walls, return walls (any thickness) including attached pilasters, columns, piers, abutmets, pillars, posts, struts, buttresses,string or lacing courses, parapets, coping bed blocks, anchor blocks, plain window sills, fillets etc upto floor five level, excluding the cost of centring, shuttering and finishing 1:2:4 (1 cement: 2coarse sand : 4 graded stone aggregate 20 mm nominal size)
| Cable trench |  | 2 | 40 | 0.15 | 0.5 | 6
|  |  | 2 | 10 | 0.15 | 0.5 | 1.5
| Total | [5 empty] | 7.5
| Say | [5 empty] | 8
Reinforced cement concrete work in beams, suspended floors, roofs having slope upto 15degree, landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases upto floor V level including cost of centering, shuttering, finishing and excluding the cost of reinforcement in 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size)
| pump room slab |  | 1 | 4 | 4 | 0.12 | 1.92
| total | [5 empty] | 1.92
| say | [5 empty] | 2
Providing and laying in position specified grade of reinforced cement concrete including the cost of centering,shuttering,finishing and excluding cost of reinforcment -All work upto plinth level. 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size
Ele room
| Column footing |  | 6 | 1.2 | 1.2 | 0.45 | 3.888
| pedestals |  | 6 | 0.3 | 0.3 | 0.6 | 0.324
| plinth beam |  | 2 | 7.5 | 0.2 | 0.6 | 1.8
|  |  | 3 | 3.5 | 0.2 | 0.6 | 1.26
| sump bottomfloor |  | 1 | 8.4 | 5.9 | 0.2 | 9.912
| sump top floor |  | 1 | 8.4 | 5.9 | 0.2 | 9.912
| curb below pump room |  | 4 | 3 | 0.2 | 0.2 | 0.48
| Poarch foundationn |  | 14 | 1.1 | 1.1 | 0.2 | 3.388
| gate |  | 2 | 2 | 2 | 0.45 | 3.6
| pedestal |  | 2 | 0.6 | 0.6 | 0.5 | 0.36
| tie |  | 1 | 5.2 | 0.45 | 0.6 | 1.404
| CHAIN FENCEING-kerb |  | 1 | 35 | 0.25 | 0.25 | 2.1875
| Total | [5 empty] | 38.5155
| Say | [5 empty] | 39
Reinforced cement concrete work in walls (any thickness) including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc upto floor V level including cost of centering, shuttering, finishing and excluding cost of reinforcement in 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20 mm nominal size)
Ele room
| columns |  | 6 | 0.2 | 0.4 | 3.4 | 1.632
| Gate post |  | 2 | 0.6 | 0.6 | 5 | 3.6
| CHAIN FENCEING-post |  | 25 | 0.2 | 0.2 | 1.8 | 1.8
| sump wall |  | 2 | 8.4 | 2.5 | 0.2 | 8.4
| sump wall |  | 4 | 5.5 | 2.5 | 0.2 | 11
| Total | [5 empty] | 26.432
| Say | [5 empty] | 27
Providing and laying in position specified grade of reinforced cement concrete excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level RCC 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size)
| ele room |  | 1 | 7.4 | 3.9 | 0.12 | 3.4632
| Total | [5 empty] | 3.4632
| Say | [5 empty] | 4
Reinforced cement concrete work in beams, suspended floors, roofs having slope upto 15degree, landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases upto floor V level including cost of centering, shuttering, finishing and excluding the cost of reinforcement in 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size)
| pump room slab |  | 1 | 4 | 4 | 0.12 | 1.92
lintels
| Toilet |  | 3*2 | 5.2 | 0.2 | 0.15 | 0.936
|  |  | 3*2 | 3 | 0.2 | 0.15 | 0.54
|  |  | 2*2 | 1.5 | 0.2 | 0.15 | 0.18
| pump room above sump |  | 4 | 3 | 0.2 | 0.15 | 0.36
| Ele room |  | 2*2 | 7.5 | 0.2 | 0.15 | 0.9
|  |  | 3*2 | 3.5 | 0.2 | 0.15 | 0.63
| Compound wall coping |  | 2 | 17 | 0.6 | 0.1 | 6.12
|  |  | 1 | 5.5 | 0.3 | 0.5 | 4.95
| Total | [5 empty] | 16.536
| Say | [5 empty] | 17
Reinforcement for RCC works including straightening, cutting, bending, placing in position and binding all complete. Thermo - Mechanically treated bars (Using Vizac, Tata or SAIL)
| Total | [5 empty] | 89
| @ 140 kg / m3 | [5 empty] | 12460
| Say | [5 empty] | 11650
Random rubble masonry with hard stone in foundation and plinth including levelling up with cement concrete 1:6:12 (1 cement : 6 coarse sand : 12 graded stone aggregate 20mm nominal size) at plinth level with: Cement mortar 1:6 (1 cement : 6 coarse sand)
toillet
| foundation |  | 3 | 5.2 | 0.6 | 0.6 | 5.616
|  |  | 3 | 3 | 0.6 | 0.6 | 3.24
|  |  | 2 | 1.5 | 0.6 | 0.6 | 1.08
| Basement |  | 3 | 5.2 | 0.45 | 0.6 | 4.212
|  |  | 3 | 3 | 0.45 | 0.6 | 2.43
|  |  | 2 | 1.5 | 0.45 | 0.6 | 0.81
| Compound wall | [5 empty] | 0
| foundation |  | 2 | 10 | 0.6 | 0.6 | 7.2
| Basement |  | 2 | 10 | 0.45 | 0.45 | 4.05
| Total | [5 empty] | 28.638
| Say | [5 empty] | 30
Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in :Cement mortar 1:4 (1 cement : 4 coarse sand
| for combound wall |  | 2 | 10 | 0.2 | 2.5 | 10
| Toilet |  | 3 | 5.2 | 0.2 | 3 | 9.36
|  |  | 3 | 3 | 0.2 | 3 | 5.4
|  |  | 2 | 1.5 | 0.2 | 3 | 1.8
| pump room above sump |  | 2 | 3 | 0.2 | 2.8 | 3.36
| pump room above sump |  | 2 | 3 | 0.2 | 2.8 | 3.36
| Ele room |  | 2 | 7.5 | 0.2 | 3.4 | 10.2
|  |  | 3 | 3.5 | 0.2 | 3.4 | 7.14
| Total | [5 empty] | 50.62
Deductions
| Ele room- shutter |  | 1 | 3 | 0.2 | 2.4 | 1.44
| window |  | 2 | 1.5 | 0.2 | 1.5 | 0.9
| toilet door |  | 4 | 0.8 | 0.2 | 2.1 | 1.344
| Total deductions | [5 empty] | 3.684
| After deductions | [5 empty] | 46.936
| Say | [5 empty] | 47
Providing and fixing G.I. chain link fabric fencing of required width in mesh size 25x25 mm made of G.I. wire of dia. 3mm including strengthening with 2mm dia. wire or nuts, bolts and washers as required complete as per the direction of Engineer-in-charge
yard work
| For DP unit | 2 | 8 | 1.8 |  |  | 28.8
|  | 2 | 7 | 1.8 |  |  | 25.2
| total | [5 empty] | 54
| SAY | [5 empty] | 60
Steel work welded in built up section / framed work including cutting ,hoisting, fixing I position and applying a priming coat of approved steel primer using structural steel etc. as required.In grating ,frames,guard bar, ladder, railings, brackets, gates and similar works.
| Gate |  | 1 | 4 | 2.5 |  | 10
| @ 50 kg / m3 | [5 empty] | 500
Steel work in built up tubular ( round, square or rectangular hollow tubes etc.) trusses etc. including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer, including welding and bolted with special shaped washers etc. complete.Hot finished welded type tubes
| casuality enry |  | 1 | 6.5 | 4.5 |  | 29.25 | 6.5 | 5.7 | 37.05
|  |  | 1 | 6 | 4 |  | 24 |  |  | 0
| near pharmacy counter area |  | 1 | 6 | 3.5 |  | 21 | 5.2 | 3.4 | 17.68
| near entrace area for counter |  | 1 | 5 | 2.5 |  | 12.5 | 5 | 2.2 | 11
| near back side stair case |  | 1 | 6 | 4 |  | 24 | 6 | 5.5 | 33
|  |  | 1 | 5.5 | 3.8 |  | 20.9 |  |  | 98.73 | 2.5 | 3.25 | 16.8125 | 4.1003
| Ele room |  | 1 | 9.5 | 5.5 |  | 52.25
| Toilet |  | 1 | 7.2 | 5 |  | 36
| total | [5 empty] | 219.9 |  |  |  | 2.5 | 3 | 15.25 | 3.9051
| @ 20 kg/m2 | [5 empty] | 4398
| say | [5 empty] | 4500 |  |  |  | 2.5 | 2.75 | 13.8125 | 3.7165
Providing corrugated G.S. sheet roofing including vertical/curved surface fixed with polymer coated J or L hooks, bolts and nuts 8 mm diameter with bitumen and G.I. limpet washers or with G.I. limpet washers filled with white lead and including a coat of approved steel primer and two coats of approved paint on overlapping of sheets complete (up to any pitch in horizontal/ vertical or curved surfaces) excluding the cost of purlins, rafters and trusses and including cutting to size and shape wherever required.0.63 mm thick with zinc coating not less than 275gm/ m²
| casuality enry |  | 1 | 6.5 | 4.5 |  | 29.25
|  |  | 1 | 6 | 4 |  | 24
| near pharmacy counter area |  | 1 | 6 | 3.5 |  | 21
| near entrace area for counter |  | 1 | 5 | 2.5 |  | 12.5
| near back side stair case |  | 1 | 6 | 4 |  | 24
|  |  | 1 | 5.5 | 3.8 |  | 20.9
| Ele room |  | 1 | 9.5 | 5.5 |  | 52.25
| Toilet |  | 1 | 7.2 | 5 |  | 36
| total | [5 empty] | 219.9
| Say | [5 empty] | 220
Providing and fixing M.S grills of required pattern in frames of windows etc with M.S.flats,square or round bars etc all complete:- Fixed to openings/wooden frames with rawl plugs screws etc
| Ele room window |  | 2 | 1.5 | 1.5 |  | 4.5
| Toilet ventiletor |  | 4 | 0.5 | 0.6 |  | 1.2
| Total | [5 empty] | 5.7
| @ 15 kg / sqm | [5 empty] | 85.5
| Say | [5 empty] | 90
12mm cement plaster on rough side of single or half brick wall finished with a floating coat of neat cement of mix 1:4 ( 1 cement : 4 fine sand)
| Toilet |  | 4*2 | 2.7 | 3 |  | 64.8
|  |  | 2 | 5.2 | 3 |  | 31.2
|  |  | 2 | 1.2 | 3 |  | 7.2
| sump in side |  | 2 | 8 | 2.5 |  | 40
| sump in side |  | 5 | 5.5 | 2.5 |  | 68.75
| sump top and bot area |  | 2 | 8 | 5.5 |  | 88
| in side pump room |  | 4 | 3 | 2.8 |  | 33.6
| Ele room |  | 2 | 7.4 | 3.4 |  | 50.32
|  |  | 2 | 3.5 | 3.4 |  | 23.8
| Total | [5 empty] | 407.67
Deductions
| Ele room- shutter |  | 1 | 3 |  | 2.4 | 7.2
| window |  | 2 | 1.5 |  | 1.5 | 4.5
| toilet door |  | 4 | 0.8 |  | 2.1 | 6.72
| Total deductions | [5 empty] | 18.42
| After deduction | [5 empty] | 389.25
| Say | [5 empty] | 390
15mm cement plaster on rough side of single or half brick wall finished with a floating coat of neat cement of mix 1:5 ( 1 cement :5 fine sand)
| Ele room |  | 2 | 7.5 | 3.5 |  | 52.5
|  |  | 2 | 3.5 | 3.5 |  | 24.5
| Toilet |  | 2 | 5.2 | 3 |  | 31.2
|  |  | 2 | 3 | 3 |  | 18
| pump room out side |  | 4 | 3.4 | 3 |  | 40.8
| Compound wall |  | 2 | 10 | 2.5 |  | 50
| Coping |  | 2 | 17 | 1.1 |  | 37.4
| gate - column |  | 2 | 2.4 | 5 |  | 24
|  |  | 1 | 5.5 | 1.6 |  | 8.8
|  |  | 2 | 5.5 | 1.5 |  | 16.5
| dummy column |  | 10 | 2.1 | 1.1 |  | 23.1
| cable trench |  | 4 | 15 | 0.5 |  | 30
|  |  | 4 | 10 | 0.5 |  | 20
| Total | [5 empty] | 376.8
| Say | [5 empty] | 380
Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade in two or more coats on new work, including finishing walls with Deluxe Multi surface paint system for interiors and exteriors using Primer as per manufacturers specifications: Two or more coats applied on walls @ 1.25 ltr/10 sqm over and including one coat of Special primer applied @ 0.75 ltr / 10 sqm
| quty from plastering | [5 empty] | 390
| say | [5 empty] | 390
Finishing walls with Acrylic Smooth exterior paint of required shade: —New work (Two or more coat applied @ 1.67 ltr/10 sqm over and including basecoat of water proofing cement paint applied @ 2.20 kg/ 10 sqm)
| quty from plastering | [5 empty] | 380
| say | [5 empty] | 380
Steel Work painting- Painting with synthetic enamel paint of approved brand and manufacture to give an even shade. Two or more coats on new work
| quty from steel work | [5 empty] | 5090
| say | [5 empty] | 5100
Providing and laying anti skid ceramic floor tiles of minimum 400x400 mm size for toilets (7.5mm thickness or nearest size) M/s. JOHNSON, KAJARIA, NITCO, SOMANY or equivalent of 1st quality conforming to IS: 15622 of approved make in all colours, shades, except white, ivory, grey, fume red brown laid on 20mm thick bed of cement mortar 1:4 (1 cement : 4 coarse sand) including pointing the joints with white cement and matching pigments etc complete.
Toilet
|  |  | 4 | 1.2 | 1.5 |  | 7.2
|  |  | 2 | 1.2 | 2.7 |  | 6.48
| Toilet | [5 empty] | 13.68
| Say | [5 empty] | 15
Providing and fixing Ist quality ceramic glazed wall tiles conforming to IS: 15622 of minimum 350x250 mm size and thickness 5MM of JOHNSON, NITCO, ORIENT, , KAJARIA ,or approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados,over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand)and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete
| Toilet |  | 4*2 | 1.2 | 2.1 |  | 20.16
|  |  | 4*2 | 1.5 | 2.1 |  | 25.2
|  |  | 2 | 2.5 | 1.5 |  | 7.5
|  |  | 1 | 1.2 | 1.5 |  | 1.8
| total | [5 empty] | 54.66
| say | [5 empty] | 55
Providing and laying 60mm thick factory made cement concrete interlocking paver blocks of M - 30 grade made by block making machine with strong vibratory compaction and of approved size and design/ shape laid in required colour and pattern over and including 50mm thick compacted bed of coarse sand, filling the joints with coarse sand etc all complete as per the direction of Engineer in charge.
| from casuality area |  | 1 | 4.8 | 5.5 |  | 26.4
|  |  | 1 | 6.7 | 4.8 |  | 32.16
|  |  | 1 | 3.15 | 5.5 |  | 17.325
|  |  | 1 | 22 | 7.6 |  | 167.2
|  |  | 1 | 11.5 | 4.35 |  | 50.025
|  |  | 0.5 | 3.6 | 4.4 |  | 7.92
|  |  | 1 | 9 | 5.1 |  | 45.9
|  |  | 1 | 36.3 | 5 |  | 181.5
|  |  | 1 | 2.3 | 1.7 |  | 3.91
|  |  | 1 | 10.5 | 4.5 |  | 47.25
|  |  | 1 | 4.8 | 9.5 |  | 45.6
|  |  | 1 | 3.8 | 11.32 |  | 43.016
| up to back side stair area |  | 1 | 6.8 | 8 |  | 54.4
| total | [5 empty] | 722.606
| say | [5 empty] | 725
Providing and laying at or near ground level factory made kerb stone of M-25 grade cement concrete in position to the required line, level and curvature, jointed with cement mortar 1:3 (1 cement: 3 coarse sand) including making joints with or without grooves (thickness of joints except at sharp curve shall not to more than 5mm), including making drainage opening wherever required complete etc. as per direction of Engineer-in-charge (length of finished kerb edging shall be measured for payment). (Precast C.C. kerb stone shall be approved by Engineer-in-charge
| side of paver block in yard |  | 2 | 45 | 0.3 | 0.5 | 13.5
|  |  | 2 | 55 | 0.3 | 0.5 | 16.5
|  |  | 2 | 68 | 0.3 | 0.5 | 20.4
|  |  | 2 | 28 | 0.3 | 0.5 | 8.4
| Total | [5 empty] | 58.8
| Say |  | cum |  |  |  | 60
Providing and fixing factory made UPVC door frame of Rajashri or equivalent make made of UPVC extruded section having an overall dimension as. Below(tolerance+1mm) with wall thickness 2.0mm+/;0.2mm, corners of the door frame to be jointed with galvanized brackets and stainless steel screws, joint mitred plastic wilded. the hinge side vertical of the frames reinforced by galvanized M.S. tube of size 19x19mm and 1mm +/- 0.1mm wall thickness and 3 nos. stainless steel hinges fixed to the frame complete as per manufacturers specification and direction of Engineer-in-charge:Extruded section Profile size 42x50mm.
Toilet door
|  |  | 4 | 5.1 |  |  | 20.4
| total | [5 empty] | 20.4
| SAY | [5 empty] | 21
Providing and fixing to existing door frames.30mm thick factory made Rajashri or equivalent make Polyvinyl Chloride(PVC) door shutter and rails of a UPVC profile section of size 30mmx60mm and wall thickness 2mm+/-0.2mm with inbuilt decorative moulding edging on one side. The styles and rails with plastic brackets of size 75x220mm mitre and welded at the corners. The-stiles of the shutter reinforced by inserting galvanized M.S. tube of size 25x20mm and 1mm+/-0.1mm wall thickness. The lock rail made up of 'H' section, a UPVC profile section of size 30mmx100mm and 2mm+/-0.2mm wall thickness welded to the shutter style with a UPVC profile section single panel of size not less than 620mm,having overall thickness of 20mm and 1mm+/-0.1mm wall thickness with 20mm panel beading of suitable size, as per manufactures specification and direction of Engineer-in-charge.
| TOILET |  | 4 | 0.9 | 2.1 |  | 7.56
| Total | [5 empty] | 7.56
| SAY | [5 empty] | 8
| Providing and fixing water closet squatting pan (Indian type W.C. pan ) with 100mm sand cast Iron P or S trap, 10 litre low level white P.V.C. flushing cistern, including flush pipe, with manually controlled device (handle lever) conforming to IS : 7231, with all fittings and fixtures complete including cutting and making good the walls and floors wherever required :White Vitreous china Orissa pattern W.C. pan of size 580x440mm with integral type foot rests. |  | 4
Providing and fixing white vitreous china flat back half stall urinal of size 580x380x350mm with white PVC automatic flushing cistern, with fittings, standard size C.P. brass flush pipe, spreaders with unions and clamps (all in C.P. brass) with waste fitting as per IS : 2556, C.I. trap with outlet grating and other couplings in C.P. brass including painting of fittings and cutting and making good the walls and floors wherever required Single half stall urinal with 5 litre P.V.C. automatic flushing cistern
| toilet |  | 2
Providing and fixing wash basin with C.I/ M.S brackets, 15mm C.P. brass pillar taps Kingston/ Gem/ Techno/ Parko, 32mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls and floors wherever require: White Vitreous China Wash basin size 550x400 mm with a pair of 15 mm C.P. brass pillar taps
| Toilet block - |  | 4
| Providing and fixing unplasticised PVC connection pipes with brass unions 30 cm length 15mm nominal bore |  | 10
| Providing and fixing waste pipe for sink, wash basin or urinals including PVC waste fittings complete:Semi Rigid Pipe-32mm diameter |  | 6
| Providing and fixing 600x450mm bevelled edge mirror 5mm thick of superior glass(of approved quality) complete with 6mm thick hard board ground fixed to wooden cleats with C.P.brass screws and washers complete. |  | 4
| Providing and fixing S.S soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements. Weighing not less than 106 gms. |  | 4
Providing and jointing PVC 63mm PVC pipes of (pressure 6 kg/cm2) for drainage line including testing of joints etc complete. (Sullage Down pipe) 63mm diameter (OD)
| for sullage disposal |  |  | 70 |  |  | 70
Providing and fixing wall face PVC pipe complete including cutting,chasing in walls and making good the walls etc complete.
| 25mm PVC pipe (10kg/sqcm) |  | 1 | 25
| 32mm PVC pipe 1(10kg/sqcm) |  | 1 | 100
| 50mm PVC pipe (10kg/sqcm) |  | 1 | 75
Providing and fixing trap of self cleansing design with screwed down or hinged grating with or without vent arm complete, including cost of cutting and making good the walls and floors: 110mm inlet and 110mm outlet pvc
| toilet block |  | 7 |  |  |  | 7
Providing and fixing PTMT (an Engineering thermo plastic ) grating of approved quality colour and make 150 mm nominal size square,100mm diameter of the inner hinged round grating. Rectangular type with circular round lid
|  |  | 7 |  |  |  | 7
| Constructing brick masonry manhole in cement mortar 1:4 (1 cement: 4 coarse sand) RCC top slab with 1:2:4 mix (1 cement:2 coarse sand:4 graded stone aggregate 20mm nominal size), foundation concrete 1:4:8 mix (1 cement:4 coarse sand:8 graded stone aggregate 40mm nominal size) inside plastering 12mm thick with cement mortar 1:3 (1 cement: 3 fine sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement: 2 coarse sand : 4 graded stone aggregate 20mm nominal size) finished with a floating coat of neat cement complete as per standard design: Inside size 90x80cm and 45cm deep including CI cover with frame (light duty) 455x610mm internal dimensions total weight of cover and frame to be not less than 38kg(weight of cover 23kg and weight of frame 15kg) with Class 75 F P S bricks. |  | 10 |  |  |  | 10
| Making soak pit 2.5 m diameter 3.0 meter deep with 45 x 45 cm dry brick honey comb shaft with bricks of class designation 75 and SW drain pipe 100 mm diameter, 1.8 m long complete as per standard design :- |  | 1 |  |  |  | 1
| Constructing soak pit 1.20x1.20x1.20m filled with brickbats including S.W. drain pipe 100 mm diameter and 1.20 m long complete as per standard design. |  | 4 |  |  |  | 4
| Providing and jointing PVC 150mm PVC pipes of (pressure 6 kg/cm2) for drainage line including testing of joints etc complete. For sewage connection & Rain water collection & disposal 150mm diameter (Nominal) |  | 1 | 150 |  |  | 150
Providing and fixing 15cm wide &45 cm overall semi circular plain GS sheet gutter with iron bracket 40x3 size washers including making nessassary connections with rain water pipe complete. 0.63mm thick zink coating not less than 275kg/m2
|  |  | 1 | 60 |  |  | 60
Construction of rain water collection chamber of size 45x45cm inside ,60cm depth,with 10cm thick floor slab of RCC 1:2:4, 23 cm thick Brick masonry side wall in 1:5 CM, Top cover of RCC 1:2:4 of 7cm thick, Plastering inside and outside with CM 1:4
|  |  | 1 | 10 |  |  | 10
Supplying and fixing C.I. cover without frame for manholes 455x610 mm rectangular C.I. cover (light duty) the weight of the cover to be not less than 23 kg.
|  |  | 21 |  |  |  | 21
Supplying and fixing rolling shutters of approved make, made of required size M.S. laths, interlocked together through their entire length and jointed together at the end by end locks, mounted on specially designed pipe shaft with brackets, side guides and arrangements for inside and outside locking with push and pull operation complete, including the cost of providing and fixing necessary 27.5 cm long wire springs manufactured from high tensile steel wire of adequate strength conforming to IS: 4454 – part 1 and M.S. top cover of required thickness for rolling shutters:80x1.25 mm M.S. laths with 1.25 mm thick top cover
|  |  | 1 | 3 | 2.5 |  | 7.5
| say | [5 empty] | 8
Providing and fixing ball bearing for rolling shutters.
|  |  | 1 |  |  |  | 1
Extra for providing grilled rolling shutters manufactured out of 8 mm dia. M.S. bar instead of laths as per design approved by Engineer-in-charge.(area of grill to be measured).
|  |  | 1 | 3 |  | 0.6 | 1.8
say
15 | Providing and fixing gun metal gate valve with CI wheel of approved quality(screwed end) –
| 25mm nominal bore |  | 5 |  |  |  | 5
| 32mm nominal bore |  | 5 |  |  |  | 5
| 40mm nominal bore |  | 4 |  |  |  | 4
16 | Providing and fixingpvc 10 kg bend of specified diamenter including cutting and finishing etc.complete
| 63mm PVC pipe (10kg/sqcm) |  | 45 |  |  |  | 45
17 | Providing and fixingpvc 10 kg 90 degerr bend of specified diamenter including cutting and finishing etc.complete
| 63mm PVC pipe (10kg/sqcm) |  | 22 |  |  |  | 22
| 110mm PVC pipe (10kg/sqcm) |  | 40 |  |  |  | 40
18 | Providing and fixingpvc 10 kg PVC TEE of specified diamenter including cutting and finishing etc.complete
| 63mm PVC pipe (10kg/sqcm) |  | 35 |  |  |  | 35
Providing M.S. foot rests including fixing in manholes with 20x20x10 cm cement concrete blocks 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) as per standard design: With 20x20 mm square bar
| yard work | 25 |  |  |  |  | 25
| total | [5 empty] | 25

## GROUND FLOOR (hidden)
Name of work : RENNOVATION OF GENERAL HOSPITAL AT KALPETTA IN WAYANAD DISTRICT
GENERAL HOSPITAL - KALPETTA
DETAILED ESTIMATE
S.N | Description | Unit | NO | Length | Width | Depth | Quantity
GROUND FLOOR
Demolishing R.C.C. work manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per direction of Engineer - in- charge.
|  |  | 1 | 6.04 | 0.6 | 0.08 | 0.28992
Extra for cutting reinforcement bars manually/ by mechanical means in R.C.C. or R.B. work (Payment shall be made on the cross sectional area of R.C.C. or R.B. work) as per direction of Engineer - in -charge
|  |  | 1 | 6.04 | 0.6 |  | 3.624
Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge
| casuality |  | 2 | 1.5 | 0.2 | 2.1 | 1.26
| passage |  | 1 | 2.4 | 0.2 | 2.1 | 1.008
| pharmacy store |  | 2 | 1.5 | 0.2 | 2.1 | 1.26
| lab |  | 1 | 1.2 | 0.2 | 2.1 | 0.504
4.032
Dismantling tile work in floors and roofs laid in cement mortar including stacking material within 50 metres lead.For thickness of tiles 10 mm to 25 mm
| casuality |  | 2 | 2.9 | 0.2 |  | 5.8
|  |  | 1 | 1 | 0.2 |  | 1
| passage |  | 1 | 1.5 | 0.2 |  | 1.5
| blood bank toilet |  | 1 | 2.3 | 2.8 |  | 2.3
| pharmacy |  | 1 | 1 | 0.2 |  | 1
| total | [5 empty] | 11.6
Dismantling aluminium/ Gypsum partitions, doors, windows, fixed glazing and false ceiling including disposal of unserviceable surplus material and stacking of serviceable material with in 50 meters lead as directed by Engineer-in-charge
| casuality |  | 1 | 1 | 2.1 |  | 2.1
| lab |  | 1 | 1 | 2.1 |  | 2.1
| passage |  | 1 | 1 | 2.1 |  | 2.1
6.3
Dismantling of flushing cistern of all types (C.I./PVC/Vitrious China) including stacking of useful materials near the site and disposal of unserviceable materials within 50 metres lead.
Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in :Cement mortar 1:4 (1 cement : 4 coarse sand
|  |  | 2 | 2.9 | 0.2 | 3 | 3.48
|  |  | 2 | 1 | 0.2 | 2.1 | 0.84
4.32
| deduction |  | 2 | 1.5 | 0.2 | 2.1 | 1.26
3.06
Half brick masonry with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level.Cement mortar 1:4 (1 cement :4 coarse sand)
| RSBY COUNTER |  | 1 | 4.16 | 0.8 |  | 3.328
| pharmacy |  | 1 | 4.24 | 0.8 |  | 3.392
| lab |  | 1 | 4.16 | 0.8 |  | 3.328
| reception |  | 1 | 11.5 | 0.6 |  | 6.9
|  |  | 1 | 2.5 | 0.9 |  | 2.25
19.198
Extra for providing and placing in position 2 Nos. 6mm dia. M.S. bars at every third course of half brick masonry
| RSBY COUNTER |  | 1 | 4.16 | 0.8 |  | 3.328
| pharmacy |  | 1 | 4.24 | 0.8 |  | 3.392
| lab |  | 1 | 4.16 | 0.8 |  | 3.328
| reception |  | 1 | 11.5 | 0.6 |  | 6.9
|  |  | 1 | 2.5 | 0.9 |  | 2.25
19.198
Reinforced cement concrete work in beams, suspended floors, roofs having slope upto 15degree, landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases upto floor V level including cost of centering, shuttering, finishing and excluding the cost of reinforcement in 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size)
| RSBY COUNTER |  | 1 | 2 | 0.8 | 0.08 | 0.128
| pharmacy |  | 1 | 3 | 0.8 | 0.08 | 0.192
| lab |  | 1 | 2 | 0.8 | 0.08 | 0.128
| reception |  | 1 | 7.8 | 0.8 | 0.08 | 0.4992
| lintel |  | 2 | 2 | 0.2 | 0.15 | 0.12
|  |  | 5 | 2 | 0.2 | 0.15 | 0.3
|  |  | 1 | 1.4 | 0.2 | 0.15 | 0.042
| lift duct |  | 2 | 1.5 | 1.5 | 0.1 | 0.45
1.8592
Reinforcement for RCC works including straightening, cutting, bending, placing in position and binding all complete. Thermo - Mechanically treated bars (Using Vizac, Tata or SAIL)
185.92
Providing and fixing factory made UPVC door frame of Rajashri or equivalent make made of UPVC extruded section having an overall dimension as. Below(tolerance+1mm) with wall thickness 2.0mm+/;0.2mm, corners of the door frame to be jointed with galvanized brackets and stainless steel screws, joint mitred plastic wilded. the hinge side vertical of the frames reinforced by galvanized M.S. tube of size 19x19mm and 1mm +/- 0.1mm wall thickness and 3 nos. stainless steel hinges fixed to the frame complete as per manufacturers specification and direction of Engineer-in-charge:Extruded section Profile size 42x50mm.
| blood bank |  | 1 | 5.1 |  |  | 5.1
|  |  | 1 | 5.1 |  |  | 5.1
| duct |  | 2 | 5.2 |  |  | 10.4
| total | [5 empty] | 20.6
Providing and fixing to existing door frames.30mm thick factory made Rajashri or equivalent make Polyvinyl Chloride(PVC) door shutter and rails of a UPVC profile section of size 30mmx60mm and wall thickness 2mm+/-0.2mm with inbuilt decorative moulding edging on one side. The styles and rails with plastic brackets of size 75x220mm mitre and welded at the corners. The-stiles of the shutter reinforced by inserting galvanized M.S. tube of size 25x20mm and 1mm+/-0.1mm wall thickness. The lock rail made up of 'H' section, a UPVC profile section of size 30mmx100mm and 2mm+/-0.2mm wall thickness welded to the shutter style with a UPVC profile section single panel of size not less than 620mm,having overall thickness of 20mm and 1mm+/-0.1mm wall thickness with 20mm panel beading of suitable size, as per manufactures specification and direction of Engineer-in-charge.
| blood bank |  | 1 | 0.9 | 2.1 |  | 1.89
| casuality |  | 1 | 0.9 | 2.1 |  | 1.89
| duct |  | 2 | 1 | 2.1 |  | 4.2
| Total | [5 empty] | 7.98
Providing and laying anti skid ceramic floor tiles of minimum 400x400 mm size for toilets (7.5mm thickness or nearest size) M/s. JOHNSON, KAJARIA, NITCO, SOMANY or equivalent of 1st quality conforming to IS: 15622 of approved make in all colours, shades, except white, ivory, grey, fume red brown laid on 20mm thick bed of cement mortar 1:4 (1 cement : 4 coarse sand) including pointing the joints with white cement and matching pigments etc complete.
|  |  | 1 | 2.3 | 2.5 |  | 5.75
Providing and fixing Ist quality ceramic glazed wall tiles conforming to IS: 15622 of minimum 350x250 mm size and thickness 5MM of JOHNSON, NITCO, ORIENT, , KAJARIA ,or approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados,over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand)and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete
|  |  | 2 | 2.3 | 1 |  | 4.6
|  |  | 2 | 2.5 | 1 |  | 5
|  |  | 2 | 3 | 1.4 |  | 8.4
12mm cement plaster on rough side of single or half brick wall finished with a floating coat of neat cement of mix 1:4 ( 1 cement : 4 fine sand)
|  |  | 6 | 2.9 | 2.05 |  | 35.67
|  |  | 8 | 0.2 | 2.1 |  | 3.36
|  |  | 6 | 1.5 | 0.2 |  | 1.8
|  |  | 2 | 1 | 2.1 |  | 4.2
|  |  | 2 | 1 | 0.7 |  | 1.4
|  |  | 2 | 1.5 | 1.5 |  | 4.5
|  |  | 2 | 5.8 | 0.8 |  | 9.28
|  |  | 1 | 2 | 0.8 |  | 1.6
|  |  | 1 | 4.6 | 0.8 |  | 3.68
|  |  | 2 | 5.8 | 0.8 |  | 9.28
|  |  | 1 | 2 | 0.8 |  | 1.6
76.37
6mm cement plaster to ceiling of mix 1 : 3 (1 cement : 3 fine sand )
15mm cement plaster on rough side of single or half brick wall finished with a floating coat of neat cement of mix 1:5 ( 1 cement :5 fine sand)
Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade in two or more coats on new work, including finishing walls with Deluxe Multi surface paint system for interiors and exteriors using Primer as per manufacturers specifications: Two or more coats applied on walls @ 1.25 ltr/10 sqm over and including one coat of Special primer applied @ 0.75 ltr / 10 sqm
|  |  | 6 | 2.9 | 2.05 |  | 35.67
|  |  | 8 | 0.2 | 2.1 |  | 3.36
|  |  | 6 | 1.5 | 0.2 |  | 1.8
|  |  | 2 | 1 | 2.1 |  | 4.2
|  |  | 2 | 1 | 0.7 |  | 1.4
|  |  | 2 | 1.5 | 1.5 |  | 4.5
|  |  | 2 | 5.8 | 0.8 |  | 9.28
|  |  | 1 | 2 | 0.8 |  | 1.6
|  |  | 1 | 4.6 | 0.8 |  | 3.68
|  |  | 2 | 5.8 | 0.8 |  | 9.28
|  |  | 1 | 2 | 0.8 |  | 1.6
76.37
Finishing walls with Acrylic Smooth exterior paint of required shade: —New work (Two or more coat applied @ 1.67 ltr/10 sqm over and including basecoat of water proofing cement paint applied @ 2.20 kg/ 10 sqm)
Steel Work painting- Painting with synthetic enamel paint of approved brand and manufacture to give an even shade. Two or more coats on new work
Providing and fixing 18mm thick gang saw cut mirror polished (premoulded and prepolished) machine cut for kitchen platforms, vanity counters, window sills, facias and similar locations of required size of approved shade, colour and texture laidover 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing moulding and polishing to edge to give high gloss finish etc. complete at all levels. Granite of any colour & Shade
| lift entry wall clading |  | 1 | 4 | 2.5 |  | 10
| lab |  | 1 | 2 | 0.6 |  | 1.2
|  |  | 1 | 2.6 | 0.1 |  | 0.26
| pharmacy |  | 1 | 3 | 0.6 |  | 1.8
|  |  | 1 | 3 | 0.1 |  | 0.3
| RSBY |  | 1 | 2.6 | 0.6 |  | 1.56
|  |  | 1 | 2.6 | 0.1 |  | 0.26
| RECEPTION |  | 1 | 15 | 0.6 |  | 9
|  |  | 1 | 15 | 0.1 |  | 1.5
| total | [5 empty] | 25.88
| say | [5 empty] | 26
Providing edge moulding to 18mm thick marble stone counters, Vanities etc. including machine polishing to edge to give high gloss finish etc. complete as per design approved by Engineer-in-Charge.
| lab |  | 1 | 2.6 |  |  | 2.6
0
| pharmacy |  | 1 | 2.6 |  |  | 2.6
0
| RSBY |  | 1 | 2.6 |  |  | 2.6
|  |  | 1 | 2 |  |  | 2
| RECEPTION |  | 2 | 15 |  |  | 30
Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixed with rawl plugs and screws or with fixing clips, or with expansion hold fasteners including necessary filling up of gaps at junctions, at top, bottom and sides with required PVC/ neoprene felt etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing/panelling. C.P. brass/ stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing and panelling to be paid for separately): For fixed portion Anodised aluminium (anodised transparent or dyed required shade according to IS: 1868, Minimum anodic coating of grade AC 15)
DOORS -(
| 150*210 |  | 10 | 5.6 |  |  | 56
| 100*210 |  | 6 | 5.1 |  |  | 30.6
86.6
| @ 1.372kg/m | [5 empty] | 118.8152
Partitions
| outer sections | [6 empty] | 2.65
| rsby |  | 1 | 11.15 |  |  | 11.15 | 9.4
| lab counter |  | 1 | 11.15 |  |  | 11.15 |  | 35.4
| reception |  | 1 | 22 |  |  | 22
| Entrance -OP& Near lift |  | 2 | 11.5 |  |  | 23
| lab |  | 1 | 16.5 |  |  | 16.5
83.8
| @ 1.777kg/m | [5 empty] | 148.9126
intermediate sections
| rsby |  | 1 | 9.15 |  |  | 9.15
| lab counter |  | 1 | 9.15 |  |  | 9.15
| reception |  | 1 | 17 |  |  | 17
| Entrance -OP& Near lift |  | 2 | 10 |  |  | 20
| lab |  | 1 | 25.5 |  |  | 25.5
| Total | [5 empty] | 80.8
| @ 1.439kg/m | [5 empty] | 116.2712
| Total | [5 empty] | 383.999
| say | [5 empty] | 400
For shutters of doors, windows & ventilators including providing and fixing hinges / pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately).Powder coated aluminium (minimum thickness of powder coating 50 micron
DOORS -
150*210
| vertical |  | 10 | 8.05 | 80.5 | @1.1kg/m | 88.55
| lock |  | 10 | 1.25 | 12.5 | @ 0.904kg/m | 11.3
| bottom |  | 10 | 1.25 | 12.5 | @ 1.504kg/m | 18.8
| top |  | 10 | 1.25 | 12.5 | @ 0.904kg/m | 11.3
| clip |  | 10 | 24.5 | 245 | @ 0.124kg/m | 30.38
| c.angle |  | 10 | 1 | 10 | @0 .632kg/m | 6.32
| beading |  | 10 | 5.25 | 52.5 | @ 0.14kg/m | 7.35
| sub total | [5 empty] | 174
100*210
| vertical |  | 6 | 4.5 | 27 | @1.1kg/m | 29.7
| lock |  | 6 | 0.85 | 5.1 | @ 0.904kg/m | 4.6104
| bottom |  | 6 | 0.85 | 5.1 | @ 1.504kg/m | 7.6704
| top |  | 6 | 0.85 | 5.1 | @ 0.904kg/m | 4.6104
| clip |  | 6 | 14 | 84 | @ 0.124kg/m | 10.416
| c.angle |  | 6 | 0.75 | 4.5 | @0 .632kg/m | 2.844
| S.total | [5 empty] | 59.8512
for partioions
clip
outer sections
| rsby |  | 2 | 11.15 |  |  | 22.3
| lab counter |  | 2 | 11.15 |  |  | 22.3
| reception |  | 2 | 22 |  |  | 44
| Entrance -OP& Near lift |  | 4 | 11.5 |  |  | 46
| lab |  | 2 | 16.5 |  |  | 33
intermediate sections
| rsby |  | 2 | 9.15 |  |  | 18.3
| lab counter |  | 2 | 9.15 |  |  | 18.3
| reception |  | 2 | 17 |  |  | 34
| Entrance -OP& Near lift |  | 4 | 10 |  |  | 40
| lab |  | 2 | 25.5 |  |  | 51
[6 empty] | @ 0.124kg/m | 329.2
| S.total | [5 empty] | 40.8208
| c.angle |  | 150 | 0.05 | 7.5 | @0 .632kg/m | 4.74
| Total | [5 empty] | 279.412
| Say | [5 empty] | 300
Providing and fixing 100mm brass locks (best make of approved quality) for aluminium doors including necessary cutting and making good etc. complete.
|  |  | 16 |  |  |  | 16
Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with PVC/neoprene gasket etc. complete as per the architectural drawings and directions of engineer-in-charge. (Cost of aluminium snap beading shall be paid in basic item): With OPAC glass panes of 6.0 mm thickness
| front entrance door |  | 1 | 1.8 | 1.5 |  | 2.7
| total | [5 empty] | 2.7
| say | [5 empty] | 3
Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with PVC/neoprene gasket etc. complete as per the architectural drawings and directions of engineer-in-charge. (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.0 mm thickness
door
| 150*210 |  | 10*2 | 1.1 | 0.75 |  | 16.5
| 100*210 |  | 6 | 1.1 | 1 |  | 6.6
Partitions
| rsby |  | 1 | 1.4 | 2 |  | 2.8
| lab counter |  | 1 | 1.4 | 2 |  | 2.8
| reception |  | 1 | 1.4 | 6.65 |  | 9.31
| Entrance -OP& Near lift |  | 4 | 1.1 | 0.75 |  | 3.3
| lab collection |  | 1 | 1.1 | 5.3 |  | 5.83
| total |  | sqm |  |  |  | 47.14
Providing and fixing 12 mm thick frameless toughened glass door shutter of approved brand and manufacture, including providing and fixing top & bottom pivot & spring type fixing arrangement and making necessary holes etc. for fixing required door fittings, all complete as per direction of Engineer-in-charge (Door handle, lock and stopper etc.to be paid separately).
| GROUND FLOOR | [5 empty] | 4
| total |  | sqm |  |  |  | 4
Providing and fixing12mm thick prelaminated particle board flat pressed three layer or graded wood particle board conforming to IS12823 Grade 1 type II, in panelling fixed in aluminium doors, windows shutters and partition frames with C.P brass/ stainless steel screws etc. complete as per architectural drawings and directions of engineer in charge Pre laminated particle board with decorative lamination on both sides
door
| 150*210 |  | 10*2 | 1 | 0.75 |  | 15
| 100*210 |  | 6 | 1 | 1 |  | 6
Partitions
| rsby |  | 1 | 1.3 | 3 |  | 3.9
| lab counter |  | 1 | 1.3 | 3 |  | 3.9
| reception |  | 1 | 1.3 | 3.15 |  | 4.095
|  |  | 1 | 1.3 | 4.5 |  | 5.85
| Entrance -OP& Near lift |  | 2 | 1.3 | 3 |  | 7.8
|  |  | 4 | 1 | 0.75 |  | 3
| lab collection |  | 1 | 1.3 | 6.3 |  | 8.19
|  |  | 1 | 1 | 5.3 |  | 5.3
| Total | [5 empty] | 63.035
| say | [5 empty] | 70
Providing and fixing double action hydraulic floor spring of approved brand andmanufacture IS : 6315 marked, for doors including cost of cutting floors as required,embedding in floors and cover plates with brass pivot and single piece M.S. sheetouter box with slide plate etc. complete as per the direction of Engineer-in-chargse With stainless steel cover plate
| door 150*210 |  | 10*2 |  |  |  | 20
| say | [5 empty] | 20
Providing and fixing IS : 3564 marked Aluminium die cast body tubular type universal hydraulic door closer with necessary accessories and screws etc. complete
| 100*210 |  | 18
Providing nad fixing aluminium hanging floor door stopper ISImarked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparant or dyed to required colour and shade with necessary screws etc. complete. Single rubber stopper
| 100*210 |  | 18
providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent od dyed to required colour or shade with necessary screws etc. complete: 250 x 10 mm
door
| 150*210 |  | 10*2
| 100*210 |  | 6
Providing and fixing bright finished stay-cum friction Hymax hinges with necessary screws etc. complete-- 250 mm (Heavy type)

## FIRST FLOOR (hidden)
Name of work : RENNOVATION OF GENERAL HOSPITAL AT KALPETTA IN WAYANAD DISTRICT
GENERAL HOSPITAL - KALPETTA
DETAILED ESTIMATE
S.N | Description | Unit | NO | Length | Width | Depth | Quantity
FIRST FLOOR
Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge
| DUCT |  | 2 | 1 | 0.2 | 2.1 | 0.84
| GYNEpassage |  | 1 | 1.5 | 0.2 | 0.3 | 0.09
0.93
Half brick masonry with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level.Cement mortar 1:4 (1 cement :4 coarse sand)
| Nursing counter in front of LB |  | 1 | 4.5 | 0.8 |  | 3.6
| Nursing counter Gy-1 & 3rd |  | 2 | 4 | 0.8 |  | 6.4
| Lb Counter |  | 1 | 10 | 0.8 |  | 8
18
Extra for providing and placing in position 2 Nos. 6mm dia. M.S. bars at every third course of half brick masonry
| Nursing counter in front of LB |  | 1 | 4.5 | 0.8 |  | 3.6
| Nursing counter Gy-1 & 3rd |  | 2 | 4 | 0.8 |  | 6.4
| Lb Counter |  | 1 | 10 | 0.8 |  | 8
18
36
Reinforced cement concrete work in beams, suspended floors, roofs having slope upto 15degree, landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases upto floor V level including cost of centering, shuttering, finishing and excluding the cost of reinforcement in 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size)
| Nursing counter in front of LB |  | 1 | 3 | 0.8 | 0.08 | 0.192
| Nursing counter Gy-1 & 3rd |  | 2 | 3 | 0.8 | 0.08 | 0.384
| Lb Counter |  | 1 | 6 | 0.8 | 0.08 | 0.384
0.96
Reinforcement for RCC works including straightening, cutting, bending, placing in position and binding all complete. Thermo - Mechanically treated bars (Using Vizac, Tata or SAIL)
96
Providing and laying anti skid ceramic floor tiles of minimum 400x400 mm size for toilets (7.5mm thickness or nearest size) M/s. JOHNSON, KAJARIA, NITCO, SOMANY or equivalent of 1st quality conforming to IS: 15622 of approved make in all colours, shades, except white, ivory, grey, fume red brown laid on 20mm thick bed of cement mortar 1:4 (1 cement : 4 coarse sand) including pointing the joints with white cement and matching pigments etc complete.
|  |  | 2 | 2 | 1.5 |  | 6
Providing and fixing Ist quality ceramic glazed wall tiles conforming to IS: 15622 of minimum 350x250 mm size and thickness 5MM of JOHNSON, NITCO, ORIENT, , KAJARIA ,or approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados,over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand)and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete
| counters |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 2 | 6 | 0.8 |  | 9.6
|  |  | 4 | 1 | 0.6 |  | 2.4
|  |  | 1 | 3 | 0.6 |  | 1.8
|  |  | 1 | 6 | 0.6 |  | 3.6
12mm cement plaster on rough side of single or half brick wall finished with a floating coat of neat cement of mix 1:4 ( 1 cement : 4 fine sand)
| Nursing counter in front of LB |  | 1 | 3 | 0.65 |  | 1.95
|  |  | 6 | 0.8 | 0.7 |  | 3.36
|  |  | 1 | 3 | 0.6 |  | 1.8
| Nursing counter Gy-1 & 3rd |  | 2 | 3 | 0.65 |  | 3.9
|  |  | 6 | 0.8 | 0.7 |  | 3.36
|  |  | 2 | 3 | 0.6 |  | 3.6
|  |  | 1 | 6 | 0.6 |  | 3.6
|  |  | 10 | 0.8 | 0.7 |  | 5.6
27.17
Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade in two or more coats on new work, including finishing walls with Deluxe Multi surface paint system for interiors and exteriors using Primer as per manufacturers specifications: Two or more coats applied on walls @ 1.25 ltr/10 sqm over and including one coat of Special primer applied @ 0.75 ltr / 10 sqm
| Nursing counter in front of LB |  | 1 | 3 | 0.65 |  | 1.95
|  |  | 6 | 0.8 | 0.7 |  | 3.36
|  |  | 1 | 3 | 0.6 |  | 1.8
| Nursing counter Gy-1 & 3rd |  | 2 | 3 | 0.65 |  | 3.9
|  |  | 6 | 0.8 | 0.7 |  | 3.36
|  |  | 2 | 3 | 0.6 |  | 3.6
| Lb Counter |  | 1 | 6 | 0.6 |  | 3.6
|  |  | 10 | 0.8 | 0.7 |  | 5.6
27.17
Providing and fixing 18mm thick gang saw cut mirror polished (premoulded and prepolished) machine cut for kitchen platforms, vanity counters, window sills, facias and similar locations of required size of approved shade, colour and texture laidover 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing moulding and polishing to edge to give high gloss finish etc. complete at all levels. Granite of any colour & Shade
| lift entry wall clading |  | 1 | 4 | 2.5 |  | 10
| Nursing counter in front of LB |  | 1 | 3 | 0.65 |  | 1.95
| Nursing counter Gy-1 & 3rd |  | 2 | 3 | 0.65 |  | 3.9
| Lb Counter |  | 1 | 6 | 0.6 |  | 3.6
| total | [5 empty] | 19.45
| say | [5 empty] | 20
Providing edge moulding to 18mm thick marble stone counters, Vanities etc. including machine polishing to edge to give high gloss finish etc. complete as per design approved by Engineer-in-Charge.
| Nursing counter in front of LB |  | 1 | 3.7 |  |  | 3.7
| Nursing counter Gy-1 & 3rd |  | 2 | 4.5 |  |  | 9
| Lb Counter |  | 1 | 6.8 |  |  | 6.8
| total | [5 empty] | 19.5
| say | [5 empty] | 20
Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixed with rawl plugs and screws or with fixing clips, or with expansion hold fasteners including necessary filling up of gaps at junctions, at top, bottom and sides with required PVC/ neoprene felt etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing/panelling. C.P. brass/ stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing and panelling to be paid for separately): For fixed portion Anodised aluminium (anodised transparent or dyed required shade according to IS: 1868, Minimum anodic coating of grade AC 15)
DOORS -(
| 150*210 |  | 2 | 5.6 |  |  | 11.2
| 100*210 |  | 3 | 5.1 |  |  | 15.3
26.5
| @ 1.372kg/m | [5 empty] | 36.358
Partitions
| outer sections | [6 empty] | 2.65
| Nursing counter in front of LB |  | 1 | 18 |  |  | 18 | 9.4
| Nursing counter Gy-1 & 3rd |  | 2 | 16.5 |  |  | 33
51
| @ 1.777kg/m | [5 empty] | 90.627
intermediate sections
| Nursing counter in front of LB |  | 1 | 27 |  |  | 27
| Nursing counter Gy-1 & 3rd |  | 2 | 25.5 |  |  | 51
| Total | [5 empty] | 78
| @ 1.439kg/m | [5 empty] | 112.242
| Total | [5 empty] | 239.227
| say | [5 empty] | 250
For shutters of doors, windows & ventilators including providing and fixing hinges / pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately).Powder coated aluminium (minimum thickness of powder coating 50 micron
DOORS -
150*210
| vertical |  | 2 | 8.05 | 16.1 | @1.1kg/m | 17.71
| lock |  | 2 | 1.25 | 2.5 | @ 0.904kg/m | 2.26
| bottom |  | 2 | 1.25 | 2.5 | @ 1.504kg/m | 3.76
| top |  | 2 | 1.25 | 2.5 | @ 0.904kg/m | 2.26
| clip |  | 2 | 24.5 | 49 | @ 0.124kg/m | 6.076
| c.angle |  | 2 | 1 | 2 | @0 .632kg/m | 1.264
| beading |  | 2 | 5.25 | 10.5 | @ 0.14kg/m | 1.47
| sub total | [5 empty] | 34.8
100*210
| vertical |  | 3 | 4.5 | 13.5 | @1.1kg/m | 14.85
| lock |  | 3 | 0.85 | 2.55 | @ 0.904kg/m | 2.3052
| bottom |  | 3 | 0.85 | 2.55 | @ 1.504kg/m | 3.8352
| top |  | 3 | 0.85 | 2.55 | @ 0.904kg/m | 2.3052
| clip |  | 3 | 14 | 42 | @ 0.124kg/m | 5.208
| c.angle |  | 3 | 0.75 | 2.25 | @0 .632kg/m | 1.422
| S.total | [5 empty] | 29.9256
for partioions
clip
outer sections
| Nursing counter in front of LB |  | 2 | 17 |  |  | 34
| Nursing counter Gy-1 & 3rd |  | 4 | 16.5 |  |  | 66
intermediate sections
| Nursing counter in front of LB |  | 2 | 27 |  |  | 54
| Nursing counter Gy-1 & 3rd |  | 4 | 25.5 |  |  | 102
[6 empty] | @ 0.124kg/m | 256
| S.total | [5 empty] | 31.744
| c.angle |  | 75 | 0.05 | 3.75 | @0 .632kg/m | 2.37
| Total | [5 empty] | 98.8396
| Say | [5 empty] | 100
Providing and fixing 100mm brass locks (best make of approved quality) for aluminium doors including necessary cutting and making good etc. complete.
|  |  | 5 |  |  |  | 5
Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with PVC/neoprene gasket etc. complete as per the architectural drawings and directions of engineer-in-charge. (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.0 mm thickness
door
| 150*210 |  | 2*2 | 1.1 | 0.75 |  | 3.3
| 100*210 |  | 3 | 1.1 | 1 |  | 3.3
Partitions
| Nursing counter in front of LB |  | 1 | 1.1 | 2.5 |  | 2.75
| Nursing counter Gy-1 & 3rd |  | 2 | 1.1 | 5.3 |  | 11.66
21.01
Providing and fixing12mm thick prelaminated particle board flat pressed three layer or graded wood particle board conforming to IS12823 Grade 1 type II, in panelling fixed in aluminium doors, windows shutters and partition frames with C.P brass/ stainless steel screws etc. complete as per architectural drawings and directions of engineer in charge Pre laminated particle board with decorative lamination on both sides
door
| 150*210 |  | 2*2 | 1 | 0.75 |  | 3
| 100*210 |  | 3 | 1 | 1 |  | 3
Partitions
| Nursing counter in front of LB |  | 1 | 1.3 | 7 |  | 9.1
|  |  | 1 | 1 | 6 |  | 6
| Nursing counter Gy-1 & 3rd |  | 1 | 1.3 | 6.3 |  | 8.19
|  |  | 1 | 1 | 5.3 |  | 5.3
| Total | [5 empty] | 34.59
| say | [5 empty] | 70
Providing and fixing double action hydraulic floor spring of approved brand andmanufacture IS : 6315 marked, for doors including cost of cutting floors as required,embedding in floors and cover plates with brass pivot and single piece M.S. sheetouter box with slide plate etc. complete as per the direction of Engineer-in-chargse With stainless steel cover plate
| door 150*210 |  | 2*2 |  |  |  | 4
| say | [5 empty] | 4
Providing and fixing IS : 3564 marked Aluminium die cast body tubular type universal hydraulic door closer with necessary accessories and screws etc. complete
| 100*210 |  | 15 |  |  |  | 15
Providing nad fixing aluminium hanging floor door stopper ISImarked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparant or dyed to required colour and shade with necessary screws etc. complete. Single rubber stopper
| 100*210 |  | 15 |  |  |  | 15
providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent od dyed to required colour or shade with necessary screws etc. complete: 250 x 10 mm
door
| 150*210 |  | 4 |  |  |  | 4
| 100*210 |  | 3 |  |  |  | 3
7
Providing and fixing wash basin with C.I/ M.S brackets, 15mm C.P. brass pillar taps Kingston/ Gem/ Techno/ Parko, 32mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls and floors wherever require: White Vitreous China Wash basin size 550x400 mm with a pair of 15 mm C.P. brass pillar taps
| consulting rooms |  | 6
| Providing and fixing unplasticised PVC connection pipes with brass unions 30 cm length 15mm nominal bore |  | 8
| Providing and fixing waste pipe for sink, wash basin or urinals including PVC waste fittings complete:Semi Rigid Pipe-32mm diameter |  | 8
| Providing and fixing stainless steel scurb 2500x600x800mm with C.I brackets and stainless steel plug 40mm including painting of fittings and brackets ,cutting and making good the walls wherever required a)Scub with drain board |  | 2
| Providing and fixing 600x450mm bevelled edge mirror 5mm thick of superior glass(of approved quality) complete with 6mm thick hard board ground fixed to wooden cleats with C.P.brass screws and washers complete. |  | 7
| Providing and fixing C.P towel rail complete with brackets fixed to wooden cleats with C.P.brass screws with conceiled fittings arrangement of approved quality ,size and make |  | 15
| Providing and fixing S.S soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements. Weighing not less than 106 gms. |  | 15
| Providing and jointing PVC 63mm PVC pipes of (pressure 6 kg/cm2) for drainage line including testing of joints etc complete. (Sullage Down pipe) 63mm diameter (OD) |  |  | 15
| Providing and fixing unplasticised-P.V.C pipes clips of approved design to unplasticised-P.V.C rain water pipes by means of 50 x 50 x 50 mm hard wood plugs, screwed with M.S screws of required length including cutting brick work and fixing in cement mortar 1 : 4 (1 cement : 4 coarse sand) and making good the walls etc. complete 110mm |  | 15 |  |  |  | 15
| Providing and fixing C.P brass long body bib cock of approved quality conforming to IS standards and weighing not less than 690 gms. 15 mm nominal bore With long Handle |  | 2 |  |  |  | 2
Providing and fixing wall face PVC pipe complete including cutting,chasing in walls and making good the walls etc complete.
| 25mm PVC pipe (10kg/sqcm) |  | 1 | 25 |  |  | 25
| 32mm PVC pipe 1(10kg/sqcm) |  | 1 | 15 |  |  | 15

## FIRST FLOOR-- Kitchen (hidden)
Name of work : RENNOVATION OF GENERAL HOSPITAL AT KALPETTA IN WAYANAD DISTRICT
GENERAL HOSPITAL - KALPETTA
DETAILED ESTIMATE
S.N | Description | Unit | NO | Length | Width | Depth | Quantity
FIRST FLOOR--KITCHEN
1 | Demolishing R.C.C. work manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per direction of Engineer - in- charge.
|  |  | 12 | 0.6 | 0.3 | 1.5 | 3.24
Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge
| passage |  | 1 | 1.5 | 0.2 | 2.1 | 0.63
| stair room |  | 4 | 3 | 0.2 | 2.8 | 6.72
| Total | [5 empty] | 7.35
| say | [5 empty] | 8
Dismantling steel work in built up sections in angles, tees, flats and channels including all gusset plates, bolts, nuts, cutting rivets, welding etc. including dismembering and stacking within 50metres lead.
| lift passage |  | 1 | 4 | 6.5 |  | 26
| @ 20 kg/m2 | [5 empty] | 520
| say | [5 empty] | 550
Dismantling roofing including ridges, hips, valleys and gutters etc., and stacking the material within 50 metres lead of:G.S. Sheet
| lift passage |  | 1 | 4 | 6.5 |  | 26
| say | [5 empty] | 28
Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in :Cement mortar 1:4 (1 cement : 4 coarse sand
| kitchen |  | 2 | 9.4 | 0.2 | 3 | 11.28
|  |  | 1 | 15.5 | 0.2 | 3 | 9.3
|  |  | 2 | 4.5 | 0.2 | 3 | 5.4
|  |  | 2 | 3 | 0.2 | 3 | 3.6
| head room |  | 2 | 4.5 | 0.2 | 3 | 5.4
|  |  | 1 | 3 | 0.2 | 2.8 | 1.68
| Total | [5 empty] | 36.66
| deduction |  | 1 | 1.5 | 0.2 | 2.1 | 0.63
|  |  | 11 | 1.5 | 0.2 | 1.5 | 4.95
5.58
| Total after deduction | [5 empty] | 31.08
Half brick masonry with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level.Cement mortar 1:4 (1 cement :4 coarse sand)
| parapet wall |  | 1 | 15.8 | 0.8 |  | 12.64
|  |  | 2 | 9.5 | 0.8 |  | 15.2
| COUNTER |  | 1 | 4.5 | 0.8 |  | 3.6
|  |  | 1 | 6 | 0.8 |  | 4.8
|  |  | 10 | 0.8 | 0.8 |  | 6.4
42.64
Extra for providing and placing in position 2 Nos. 6mm dia. M.S. bars at every third course of half brick masonry
| parapet wall |  | 1 | 15.8 | 0.8 |  | 12.64
|  |  | 2 | 9.5 | 0.8 |  | 15.2
| COUNTER |  | 1 | 4.5 | 0.8 |  | 3.6
|  |  | 1 | 6 | 0.8 |  | 4.8
|  |  | 10 | 0.8 | 0.8 |  | 6.4
14.8
Reinforced cement concrete work in beams, suspended floors, roofs having slope upto 15degree, landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases upto floor V level including cost of centering, shuttering, finishing and excluding the cost of reinforcement in 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size)
| slab |  | 1 | 9.5 | 15.8 | 0.12 | 18.012
| beams |  | 4 | 9.5 | 0.2 | 0.5 | 3.8
|  |  | 3 | 15.8 | 0.2 | 0.6 | 5.688
|  |  | 1 | 3 | 0.3 | 0.45 | 0.405
| sunshade |  | 2 | 9.5 | 1.2 | 0.1 | 2.28
|  |  | 1 | 15.8 | 1.2 | 0.1 | 1.896
| lintel |  | 4 | 2 | 0.2 | 0.2 | 0.32
|  |  | 1 | 35 | 0.2 | 0.2 | 1.4
| stair case |  | 1 | 3 | 1 | 0.15 | 0.45
|  |  | 2 | 3.8 | 1 | 0.15 | 1.14
| steps |  | 25 | 1 | 0.15 | 0.15 | 0.5625
| counter |  | 1 | 4.5 | 0.7 | 0.08 | 0.252
|  |  | 1 | 6 | 0.7 | 0.08 | 0.336
| kerb in srair head room |  | 1 | 3 | 0.2 | 0.2 | 0.12
|  |  | 2 | 4.5 | 0.2 | 0.2 | 0.36
| Total | [5 empty] | 37.0215
deduction
| stair room |  | 1 | 4.5 | 3 | 0.12 | 1.62
| total after dediuction | [5 empty] | 35.4015
| Say | [5 empty] | 38
Reinforced cement concrete work in walls (any thickness) including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc upto floor V level including cost of centering, shuttering, finishing and excluding cost of reinforcement in 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20 mm nominal size)
| columns |  | 12 | 0.6 | 0.3 | 3.45 | 7.452
|  |  | 6 | 0.6 | 0.3 | 2.8 | 3.024
| Total | [5 empty] | 10.476
| Say | [5 empty] | 11
Reinforced cement concrete work in walls (any thickness) including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc upto floor V level including cost of centering, shuttering, finishing and excluding cost of reinforcement in 1:3:6 (1 cement: 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) For dummy columns
|  |  | 6 | 1.5 | 0.6 | 0.3 | 1.62
2
Reinforcement for RCC works including straightening, cutting, bending, placing in position and binding all complete. Thermo - Mechanically treated bars (Using Vizac, Tata or SAIL)
| total concrete qty. | [5 empty] | 51
| total |  | @ 140 kg / m3 |  |  |  | 7140
| say | [5 empty] | 7200
Providing and fixing M.S grills of required pattern in frames of windows etc with M.S.flats,square or round bars etc all complete:- Fixed to openings/wooden frames with rawl plugs screws etc
| window 150 x 150 |  | 11 | 1.5 | 1.5 |  | 24.75
| total |  | @ 15 kg / sqm |  |  |  | 371.25
| say | [5 empty] | 380
Providing and fixing stainless steel 12mm dia bar bent to shape with hooked ends in R.C.C. slabs during laying including, all as per standard design complete.
| fan points |  | 15 |  |  |  | 15
| say | [5 empty] | 15
Supplying and fixing 1.10m height hand rails for stair cases with 2 Nos. polished stainless steel tube of outer diameter 50mm at top and bottom with wall thickness not less than 1.60mm as per SS 304 vertical members of 50mm diameter pipe 1.00m length(approximately) welded together at 1.50m center to center and providing and fixing 2 nos 32 mm outer diameter stainless steel tube horizontally between the top and bottom tubes including fixing with steel nuts and bolts as per the direction of the Engineer – in – charge. Hand rails shall be fixed in the floor/steps with expansion hold fasters of required size including drilling etc. complete.
50mmØ ss.pips
| horizontal |  | 2 | 12 |  |  | 24
| vertical |  | 8 | 1.1 |  |  | 8.8
| Sub total | [5 empty] | 32.8
| 50mm Dia @1.822 kg/m | [5 empty] | 59.7616
| 32mmØ ss.pips |  | 2 | 12 |  |  | 24
| 32mm Dia @ 1.11 kg/m | [5 empty] | 26.64
| total | [5 empty] | 86.4016
| say | [5 empty] | 90
Providing and laying polished vitrified floor tiles of minimum size 600x600mm of thickness 10mm or nearest size of M/s. JOHNSON, KAJARIA, NITCO, SOMANY or equivalent in light colours and shades, with water absorption's less than 0.08% and conforming to IS:15622, laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand) including grouting the joints with cement and matching pigments etc, complete as directed by the Engineer-in-charge.
| kitchen area & dininig |  | 1 | 15.5 | 9.3 |  | 144.15
|  |  | 1 | 1.5 | 0.2 |  | 0.3
| steps |  | 25 | 1.2 | 0.3 |  | 9
|  |  | 25 | 1.2 | 0.15 |  | 4.5
157.95
| deduct |  | 1 | 4 | 3 |  | 12
145.95
| Say | [5 empty] | 146
Providing and fixing Ist quality ceramic glazed wall tiles conforming to IS: 15622 of minimum 350x250 mm size and thickness 5MM of JOHNSON, NITCO, ORIENT, , KAJARIA ,or approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados,over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand)and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete
| kitchen and dining |  | 4 | 9.3 | 1.4 |  | 52.08
|  |  | 2 | 15.5 | 1.4 |  | 43.4
|  |  | 2 | 3 | 1.4 |  | 8.4
|  |  | 2 | 5.5 | 1.4 |  | 15.4
119.28
deduct
| windows |  | 8 | 1.5 | 0.3 |  | 3.6
| door |  | 2 | 1.5 | 1.5 |  | 4.5
| door |  | 2 | 1.2 | 1.5 |  | 3.6
| total | [5 empty] | 11.7
| say | [5 empty] | 107.58
12mm cement plaster on rough side of single or half brick wall finished with a floating coat of neat cement of mix 1:4 ( 1 cement : 4 fine sand)
| kitchen and dining area |  | 1 | 15.8 | 3.55 |  | 56.09
|  |  | 5 | 9.2 | 3.55 |  | 163.3
|  |  | 1 | 6.3 | 3.55 |  | 22.365
|  |  | 1 | 3 | 3.55 |  | 10.65
|  |  | 1 | 3 | 3.55 |  | 10.65
|  |  | 2 | 1.5 | 1.5 |  | 4.5
| parapet wall |  | 1 | 15.8 | 0.8 |  | 12.64
|  |  | 2 | 9.5 | 0.8 |  | 15.2
| stair case |  | 2 | 3.8 | 1 |  | 7.6
| steps |  | 25 | 1 | 0.15 |  | 3.75
| counter |  | 1 | 4.5 | 0.7 |  | 3.15
|  |  | 1 | 6 | 0.7 |  | 4.2
| stair head room |  | 1 | 3.2 | 2.8 |  | 8.96
|  |  | 2 | 6 | 2.8 |  | 33.6
| terrace plastering |  | 1 | 15.8 | 9.2 |  | 145.36
| total | [5 empty] | 502.015
deduct
| door |  | 4 | 1.5 | 2.1 |  | 12.6
| door |  | 4 | 1.2 | 2.1 |  | 10.08
| total | [5 empty] | 22.68
| total after deduction | [5 empty] | 479.335
| say | [5 empty] | 485
6mm cement plaster to ceiling of mix 1 : 3 (1 cement : 3 fine sand )
| slab |  | 1 | 9.5 | 15.8 |  | 150.1
| beams |  | 4 | 9.5 | 0.2 |  | 7.6
|  |  | 3 | 15.8 | 0.2 |  | 9.48
|  |  | 1 | 3 | 0.3 |  | 0.9
| sunshade |  | 2 | 9.5 | 1.2 |  | 22.8
|  |  | 1 | 15.8 | 1.2 |  | 18.96
| total | [5 empty] | 209.84
15mm cement plaster on rough side of single or half brick wall finished with a floating coat of neat cement of mix 1:5 ( 1 cement :5 fine sand)
| kitchen out side and dining outside area |  | 1 | 15.8 | 5.25 |  | 82.95
|  |  | 2 | 9.5 | 5.25 |  | 99.75
| stair head room |  | 1 | 3.2 | 2.8 |  | 8.96
|  |  | 2 | 6 | 2.8 |  | 33.6
| total | [5 empty] | 225.26
| say | [5 empty] | 226
Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade in two or more coats on new work, including finishing walls with Deluxe Multi surface paint system for interiors and exteriors using Primer as per manufacturers specifications: Two or more coats applied on walls @ 1.25 ltr/10 sqm over and including one coat of Special primer applied @ 0.75 ltr / 10 sqm
| quty from plastering | [5 empty] | 694.84
| say | [5 empty] | 550
Finishing walls with Acrylic Smooth exterior paint of required shade: —New work (Two or more coat applied @ 1.67 ltr/10 sqm over and including basecoat of water proofing cement paint applied @ 2.20 kg/ 10 sqm)
| quty from plastering | [5 empty] | 226
| say | [5 empty] | 226
Steel Work painting- Painting with synthetic enamel paint of approved brand and manufacture to give an even shade. Two or more coats on new work
| window grill painting |  | 11 | 1.5 | 1.5 |  | 24.75
| say |  | sqm |  |  |  | 25
Extra for providing and mixing water proofing material in cement plaster work in proportion recommended by the manufacturers.
| terrace plastering |  | 1 | 15.8 | 9.2 |  | 145.36
| @ 5.4 kg/ sqm | [5 empty] | 15.6989
| Say | [5 empty] | 16 bags
Providing and fixing 18mm thick gang saw cut mirror polished (premoulded and prepolished) machine cut for kitchen platforms, vanity counters, window sills, facias and similar locations of required size of approved shade, colour and texture laidover 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing moulding and polishing to edge to give high gloss finish etc. complete at all levels. Granite of any colour & Shade
| kitchen platform |  | 1 | 6.1 | 0.7 |  | 4.27
|  |  | 1 | 4.5 | 0.7 |  | 3.15
| total | [5 empty] | 7.42
| say | [5 empty] | 7.5
Providing edge moulding to 18mm thick marble stone counters, Vanities etc. including machine polishing to edge to give high gloss finish etc. complete as per design approved by Engineer-in-Charge.
| kitchen platform |  | 1 | 6.1 |  |  | 6.1
|  |  | 1 | 4.5 |  |  | 4.5
| total | [5 empty] | 10.6
| say | [5 empty] | 11
| Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixed with rawl plugs and screws or with fixing clips, or with expansion hold fasteners including necessary filling up of gaps at junctions, at top, bottom and sides with required PVC/ neoprene felt etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing/panelling. C.P. brass/ stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing and panelling to be paid for separately): For fixed portion Anodised aluminium (anodised transparent or dyed required shade according to IS: 1868, Minimum anodic coating of grade AC 15) | [6 empty] | 35.4
DOORS -(
| 150*210 |  | 2 | 5.6 |  |  | 11.2
| 100*210 |  | 3 | 5.1 |  |  | 15.3
26.5
| @ 1.372kg/m | [5 empty] | 36.358
150*150
| botttom |  | 11 | 1.5 | 16.5 | @ 1.042kg/m | 17.193
| top |  | 11 | 4.5 | 49.5 | @ .926kg/m | 45.837
| total | [5 empty] | 63.03
| Total | [5 empty] | 99.388
| say | [5 empty] | 100
For shutters of doors, windows & ventilators including providing and fixing hinges / pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately).Powder coated aluminium (minimum thickness of powder coating 50 micron
DOORS -
150*210
| vertical |  | 2 | 8.05 | 16.1 | @1.1kg/m | 17.71
| lock |  | 2 | 1.25 | 2.5 | @ 0.904kg/m | 2.26
| bottom |  | 2 | 1.25 | 2.5 | @ 1.504kg/m | 3.76
| top |  | 2 | 1.25 | 2.5 | @ 0.904kg/m | 2.26
| clip |  | 2 | 24.5 | 49 | @ 0.124kg/m | 6.076
| c.angle |  | 2 | 1 | 2 | @0 .632kg/m | 1.264
| beading |  | 2 | 5.25 | 10.5 | @ 0.14kg/m | 1.47
100*210
| vertical |  | 3 | 4.5 | 13.5 | @1.1kg/m | 14.85
| lock |  | 3 | 0.85 | 2.55 | @ 0.904kg/m | 2.3052
| bottom |  | 3 | 0.85 | 2.55 | @ 1.504kg/m | 3.8352
| top |  | 3 | 0.85 | 2.55 | @ 0.904kg/m | 2.3052
| clip |  | 3 | 14 | 42 | @ 0.124kg/m | 5.208
| c.angle |  | 3 | 0.75 | 2.25 | @0 .632kg/m | 1.422
| S.total | [5 empty] | 64.7256
| 150*150 | [5 empty] | 0
| lock |  | 11 | 6 | 66 | @ 0.492kg/m | 32.472
| side |  | 11 | 3 | 33 | @ 0.444kg/m | 14.652
| t&B |  | 11 | 3.12 | 34.32 | @ 0.362kg/m | 12.4238
| clip |  | 11 | 19 | 209 | @ 0.194kg/m | 40.546
| c.angle |  | 11 | 0.52 | 5.72 | @ 0.424kg/m | 2.4253
| beading |  | 11 | 12 | 132 | @ 0.12kg/m | 15.84
| S.total | [5 empty] | 118.3591
| Total | [5 empty] | 183.0847
| say | [5 empty] | 190
Providing and fixing 100mm brass locks (best make of approved quality) for aluminium doors including necessary cutting and making good etc. complete.
| total |  | 5 |  |  |  | 5
Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with PVC/neoprene gasket etc. complete as per the architectural drawings and directions of engineer-in-charge. (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.0 mm thickness
door
| 150*210 |  | 2*2 | 1.1 | 0.75 |  | 3.3
| 100*210 |  | 3 | 1.1 | 1 |  | 3.3
| total | [5 empty] | 6.6
| say | [5 empty] | 7
Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with PVC/neoprene gasket etc. complete as per the architectural drawings and directions of engineer-in-charge. (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 4.0 mm thickness
| window glass |  | 11*3 | 0.5 | 1.5 |  | 24.75
| say | [5 empty] | 25
Providing and fixing12mm thick prelaminated particle board flat pressed three layer or graded wood particle board conforming to IS12823 Grade 1 type II, in panelling fixed in aluminium doors, windows shutters and partition frames with C.P brass/ stainless steel screws etc. complete as per architectural drawings and directions of engineer in charge Pre laminated particle board with decorative lamination on both sides
door
| 150*210 |  | 2*2 | 1 | 0.75 |  | 3
| 100*210 |  | 3 | 1 | 1 |  | 3
| Total | [5 empty] | 6
| say | [5 empty] | 6
Providing and fixing double action hydraulic floor spring of approved brand andmanufacture IS : 6315 marked, for doors including cost of cutting floors as required,embedding in floors and cover plates with brass pivot and single piece M.S. sheetouter box with slide plate etc. complete as per the direction of Engineer-in-chargse With stainless steel cover plate
| door 150*210 |  | 2*2 |  |  |  | 4
| say | [5 empty] | 4
Providing and fixing IS : 3564 marked Aluminium die cast body tubular type universal hydraulic door closer with necessary accessories and screws etc. complete
| 100*210 |  | 2 |  |  |  | 2
Providing nad fixing aluminium hanging floor door stopper ISImarked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparant or dyed to required colour and shade with necessary screws etc. complete. Single rubber stopper
| 100*210 |  | 2 |  |  |  | 2
providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent od dyed to required colour or shade with necessary screws etc. complete: 250 x 10 mm
door
| 150*210 |  | 2*2*2 |  |  |  | 8
| 100*210 |  | 3 |  |  |  | 3
| total | [5 empty] | 11
11
Providing and fixing window handles with necessary screws etc. complete-
| windows |  | 11*3 |  |  |  | 33
| total | [5 empty] | 33
Providing and fixing wash basin with C.I/ M.S brackets, 15mm C.P. brass pillar taps Kingston/ Gem/ Techno/ Parko, 32mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls and floors wherever require: White Vitreous China Wash basin size 550x400 mm with a pair of 15 mm C.P. brass pillar taps
| dining area |  | 4
| Providing and fixing unplasticised PVC connection pipes with brass unions 30 cm length 15mm nominal bore |  | 5
| Providing and fixing waste pipe for sink, wash basin or urinals including PVC waste fittings complete:Semi Rigid Pipe-32mm diameter |  | 5
| Providing and fixing Salem stainless steel A ISI 304 (18/8) kitchen sink as per IS 13983 with C.I brackets and stainless steel plug 40mm including painting of fittings and brackets, cutting and making good the walls wherever required a) Kitchen sink without drain board |  | 2
| Providing and fixing 600x450mm bevelled edge mirror 5mm thick of superior glass(of approved quality) complete with 6mm thick hard board ground fixed to wooden cleats with C.P.brass screws and washers complete. |  | 4
| Providing and fixing C.P towel rail complete with brackets fixed to wooden cleats with C.P.brass screws with conceiled fittings arrangement of approved quality ,size and make |  | 2
| Providing and fixing S.S soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements. Weighing not less than 106 gms. |  | 4
Providing and jointing PVC 63mm PVC pipes of (pressure 6 kg/cm2) for drainage line including testing of joints etc complete. (Sullage Down pipe) 63mm diameter (OD)
| for sink and wash basin |  |  | 70 |  |  | 70
Providing and fixing unplasticised-P.V.C pipes clips of approved design to unplasticised-P.V.C rain water pipes by means of 50 x 50 x 50 mm hard wood plugs, screwed with M.S screws of required length including cutting brick work and fixing in cement mortar 1 : 4 (1 cement : 4 coarse sand) and making good the walls etc. complete 110mm
| total |  | 50 |  |  |  | 50
Providing and fixing wall face PVC pipe complete including cutting,chasing in walls and making good the walls etc complete.
| 25mm PVC pipe (10kg/sqcm) |  | 1 | 25
| 32mm PVC pipe 1(10kg/sqcm) |  | 1 | 40
| 50mm PVC pipe (10kg/sqcm) |  | 1 | 50
Providing and fixing trap of self cleansing design with screwed down or hinged grating with or without vent arm complete, including cost of cutting and making good the walls and floors: 110mm inlet and 110mm outlet pvc
| kitchen and dining |  | 6 |  |  |  | 6
Providing and fixing PTMT (an Engineering thermo plastic ) grating of approved quality colour and make 150 mm nominal size square,100mm diameter of the inner hinged round grating. Rectangular type with circular round lid
|  |  | 6 |  |  |  | 6

## SECOND FLOOR (hidden)
Name of work : RENNOVATION OF GENERAL HOSPITAL AT KALPETTA IN WAYANAD DISTRICT
GENERAL HOSPITAL - KALPETTA
DETAILED ESTIMATE
S.N | Description | Unit | NO | Length | Width | Depth | Quantity
SECOND FLOOR
1 | Demolishing R.C.C. work manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per direction of Engineer - in- charge.
| counters |  | 3 | 6 | 0.8 | 0.1 | 1.44
| TOTAL | [5 empty] | 1.5
| Say | [5 empty] | 1.5
Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge
| counters |  | 12 | 0.8 | 0.1 | 0.8 | 0.768
| scrub |  | 1 | 3 | 0.6 | 0.6 | 1.08
| passage |  | 1 | 3 | 0.2 | 3 | 1.8
| door widening |  | 4 | 1 | 0.2 | 2.1 | 1.68
| duct |  | 1 | 1 | 0.2 | 1.5 | 0.3
| TOTAL | [5 empty] | 5.628
| say | [5 empty] | 6
Dismantling tile work in floors and roofs laid in cement mortar including stacking material within 50 metres lead.For thickness of tiles 10 mm to 25 mm
| OT floor tiles |  | 2 | 6.05 | 6.03 |  | 72.963
| Sterilization |  | 1 | 6 | 3 |  | 18
|  |  | 1 | 6 | 4.5 |  | 27
| scrub |  | 1 | 3 | 3 |  | 9
|  |  | 1 | 3 | 0.2 |  | 0.6
| wall |  | 4 | 6.03 | 1.5 |  | 36.18
|  |  | 4 | 6.05 | 1.5 |  | 36.3
|  |  | 2 | 6 | 1.5 |  | 18
|  |  | 2 | 4.5 | 1.5 |  | 13.5
231.543
| say | [5 empty] | 235
Dismantling aluminium/ Gypsum partitions, doors, windows, fixed glazing and false ceiling including disposal of unserviceable surplus material and stacking of serviceable material with in 50 meters lead as directed by Engineer-in-charge
| ot doors |  | 3 | 1.4 | 2.1 |  | 8.82
| Sterilization |  | 1 | 1.4 | 2.1 |  | 2.94
|  |  | 3 | 1 | 2.1 |  | 6.3
| ABOVE LINTEL LEVEL OF HOLDING |  | 2 | 6.5 | 1 |  | 13
|  |  | 2 | 1.5 | 2.4 |  | 7.2
| Total | [5 empty] | 38.26
40
Dismantling doors, windows and clerestory windows (steel or wood) shutter including chowkhats, architrave, holdfasts etc. complete and stacking within 50 metres lead :Of area beyond 3 sq. metres
| passage |  | 1 | 3 | 3.5 |  | 10.5
| say | [5 empty] | 12
Dismantling steel work in built up sections in angles, tees, flats and channels including all gusset plates, bolts, nuts, cutting rivets, welding etc. including dismembering and stacking within 50metres lead.
| lift passage |  | 1 | 13 | 4 |  | 52
| @ 20 kg/m2 | [5 empty] | 1040
| say | [5 empty] | 1050
Dismantling roofing including ridges, hips, valleys and gutters etc., and stacking the material within 50 metres lead of:G.S. Sheet
| lift passage |  | 1 | 13 | 4 |  | 52
| say | [5 empty] | 55
Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in :Cement mortar 1:4 (1 cement : 4 coarse sand
| icu |  | 5 | 12.9 | 0.2 | 3.1 | 39.99
|  |  | 1 | 6.2 | 0.2 | 3.1 | 3.844
| conect pasage |  | 2 | 3.1 | 0.2 | 3.1 | 3.844
| LIFT ROOM |  | 2 | 1.8 | 0.2 | 3.1 | 2.232
|  |  | 2 | 3.1 | 0.2 | 3.1 | 3.844
| Sterilization |  | 1 | 3 | 0.2 | 3.1 | 1.86
| passage |  | 1 | 3 | 0.2 | 3.1 | 1.86
| PASSAGE WALL IN STERAIL |  | 1 | 3 | 0.2 | 3.45 | 2.07
| door closing |  | 1 | 1.5 | 0.2 | 2.1 | 0.63
| TOTAL | [5 empty] | 60.174
| deduction |  | 12 | 1.5 | 0.2 | 1.5 | 5.4
|  |  | 2 | 1.5 | 0.2 | 2.1 | 1.26
6.66
| Total after deduction | [5 empty] | 53.514
| SAY | [5 empty] | 53
Half brick masonry with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level.Cement mortar 1:4 (1 cement :4 coarse sand)
| VETILATOR CLOSING IN OT PASSAGE |  | 15 | 1.5 | 0.7 |  | 15.75
| ABOVE LINTEL LEVEL OF HOLDING |  | 2 | 6.5 | 1 |  | 13
| OT 3 PLATFORM |  | 4 | 0.6 | 0.6 |  | 1.44
| COUNTER-ICU |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| COUNTER-F P O WARD |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| COUNTER-M P OWARD |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| Total | [5 empty] | 43.15
| SAY | [5 empty] | 45
Extra for providing and placing in position 2 Nos. 6mm dia. M.S. bars at every third course of half brick masonry
| VETILATOR CLOSING IN OT PASSAGE |  | 15 | 1.5 | 0.7 |  | 15.75
| ABOVE LINTEL LEVEL OF HOLDING |  | 2 | 6.5 | 1 |  | 13
| OT 3 PLATFORM |  | 4 | 0.6 | 0.6 |  | 1.44
| COUNTER-ICU |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| COUNTER-F P O WARD |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| COUNTER-M P OWARD |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| Total | [5 empty] | 43.15
| SAY | [5 empty] | 45
Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering1:3:6 (1 Cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size).
| in ICU toilet |  | 2 | 1.5 | 1.5 | 0.2 | 0.9
| Total | [5 empty] | 0.9
| SAY | [5 empty] | 1
Providing and laying water proofing treatment in sunken portion of WCs, bathroom etc., by applying cement slurry mixed with water proofing cement compound consisting of applying : (a) First layer of slurry of cement @ 0.488 kg/sqm mixed with water proofing cement compound @ 0.253 kg/sqm. This layer will be allowed to air cure for 4 hours (b) Second layer of slurry of cement @ 0.242 kg/sqm mixed with water proofing cement compound @ 0.126 kg/sqm. This layer will be allowed to air cure for 4 hours followed with water curing for 48 hours The rate includes preparation of surface, treatment and sealing of all joints,corners, junctions of pipes and masonry with polymer mixed slurry.
| in ICU toilet |  | 2 | 2 | 2 |  | 8
| total | [5 empty] | 8
| say | [5 empty] | 8
Reinforced cement concrete work in beams, suspended floors, roofs having slope upto 15degree, landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases upto floor V level including cost of centering, shuttering, finishing and excluding the cost of reinforcement in 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size)
| slab |  | 1 | 12.85 | 12.85 | 0.12 | 19.8147
| connection passage |  | 1 | 3 | 3 | 0.12 | 1.08
| connection passage- beam |  | 2 | 3 | 0.2 | 0.6 | 0.72
| beams |  | 3 | 12.85 | 0.2 | 0.6 | 4.626
|  |  | 5 | 12.85 | 0.2 | 0.6 | 7.71
|  |  | 2 | 6.5 | 0.2 | 0.45 | 1.17
| sunshade |  | 2 | 12.85 | 1.2 | 0.1 | 3.084
|  |  | 2 | 3 | 1.2 | 0.1 | 0.72
|  |  | 2 | 12.85 | 1.2 | 0.1 | 3.084
| lintel |  | 4 | 12.85 | 0.2 | 0.2 | 2.056
|  |  | 2 | 3 | 0.2 | 0.2 | 0.24
|  |  | 5 | 2 | 0.2 | 0.2 | 0.4
|  |  | 4 | 2.4 | 0.1 | 0.2 | 0.192
|  |  | 2 | 3 | 0.1 | 0.2 | 0.12
| stair case |  | 1 | 3 | 1.5 | 0.15 | 0.675
|  |  | 2 | 4.2 | 1 | 0.15 | 1.26
| steps |  | 25 | 1 | 0.15 | 0.15 | 0.5625
| LINTEL OF HOLDING |  | 2 | 6.5 | 0.2 | 0.2 | 2.6
| counter |  | 4 | 4.5 | 0.7 | 0.08 | 1.008
|  |  | 1 | 4.5 | 0.7 | 0.08 | 0.252
| Total | [5 empty] | 51.3742
deduction
| stair room |  | 1 | 4.5 | 3 | 0.12 | 1.62
| LIFT ROOM |  | 1 | 4 | 6 | 0.12 | 2.88
| total deduction | [5 empty] | 4.5
| total after dediuction | [5 empty] | 46.8742
| Say | [5 empty] | 47
Reinforced cement concrete work in walls (any thickness) including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc upto floor V level including cost of centering, shuttering, finishing and excluding cost of reinforcement in 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20 mm nominal size)
| columns |  | 16 | 0.6 | 0.3 | 3.45 | 9.936
| Total | [5 empty] | 9.936
| Say | [5 empty] | 10
Reinforcement for RCC works including straightening, cutting, bending, placing in position and binding all complete. Thermo - Mechanically treated bars (Using Vizac, Tata or SAIL)
| total concrete qty. | [5 empty] | 57
| total |  | @ 140 kg / m3 |  |  |  | 7980
| say | [5 empty] | 7800
Providing and fixing M.S grills of required pattern in frames of windows etc with M.S.flats,square or round bars etc all complete:- Fixed to openings/wooden frames with rawl plugs screws etc
| window 150 x 150 |  | 12 | 1.5 | 1.5 |  | 27
|  |  | 2 | 0.65 | 0.65 |  | 0.845
| total | [5 empty] | 27.845
| total |  | @ 15 kg / sqm |  |  |  | 417.675
| say | [5 empty] | 418
Providing and fixing stainless steel 12mm dia bar bent to shape with hooked ends in R.C.C. slabs during laying including, all as per standard design complete.
| fan points |  | 15 |  |  |  | 15
| say | [5 empty] | 15
Supplying and fixing 1.10m height hand rails for stair cases with 2 Nos. polished stainless steel tube of outer diameter 50mm at top and bottom with wall thickness not less than 1.60mm as per SS 304 vertical members of 50mm diameter pipe 1.00m length(approximately) welded together at 1.50m center to center and providing and fixing 2 nos 32 mm outer diameter stainless steel tube horizontally between the top and bottom tubes including fixing with steel nuts and bolts as per the direction of the Engineer – in – charge. Hand rails shall be fixed in the floor/steps with expansion hold fasters of required size including drilling etc. complete.
50mmØ ss.pips
| horizontal |  | 2 | 15 |  |  | 30
| vertical |  | 12 | 1.1 |  |  | 13.2
| Sub total | [5 empty] | 43.2
| 50mm Dia @1.822 kg/m | [5 empty] | 78.7104
| 32mmØ ss.pips |  | 2 | 15 |  |  | 30
| 32mm Dia @ 1.11 kg/m | [5 empty] | 33.3
| total | [5 empty] | 112.0104
| say | [5 empty] | 115
Providing and laying polished vitrified floor tiles of minimum size 600x600mm of thickness 10mm or nearest size of M/s. JOHNSON, KAJARIA, NITCO, SOMANY or equivalent in light colours and shades, with water absorption's less than 0.08% and conforming to IS:15622, laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand) including grouting the joints with cement and matching pigments etc, complete as directed by the Engineer-in-charge.
| OT 1,2 |  | 2 | 6.1 | 6.1 |  | 74.42
| OT-3 |  | 1 | 6.1 | 4.7 |  | 28.67
| AUTO CLAVE |  | 1 | 6.1 | 3.5 |  | 21.35
| ICU BLOCK |  | 1 | 12.7 | 6.3 |  | 80.01
|  |  | 1 | 12.75 | 3.1 |  | 39.525
|  |  | 1 | 3 | 3.5 |  | 10.5
254.475
deduct
| TOILET AREA |  | 1 | 2.4 | 1.5 |  | 3.6
| TOTAL AFTER DEDUCTIONS | [5 empty] | 250.875
| Say | [5 empty] | 251
Providing and fixing Ist quality ceramic glazed wall tiles conforming to IS: 15622 of minimum 350x250 mm size and thickness 5MM of JOHNSON, NITCO, ORIENT, , KAJARIA ,or approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados,over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand)and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete
| ICU BLOCK |  | 2 | 12.75 | 1.5 |  | 38.25
|  |  | 2 | 6.75 | 1.5 |  | 20.25
| connection passage |  | 2 | 4.5 | 1.5 |  | 13.5
| MAIN PASSAGE |  | 2 | 3.1 | 1.5 |  | 9.3
|  |  | 2 | 12.85 | 1.5 |  | 38.55
|  |  | 1 | 3.5 | 1.5 |  | 5.25
|  |  | 2 | 2.5 | 1.5 |  | 7.5
|  |  | 2 | 3 | 1.5 |  | 9
| TOILET |  | 4 | 1.2 | 1.5 |  | 7.2
|  |  | 4 | 1.5 | 1.5 |  | 9
|  |  | 2 | 1.5 | 1.5 |  | 4.5
|  |  | 2 | 2.5 | 1.5 |  | 7.5
| counters |  | 5 | 3 | 0.8 |  | 19.2
189
deduct
| windows |  | 8 | 1.5 | 0.3 |  | 3.6
| door |  | 2 | 1.5 | 1.5 |  | 4.5
| door |  | 1 | 1.2 | 1.5 |  | 1.8
| total | [5 empty] | 9.9
| TOTAL AFTER DEDUCTIONS | [5 empty] | 179.1
| SAY | [5 empty] | 180
Providing and laying anti skid ceramic floor tiles of minimum 400x400 mm size for toilets (7.5mm thickness or nearest size) M/s. JOHNSON, KAJARIA, NITCO, SOMANY or equivalent of 1st quality conforming to IS: 15622 of approved make in all colours, shades, except white, ivory, grey, fume red brown laid on 20mm thick bed of cement mortar 1:4 (1 cement : 4 coarse sand) including pointing the joints with white cement and matching pigments etc complete.
| ICU TOILETS |  | 2 | 1.3 | 1.5 |  | 3.9
| TOTAL | [5 empty] | 3.9
| SAY | [5 empty] | 4
12mm cement plaster on rough side of single or half brick wall finished with a floating coat of neat cement of mix 1:4 ( 1 cement : 4 fine sand)
| INSIDE OF OT-1,2 |  | 8 | 13 | 3.5 |  | 364
| CURVING THE corner & COLUMN SIDE |  | 3*8 | 3.5 | 0.5 |  | 42
| INSIDE OF OT-3 |  | 4 | 6.5 | 3.5 |  | 91
| AUTO CLAVE ROOM |  | 2 | 9.5 | 3.5 |  | 66.5
| VENTLATO CLOSINGS |  | 30 | 1.5 | 0.6 |  | 27
| ABOVE LINTEL LEVEL OF HOLDING |  | 4 | 6.5 | 1 |  | 26
| DUCT INSIDE |  | 16 | 1.5 | 3.45 |  | 82.8
| ICU BLOCK |  | 2 | 12.75 | 1.5 |  | 38.25
|  |  | 2 | 6.75 | 1.5 |  | 20.25
| MAIN PASSAGE |  | 2 | 3.1 | 1.5 |  | 9.3
|  |  | 2 | 12.85 | 1.5 |  | 38.55
|  |  | 1 | 3.5 | 1.5 |  | 5.25
|  |  | 2 | 2.5 | 1.5 |  | 7.5
|  |  | 2 | 3 | 1.5 |  | 9
| LIFT IN SIDE |  | 4 | 1.8 | 3.55 |  | 25.56
|  |  | 4 | 3 | 3.55 |  | 42.6
| TOILET |  | 4 | 1.2 | 1.5 |  | 7.2
|  |  | 4 | 1.5 | 1.5 |  | 9
|  |  | 2 | 1.5 | 1.5 |  | 4.5
|  |  | 2 | 2.5 | 1.5 |  | 7.5
|  |  | 2 | 1.2 | 1.5 |  | 3.6
|  |  | 2 | 1.5 | 1.5 |  | 4.5
counters
| OT 3 PLATFORM |  | 4 | 0.6 | 0.6 |  | 1.44
| COUNTER-ICU |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| COUNTER-F P O WARD |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| COUNTER-M P OWARD |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
946.26
deduct
| door |  | 2 | 1.5 | 1.5 |  | 4.5
| door |  | 1 | 1.2 | 1.5 |  | 1.8
| total | [5 empty] | 6.3
| TOTAL AFTER DEDUCTIONS | [5 empty] | 939.96
| SAY | [5 empty] | 940
6mm cement plaster to ceiling of mix 1 : 3 (1 cement : 3 fine sand )
| ICU BLOCK |  | 1 | 12.75 | 12.75 |  | 162.5625
| SUNSHADE BOTTOM |  | 2 | 13 | 1.1 |  | 28.6
|  |  | 2 | 13 | 1.1 |  | 28.6
| STAIR BOTTOM |  | 1 | 3 | 1.5 |  | 4.5
|  |  | 2 | 5.5 | 1.5 |  | 16.5
|  |  | 2 | 5.5 | 0.5 |  | 5.5
| counter slab bottom |  | 5 | 3 | 0.8 |  | 12
| TOTAL | [5 empty] | 258.2625
| SAY | [5 empty] | 260
15mm cement plaster on rough side of single or half brick wall finished with a floating coat of neat cement of mix 1:5 ( 1 cement :5 fine sand)
| ICU BLOCK |  | 2 | 12.85 | 5.25 |  | 134.925
|  |  | 2 | 12.85 | 5.25 |  | 134.925
| sunshade top |  | 4 | 12.85 | 1.1 |  | 56.54
| total | [5 empty] | 326.39
| DEDUCT |  | 5 | 1.5 | 1.5 |  | 11.25
| total | [5 empty] | 315.14
| say | [5 empty] | 320
Extra for plastering on circular work not exceeding 6 m in radius:In two coats
| CURVING THE corner & COLUMN SIDE |  | 3*8 | 3.5 | 0.5 |  | 42
| SAY | [5 empty] | 45
Providing and applying plaster of paris putty of 2 mm thickness over plastered surface to prepare the surface even and smooth complete
| INSIDE OF OT-1,2 |  | 8 | 13 | 3.5 |  | 364
| CURVING THE COLUMN SIDE |  | 3*8 | 3.5 | 0.5 |  | 42
| INSIDE OF OT-3 |  | 4 | 6.5 | 3.5 |  | 91
| AUTO CLAVE ROOM |  | 2 | 9.5 | 3.5 |  | 66.5
| VENTLATO CLOSINGS |  | 30 | 1.5 | 0.6 |  | 27
| ABOVE LINTEL LEVEL OF HOLDING |  | 4 | 6.5 | 1 |  | 26
| PASSAGE |  | 4 | 3 | 1.5 |  | 18
|  |  | 2 | 28 | 1.5 |  | 84
| ceiling area | [5 empty] | 0
| ot 1,2 |  | 2 | 6 | 6 |  | 72
| ot 3 |  | 1 | 6 | 4.5 |  | 27
| autoclave |  | 1 | 6 | 3 |  | 18
| holding |  | 1 | 6 | 3 |  | 18
| main passage |  | 1 | 25 | 3 |  | 75
| icu area |  | 1 | 12.7 | 6 |  | 76.2
| neonatal icu |  | 1 | 6 | 4.5 |  | 27
| pediatric ward |  | 1 | 12.7 | 6 |  | 76.2
1107.9
| Total | [5 empty] | 1110
Applying one coat of water thinnable cement primer of approved brand and manufacture on wall surface :
| ICU BLOCK & pediatric |  | 2 | 12.75 | 12.75 |  | 325.125
| Say | [5 empty] | 330
Finishing with Epoxy paint (two or more coats) at all locations prepared and applied as per manufacturer's specifications including appropriate priming coat, preparation of surface, etc. complete.On concrete work
| INSIDE OF OT-1,2 |  | 8 | 13 | 3.5 |  | 364
| CURVING THE COLUMN SIDE |  | 3*8 | 3.5 | 0.5 |  | 42
| INSIDE OF OT-3 |  | 4 | 6.5 | 3.5 |  | 91
| AUTO CLAVE ROOM |  | 2 | 9.5 | 3.5 |  | 66.5
| VENTLATO CLOSINGS |  | 30 | 1.5 | 0.6 |  | 27
| HOLDING |  | 4 | 9.5 | 3.5 |  | 133
| PASSAGE |  | 4 | 3 | 1.5 |  | 18
|  |  | 2 | 28 | 1.5 |  | 84
| Total | [5 empty] | 825.5
| Say | [5 empty] | 830
Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade in two or more coats on new work, including finishing walls with Deluxe Multi surface paint system for interiors and exteriors using Primer as per manufacturers specifications: Two or more coats applied on walls @ 1.25 ltr/10 sqm over and including one coat of Special primer applied @ 0.75 ltr / 10 sqm
| quty from plastering | [5 empty] | 2320
| say | [5 empty] | 2320
Finishing walls with Acrylic Smooth exterior paint of required shade: —New work (Two or more coat applied @ 1.67 ltr/10 sqm over and including basecoat of water proofing cement paint applied @ 2.20 kg/ 10 sqm)
| quty from plastering | [5 empty] | 320
| say | [5 empty] | 320
Steel Work painting- Painting with synthetic enamel paint of approved brand and manufacture to give an even shade. Two or more coats on new work
| window grill painting |  | 12 | 1.5 | 1.5 |  | 27
|  |  | 2 | 0.65 | 0.65 |  | 0.845
| total |  | sqm |  |  |  | 27.845
| say | [5 empty] | 28
Providing and fixing factory made UPVC door frame of Rajashri or equivalent make made of UPVC extruded section having an overall dimension as. Below(tolerance+1mm) with wall thickness 2.0mm+/;0.2mm, corners of the door frame to be jointed with galvanized brackets and stainless steel screws, joint mitred plastic wilded. the hinge side vertical of the frames reinforced by galvanized M.S. tube of size 19x19mm and 1mm +/- 0.1mm wall thickness and 3 nos. stainless steel hinges fixed to the frame complete as per manufacturers specification and direction of Engineer-in-charge:Extruded section Profile size 42x50mm.
| ICU BLOCK |  | 2 | 5.1 |  |  | 10.2
|  |  | 4 | 5.1 |  |  | 20.4
| duct |  | 2 | 5.2 |  |  | 10.4
| total | [5 empty] | 41
| SAY | [5 empty] | 47
Providing and fixing to existing door frames.30mm thick factory made Rajashri or equivalent make Polyvinyl Chloride(PVC) door shutter and rails of a UPVC profile section of size 30mmx60mm and wall thickness 2mm+/-0.2mm with inbuilt decorative moulding edging on one side. The styles and rails with plastic brackets of size 75x220mm mitre and welded at the corners. The-stiles of the shutter reinforced by inserting galvanized M.S. tube of size 25x20mm and 1mm+/-0.1mm wall thickness. The lock rail made up of 'H' section, a UPVC profile section of size 30mmx100mm and 2mm+/-0.2mm wall thickness welded to the shutter style with a UPVC profile section single panel of size not less than 620mm,having overall thickness of 20mm and 1mm+/-0.1mm wall thickness with 20mm panel beading of suitable size, as per manufactures specification and direction of Engineer-in-charge.
| ICU BLOCK |  | 2 | 0.9 | 2.1 |  | 3.78
| duct |  | 2 | 1 | 1.2 |  | 2.4
| Total | [5 empty] | 6.18
| SAY | [5 empty] | 18
Providing and fixing 18mm thick gang saw cut mirror polished (premoulded and prepolished) machine cut for kitchen platforms, vanity counters, window sills, facias and similar locations of required size of approved shade, colour and texture laidover 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing moulding and polishing to edge to give high gloss finish etc. complete at all levels. Granite of any colour & Shade
| lift entry wall clading |  | 1 | 4 | 2.5 |  | 10
| OT 3 PLATFORM |  | 1 | 3 | 0.65 |  | 1.95
| COUNTER-ICU |  | 1 | 3 | 0.65 |  | 1.95
| COUNTER-F P O WARD |  | 1 | 3 | 0.65 |  | 1.95
| COUNTER-M P OWARD |  | 1 | 3 | 0.65 |  | 1.95
| TOTAL | [5 empty] | 17.8
| say | [5 empty] | 18
Providing edge moulding to 18mm thick marble stone counters, Vanities etc. including machine polishing to edge to give high gloss finish etc. complete as per design approved by Engineer-in-Charge.
| OT 3 PLATFORM |  | 2 | 3.7 |  |  | 7.4
| COUNTER-ICU |  | 2 | 3.7 |  |  | 7.4
| COUNTER-F P O WARD |  | 2 | 3.7 |  |  | 7.4
| COUNTER-M P OWARD |  | 2 | 3.7 |  |  | 7.4
| total | [5 empty] | 29.6
| say | [5 empty] | 30
| Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixed with rawl plugs and screws or with fixing clips, or with expansion hold fasteners including necessary filling up of gaps at junctions, at top, bottom and sides with required PVC/ neoprene felt etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing/panelling. C.P. brass/ stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing and panelling to be paid for separately): For fixed portion Anodised aluminium (anodised transparent or dyed required shade according to IS: 1868, Minimum anodic coating of grade AC 15) | [6 empty] | 35.4
DOORS -(
| 180*210 |  | 5 | 6.1 |  |  | 30.5
| @ 1.516kg/m | [5 empty] | 46.238
| 150*210 |  | 4 | 5.6 |  |  | 22.4
| 100*210 |  | 5 | 5.1 |  |  | 25.5
| total | [5 empty] | 47.9
| @ 1.372kg/m | [5 empty] | 65.7188
WINDOWS 150*150
| botttom |  | 12 | 1.5 | 18 | @ 1.042kg/m | 18.756
| top |  | 12 | 4.5 | 54 | @ .926kg/m | 50.004
| total | [5 empty] | 68.76
outer sections
| OT 3 PLATFORM |  | 1 | 14.95 |  |  | 14.95
| COUNTER-ICU |  | 1 | 16.15 |  |  | 16.15
| AUTO CLAVE ROOM |  | 1 | 16.15 |  |  | 16.15
| STERAIL STORE |  | 1 | 16.15 |  |  | 16.15
| COUNTER-F P O WARD |  | 1 | 16.15 |  |  | 16.15
| COUNTER-M P OWARD |  | 1 | 16.15 |  |  | 16.15
| total | [5 empty] | 95.7
| @ 1.777kg/m | [5 empty] | 170.0589
intermediate sections
| OT 3 PLATFORM |  | 1 | 11.3 |  |  | 11.3
| COUNTER-ICU |  | 1 | 18.85 |  |  | 18.85
| AUTO CLAVE ROOM |  | 1 | 16.15 |  |  | 16.15
| STERAIL STORE |  | 1 | 16.15 |  |  | 16.15
| COUNTER-F P O WARD |  | 1 | 18.85 |  |  | 18.85
| COUNTER-M P OWARD |  | 1 | 18.85 |  |  | 18.85
| Total | [5 empty] | 100.15
| @ 1.439kg/m | [5 empty] | 144.1158
| Total | [5 empty] | 494.8915
| say | [5 empty] | 500
For shutters of doors, windows & ventilators including providing and fixing hinges / pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately).Powder coated aluminium (minimum thickness of powder coating 50 micron
DOORS -
180*210
| vertical |  | 5 | 8.05 | 40.25 | @1.417kg/m | 57.0343
| lock |  | 5 | 1.55 | 7.75 | @ 1.497kg/m | 11.6018
| bottom |  | 5 | 1.55 | 7.75 | @ 2.172kg/m | 16.833
| top |  | 5 | 1.55 | 7.75 | @ 1.497kg/m | 11.6018
| clip |  | 5 | 38 | 190 | @ 0.124kg/m | 23.56
| c.angle |  | 5 | 1.5 | 7.5 | @0 .632kg/m | 4.74
| beading |  | 5 | 9 | 45 | @ 0.14kg/m | 6.3
150*210
| vertical |  | 4 | 8.05 | 32.2 | @1.1kg/m | 35.42
| lock |  | 4 | 1.25 | 5 | @ 0.904kg/m | 4.52
| bottom |  | 4 | 1.25 | 5 | @ 1.504kg/m | 7.52
| top |  | 4 | 1.25 | 5 | @ 0.904kg/m | 4.52
| clip |  | 4 | 24.5 | 98 | @ 0.124kg/m | 12.152
| c.angle |  | 4 | 1 | 4 | @0 .632kg/m | 2.528
| beading |  | 4 | 5.25 | 21 | @ 0.14kg/m | 2.94
100*210
| vertical |  | 5 | 4.5 | 22.5 | @1.1kg/m | 24.75
| lock |  | 5 | 0.85 | 4.25 | @ 0.904kg/m | 3.842
| bottom |  | 5 | 0.85 | 4.25 | @ 1.504kg/m | 6.392
| top |  | 5 | 0.85 | 4.25 | @ 0.904kg/m | 3.842
| clip |  | 5 | 14 | 70 | @ 0.124kg/m | 8.68
| c.angle |  | 5 | 0.75 | 3.75 | @0 .632kg/m | 2.37
| S.total | [5 empty] | 251.1468
windows
150*150
| lock |  | 12 | 6 | 72 | @ 0.492kg/m | 35.424
| side |  | 12 | 3 | 36 | @ 0.444kg/m | 15.984
| t&B |  | 12 | 3.12 | 37.44 | @ 0.362kg/m | 13.5533
| clip |  | 12 | 19 | 228 | @ 0.194kg/m | 44.232
| c.angle |  | 12 | 0.52 | 6.24 | @ 0.424kg/m | 2.6458
| beading |  | 12 | 12 | 144 | @ 0.12kg/m | 17.28
| S.total | [5 empty] | 129.119
for partioions
clip
outer sections
| OT 3 PLATFORM |  | 2 | 14.95 |  |  | 29.9
| COUNTER-ICU |  | 2 | 16.15 |  |  | 32.3
| AUTO CLAVE ROOM |  | 2 | 16.15 |  |  | 32.3
| STERAIL STORE |  | 2 | 16.15 |  |  | 32.3
| COUNTER-F P O WARD |  | 2 | 16.15
| COUNTER-M P OWARD |  | 2 | 16.15 |  |  | 32.3
intermediate sections
| OT 3 PLATFORM |  | 2 | 11.3 |  |  | 22.6
| COUNTER-ICU |  | 2 | 18.85
| AUTO CLAVE ROOM |  | 2 | 16.15 |  |  | 32.3
| STERAIL STORE |  | 2 | 16.15 |  |  | 32.3
| COUNTER-F P O WARD |  | 2 | 18.85 |  |  | 37.7
| COUNTER-M P OWARD |  | 2 | 18.85 |  |  | 37.7
| total | [5 empty] | 321.7
| @ 0.124kg/m | [5 empty] | 40.2125
| grand total | [5 empty] | 420.4783
| say | [5 empty] | 425
Providing and fixing 100mm brass locks (best make of approved quality) for aluminium doors including necessary cutting and making good etc. complete.
| total |  | 15 |  |  |  | 15
Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with PVC/neoprene gasket etc. complete as per the architectural drawings and directions of engineer-in-charge. (Cost of aluminium snap beading shall be paid in basic item): With OPAC glass panes of 6.0 mm thickness
door
| 180*210 |  | 8 | 1.8 | 2.1 |  | 30.24
Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with PVC/neoprene gasket etc. complete as per the architectural drawings and directions of engineer-in-charge. (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.0 mm thickness
door
| 150*210 |  | 8 | 1.1 | 0.75 |  | 6.6
| 100*210 |  | 5 | 1.1 | 1 |  | 5.5
| partitions |  | 8 | 3 | 1.3 |  | 31.2
|  |  | 4 | 1.5 | 1.3 |  | 7.8
| total | [5 empty] | 51.1
| say | [5 empty] | 55
Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with PVC/neoprene gasket etc. complete as per the architectural drawings and directions of engineer-in-charge. (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 4.0 mm thickness
| window glass |  | 12*3 | 0.5 | 1.5 |  | 27
| ventlator glass |  | 2 | 0.65 | 0.65 |  | 0.845
| total | [5 empty] | 27.845
| say | [5 empty] | 28
Providing and fixing12mm thick prelaminated particle board flat pressed three layer or graded wood particle board conforming to IS12823 Grade 1 type II, in panelling fixed in aluminium doors, windows shutters and partition frames with C.P brass/ stainless steel screws etc. complete as per architectural drawings and directions of engineer in charge Pre laminated particle board with decorative lamination on both sides
door
| 150*210 |  | 8 | 1 | 0.75 |  | 6
| 100*210 |  | 5 | 1 | 1 |  | 5
| partitions |  | 8 | 3 | 1.4 |  | 33.6
|  |  | 4 | 1.5 | 1.4 |  | 8.4
| Total | [5 empty] | 53
| say | [5 empty] | 55
Providing and fixing double action hydraulic floor spring of approved brand andmanufacture IS : 6315 marked, for doors including cost of cutting floors as required,embedding in floors and cover plates with brass pivot and single piece M.S. sheetouter box with slide plate etc. complete as per the direction of Engineer-in-chargse With stainless steel cover plate
| door 150*210 |  | 5*2 |  |  |  | 10
| door 150*210 |  | 4*2 |  |  |  | 8
| say | [5 empty] | 18
Providing and fixing IS : 3564 marked Aluminium die cast body tubular type universal hydraulic door closer with necessary accessories and screws etc. complete
| 100*210 |  | 5 |  |  |  | 5
| say | [5 empty] | 5
Providing nad fixing aluminium hanging floor door stopper ISImarked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparant or dyed to required colour and shade with necessary screws etc. complete. Single rubber stopper
| 100*210 |  | 5 |  |  |  | 5
| say | [5 empty] | 5
providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent od dyed to required colour or shade with necessary screws etc. complete: 250 x 10 mm
door
| 180*210 |  | 5*2 |  |  |  | 10
| 150*210 |  | 4*2 |  |  |  | 8
| 100*210 |  | 5 |  |  |  | 5
| total | [5 empty] | 23
| say | [5 empty] | 23
Providing and fixing window handles with necessary screws etc. complete-
| windows |  | 12*3 |  |  |  | 36
| ventilators |  | 3 |  |  |  | 3
| total | [5 empty] | 39
Providing and fixing white vitreous china pedestal type water closet (European type W.C. pan) with seat and lid, 10 litre low level white P.V.C. flushing cistern, including flush pipe, with manually controlled device (handle lever), conforming to IS : 7231, with all fittings and fixtures complete including cutting and making good the walls and floors wherever required :W.C. pan with ISI marked white solid plastic seat and lid
| IN ICU BLOCK |  | 2 |  |  |  | 2
Providing and fixing wash basin with C.I/ M.S brackets, 15mm C.P. brass pillar taps Kingston/ Gem/ Techno/ Parko, 32mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls and floors wherever require: White Vitreous China Wash basin size 550x400 mm with a pair of 15 mm C.P. brass pillar taps
| IN ICU BLOCK |  | 2 |  |  |  | 2
| Providing and fixing unplasticised PVC connection pipes with brass unions 30 cm length 15mm nominal bore |  | 5 |  |  |  | 5
| Providing and fixing waste pipe for sink, wash basin or urinals including PVC waste fittings complete:Semi Rigid Pipe-32mm diameter |  | 2 |  |  |  | 2
| Providing and fixing 600x450mm bevelled edge mirror 5mm thick of superior glass(of approved quality) complete with 6mm thick hard board ground fixed to wooden cleats with C.P.brass screws and washers complete. |  | 2 |  |  |  | 2
| Providing and fixing C.P towel rail complete with brackets fixed to wooden cleats with C.P.brass screws with conceiled fittings arrangement of approved quality ,size and make |  | 4 |  |  |  | 4
| Providing and fixing S.S soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements. Weighing not less than 106 gms. |  | 10 |  |  |  | 10
Providing and jointing PVC 63mm PVC pipes of (pressure 6 kg/cm2) for drainage line including testing of joints etc complete. (Sullage Down pipe) 63mm diameter (OD)
| new extension work |  | 1 | 30 |  |  | 30
| total | [5 empty] | 30
Providing and fixing unplasticised-P.V.C pipes clips of approved design to unplasticised-P.V.C rain water pipes by means of 50 x 50 x 50 mm hard wood plugs, screwed with M.S screws of required length including cutting brick work and fixing in cement mortar 1 : 4 (1 cement : 4 coarse sand) and making good the walls etc. complete 110mm
| total |  | 30 |  |  |  | 30
Providing and fixing on wall face unplasticised- Rigid PVC rain water pipes conforming to IS:13592 type A including jointing with seal ring conforming to IS:5382 leaving 10mm gap for thermal expansion (i) Single socketed pipes – 110mm diameter OD
| toilet line |  | 1 | 30 |  |  | 30
| Providing and fixing on wall face unplasticised - PVC moulded fittings/ accessories for unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion: Bend 87.5°. 110 mm bend |  | 3 |  |  |  | 3
| Providing and fixing on wall face unplasticised - PVC moulded fittings/ accessories for unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion. Single tee without door:110x110x110mm |  | 3 |  |  |  | 3
Providing and fixing wall face PVC pipe complete including cutting,chasing in walls and making good the walls etc complete.
| 25mm PVC pipe (10kg/sqcm) |  | 1 | 20 |  |  | 20
| Providing and fixing CP brass long body bib cock of approved quality confirming to IS standards weighing not less than 690gms 15mm nominal bore |  | 2 |  |  |  | 10
| Providing and fixing brass Bib cock of approved quality - 15mm nominal bore |  | 2 |  |  |  | 5
| Providing and fixing trap of self cleansing design with screwed down or hinged grating with or without vent arm complete, including cost of cutting and making good the walls and floors: 110mm inlet and 110mm outlet pvc |  | 6 |  |  |  | 6
| Providing and fixing PTMT (an Engineering thermo plastic ) grating of approved quality colour and make 150 mm nominal size square,100mm diameter of the inner hinged round grating. Rectangular type with circular round lid |  | 6 |  |  |  | 6
Providing and fixing at all height false ceiling of 12.5 mm thick tapered edge gypsum board conforming to IS : 2095/calcium silicate boards, including providing and fixing of frame work made of special sections power pressed from M.S. sheet and galvanised in accordance with zinc coating 600 as per IS : 277 and consisting of angle cleats of size 25mm wide x 1.6mm thick with flanges of 22mm and 37mm at 1200mm centre to centre one flange fixed to the ceiling with dash fastner 12.5mm diax40mm long with 6mm dia bolts to the angle hangers of 25x25x5mm of required length, and other end of angle hanger being fixed with nut and bolts to G.I. channels 45x15x0.9mm running at the rate of 1200mm centre to centre to which the ceiling section 0.5mm thick botton wedge of 80mm with tapered flanges of 26mm each having clips of 10.5mm at 450mm centre to centre shall be fixed in a direction perpendicular to G.I. channel with connecting clips made out of 2.64mm diax230mm long G.I. wire at every junction including fixing the gypsum board with ceiling section and perimeter channels 0.5mm thick 27mm and as per detail specification
Partition Gypsum board
| ot 1,2 |  | 2 | 6 | 6 |  | 72
| ot 3 |  | 1 | 6 | 4.5 |  | 27
| autoclave |  | 1 | 6 | 3 |  | 18
| holding |  | 1 | 6 | 3 |  | 18
| main passage |  | 1 | 25 | 3 |  | 75
| icu area |  | 1 | 12.7 | 6 |  | 76.2
| neonatal icu |  | 1 | 6 | 4.5 |  | 27
| pediatric ward |  | 1 | 12.7 | 6 |  | 76.2
| total | [5 empty] | 389.4
| say | [5 empty] | 800

## THIRD FLOOR (hidden)
Name of work : RENNOVATION OF GENERAL HOSPITAL AT KALPETTA IN WAYANAD DISTRICT
DETAILED ESTIMATE
S.N | Description | Unit | NO | Length | Width | Depth | Quantity
THIRD FLOOR
1 | Demolishing R.C.C. work manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per direction of Engineer - in- charge.
| DUMMY COLUMN |  | 16 | 0.6 | 0.3 | 1.5 | 4.32
| TOTAL | [5 empty] | 4.5
| Say | [5 empty] | 5
Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge
| MEDICAL MALE WARD DOOR &passage |  | 2 | 1.5 | 0.2 | 2.1 | 1.26
| lift door |  | 2 | 6.6 | 0.2 | 2.8 | 7.392
| passage |  | 1 | 3 | 0.2 | 1 | 0.6
| TOTAL | [5 empty] | 9.252
| say | [5 empty] | 10
Dismantling tile work in floors and roofs laid in cement mortar including stacking material within 50 metres lead.For thickness of tiles 10 mm to 25 mm
| baths in all wards |  | 4 | 2.5 | 0.15 |  | 1.5
| pediatric ward |  | 1 | 1.3 | 1.6 |  | 1.3
| total | [5 empty] | 2.8
| say | [5 empty] | 3
Dismantling doors, windows and clerestory windows (steel or wood) shutter including chowkhats, architrave, holdfasts etc. complete and stacking within 50 metres lead :Of area beyond 3 sq. metres
| passage |  | 1 | 3 | 3.5 |  | 10.5
| say | [5 empty] | 12
Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in :Cement mortar 1:4 (1 cement : 4 coarse sand
| PEDIATRIC WARD |  | 5 | 12.9 | 0.2 | 3.1 | 39.99
|  |  | 1 | 6.2 | 0.2 | 3.1 | 3.844
|  |  | 2 | 3.1 | 0.2 | 3.1 | 3.844
| PEDIATRIC WARD parapet wall |  | 2 | 12.85 | 0.2 | 0.8 | 4.112
|  |  | 2 | 12.85 | 0.2 | 0.8 | 4.112
| LIFT ROOM |  | 2 | 1.8 | 0.2 | 3.1 | 2.232
|  |  | 2 | 3.1 | 0.2 | 3.1 | 3.844
| head room |  | 2 | 5 | 0.2 | 2.8 | 5.6
|  |  | 2 | 3 | 0.2 | 2.8 | 3.36
| TOTAL | [5 empty] | 70.938
| deduction |  | 12 | 1.5 | 0.2 | 1.5 | 5.4
|  |  | 2 | 1.5 | 0.2 | 2.1 | 1.26
6.66
| Total after deduction | [5 empty] | 64.278
| SAY | [5 empty] | 65
Half brick masonry with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level.Cement mortar 1:4 (1 cement :4 coarse sand)
| TOILT IN PEDI..WARD |  | 3 | 3.2 | 3.45 |  | 33.12
|  |  | 1 | 1.5 | 3.45 |  | 5.175
| Add.. baths in all wards |  | 4 | 2.4 | 2.2 |  | 21.12
| COUNTER-PEDIATRIC WARDNEW |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| COUNTER-PEDIATRIC WARD |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| COUNTER-SURGICAL MALE WARD |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| COUNTER-MEDICAL MALE WARD |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| COUNTER-MEDICAL FEMALE WARD |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| Total | [5 empty] | 81.015
| SAY | [5 empty] | 82
Extra for providing and placing in position 2 Nos. 6mm dia. M.S. bars at every third course of half brick masonry
| TOILT IN PEDI..WARD |  | 3 | 3.2 | 3.45 |  | 33.12
|  |  | 1 | 1.5 | 3.45 |  | 5.175
| Add.. baths in all wards |  | 4 | 2.4 | 2.2 |  | 21.12
| COUNTER-PEDIATRIC WARDNEW |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| COUNTER-PEDIATRIC WARD |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| COUNTER-SURGICAL MALE WARD |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| COUNTER-MEDICAL MALE WARD |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| COUNTER-MEDICAL FEMALE WARD |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| Total | [5 empty] | 81.015
| SAY | [5 empty] | 82
Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering1:3:6 (1 Cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size).
| in ward toilet |  | 4 | 1.2 | 1 | 0.2 | 0.96
| pediatric ward toilet |  | 1 | 1.3 | 1.6 | 0.2 | 0.416
| Total | [5 empty] | 1.376
| SAY | [5 empty] | 1.5
Providing and laying water proofing treatment in sunken portion of WCs, bathroom etc., by applying cement slurry mixed with water proofing cement compound consisting of applying : (a) First layer of slurry of cement @ 0.488 kg/sqm mixed with water proofing cement compound @ 0.253 kg/sqm. This layer will be allowed to air cure for 4 hours (b) Second layer of slurry of cement @ 0.242 kg/sqm mixed with water proofing cement compound @ 0.126 kg/sqm. This layer will be allowed to air cure for 4 hours followed with water curing for 48 hours The rate includes preparation of surface, treatment and sealing of all joints,corners, junctions of pipes and masonry with polymer mixed slurry.
| TOILT IN PEDI..WARDs |  | 1 | 2.2 | 2 |  | 4.4
|  |  | 2 | 1.8 | 2.1 |  | 7.56
| total | [5 empty] | 11.96
| say | [5 empty] | 12
Reinforced cement concrete work in beams, suspended floors, roofs having slope upto 15degree, landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases upto floor V level including cost of centering, shuttering, finishing and excluding the cost of reinforcement in 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20mm nominal size)
| slab |  | 1 | 12.85 | 12.85 | 0.12 | 19.8147
| connection passage |  | 1 | 3 | 3 | 0.12 | 1.08
| connection passage- beam |  | 2 | 3 | 0.2 | 0.6 | 0.72
| beams |  | 3 | 12.85 | 0.2 | 0.6 | 4.626
|  |  | 5 | 12.85 | 0.2 | 0.6 | 7.71
|  |  | 2 | 6.5 | 0.2 | 0.45 | 1.17
| head room tank slab |  | 1 | 3.4 | 3.4 | 0.2 | 2.312
| head room tank beams |  | 5 | 3 | 0.2 | 0.6 | 1.8
| STAIR CASE HEAD ROOM SLAB |  | 1 | 4 | 6 | 0.12 | 2.88
| LIFT HEAD ROOM |  | 1 | 3.8 | 3.2 | 0.25 | 3.04
| beams |  | 2 | 3.2 | 0.2 | 0.6 | 0.768
|  |  | 2 | 3.8 | 0.2 | 0.6 | 0.912
| sunshade |  | 2 | 12.85 | 1.2 | 0.1 | 3.084
|  |  | 2 | 3 | 1.2 | 0.1 | 0.72
|  |  | 2 | 12.85 | 1.2 | 0.1 | 3.084
| lintel |  | 4 | 12.85 | 0.2 | 0.2 | 2.056
|  |  | 2 | 3 | 0.2 | 0.2 | 0.24
|  |  | 5 | 2 | 0.2 | 0.2 | 0.4
|  |  | 4 | 2.4 | 0.1 | 0.2 | 0.192
|  |  | 2 | 3 | 0.1 | 0.2 | 0.12
| stair case |  | 1 | 3 | 1.5 | 0.15 | 0.675
|  |  | 2 | 4.2 | 1 | 0.15 | 1.26
| steps |  | 25 | 1 | 0.15 | 0.15 | 0.5625
| counter |  | 5 | 4.5 | 0.7 | 0.08 | 1.26
| kerb in srair head room |  | 1 | 3 | 0.2 | 0.2 | 0.12
|  |  | 2 | 4.5 | 0.2 | 0.2 | 0.36
| Total | [5 empty] | 60.9662
deduction
| stair room |  | 1 | 4.5 | 3 | 0.12 | 1.62
|  |  | 1 | 4 | 6 | 0.12 | 2.88
| total deduction | [5 empty] | 4.5
| total after dediuction | [5 empty] | 56.4662
| Say | [5 empty] | 57
Reinforced cement concrete work in walls (any thickness) including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc upto floor V level including cost of centering, shuttering, finishing and excluding cost of reinforcement in 1:1.5:3 (1 cement: 1.5 coarse sand : 3 graded stone aggregate 20 mm nominal size)
| columns |  | 16 | 0.6 | 0.3 | 3.45 | 9.936
| tank column |  | 4 | 0.2 | 0.6 | 3 | 1.44
| tank column walls |  | 5 | 3 | 0.2 | 1.5 | 4.5
|  |  | 4 | 0.6 | 0.3 | 2.8 | 2.016
|  |  | 4 | 0.6 | 0.3 | 2.5 | 1.8
| Total | [5 empty] | 19.692
| Say | [5 empty] | 20
Reinforced cement concrete work in walls (any thickness) including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc upto floor V level including cost of centering, shuttering, finishing and excluding cost of reinforcement in 1:3:6 (1 cement: 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) For dummy columns
| DUMMY COLUMN |  | 12 | 1.5 | 0.6 | 0.3 | 3.24
| TOTAL | [5 empty] | 3.5
Reinforcement for RCC works including straightening, cutting, bending, placing in position and binding all complete. Thermo - Mechanically treated bars (Using Vizac, Tata or SAIL)
| total concrete qty. | [5 empty] | 80.5
| total |  | @ 140 kg / m3 |  |  |  | 11270
| say | [5 empty] | 11150
Providing and fixing M.S grills of required pattern in frames of windows etc with M.S.flats,square or round bars etc all complete:- Fixed to openings/wooden frames with rawl plugs screws etc
| window 150 x 150 |  | 12 | 1.5 | 1.5 |  | 27
|  |  | 3 | 0.65 | 0.65 |  | 1.2675
| total | [5 empty] | 28.2675
| total |  | @ 15 kg / sqm |  |  |  | 424.0125
| say | [5 empty] | 425
Providing and fixing stainless steel 12mm dia bar bent to shape with hooked ends in R.C.C. slabs during laying including, all as per standard design complete.
| fan points |  | 15 |  |  |  | 15
| say | [5 empty] | 15
Supplying and fixing 1.10m height hand rails for stair cases with 2 Nos. polished stainless steel tube of outer diameter 50mm at top and bottom with wall thickness not less than 1.60mm as per SS 304 vertical members of 50mm diameter pipe 1.00m length(approximately) welded together at 1.50m center to center and providing and fixing 2 nos 32 mm outer diameter stainless steel tube horizontally between the top and bottom tubes including fixing with steel nuts and bolts as per the direction of the Engineer – in – charge. Hand rails shall be fixed in the floor/steps with expansion hold fasters of required size including drilling etc. complete.
50mmØ ss.pips
| horizontal |  | 2 | 15 |  |  | 30
| vertical |  | 12 | 1.1 |  |  | 13.2
| Sub total | [5 empty] | 43.2
| 50mm Dia @1.822 kg/m | [5 empty] | 78.7104
| 32mmØ ss.pips |  | 2 | 15 |  |  | 30
| 32mm Dia @ 1.11 kg/m | [5 empty] | 33.3
| total | [5 empty] | 112.0104
| say | [5 empty] | 115
Providing and laying polished vitrified floor tiles of minimum size 600x600mm of thickness 10mm or nearest size of M/s. JOHNSON, KAJARIA, NITCO, SOMANY or equivalent in light colours and shades, with water absorption's less than 0.08% and conforming to IS:15622, laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand) including grouting the joints with cement and matching pigments etc, complete as directed by the Engineer-in-charge.
| PEDIATRIC WARD |  | 1 | 12.7 | 6.3 |  | 80.01
|  |  | 1 | 12.75 | 3.1 |  | 39.525
|  |  | 1 | 3 | 3.5 |  | 10.5
|  |  | 25 | 1.5 | 0.3 |  | 11.25
|  |  | 25 | 1.5 | 0.15 |  | 5.625
146.91
deduct
| TOILET AREA |  | 1 | 2.4 | 1.5 |  | 3.6
| TOTAL AFTER DEDUCTIONS | [5 empty] | 143.31
| Say | [5 empty] | 145
Providing and fixing Ist quality ceramic glazed wall tiles conforming to IS: 15622 of minimum 350x250 mm size and thickness 5MM of JOHNSON, NITCO, ORIENT, , KAJARIA ,or approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados,over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand)and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete
| PEDIATRIC WARD |  | 2 | 12.75 | 1.5 |  | 38.25
|  |  | 2 | 6.75 | 1.5 |  | 20.25
| connection passage |  | 2 | 4.5 | 1.5 |  | 13.5
| MAIN PASSAGE |  | 2 | 3.1 | 1.5 |  | 9.3
|  |  | 2 | 12.85 | 1.5 |  | 38.55
|  |  | 1 | 3.5 | 1.5 |  | 5.25
|  |  | 2 | 2.5 | 1.5 |  | 7.5
|  |  | 2 | 3 | 1.5 |  | 9
| inside of tank |  | 6 | 3 | 1.5 |  | 27
|  |  | 1 | 3 | 3 |  | 9
| TOILET |  | 4 | 1.2 | 1.5 |  | 7.2
|  |  | 4 | 1.5 | 1.5 |  | 9
|  |  | 2 | 1.5 | 1.5 |  | 4.5
|  |  | 2 | 2.5 | 1.5 |  | 7.5
| PEDIATRIC WARD OLD TOILET |  | 2 | 1.2 | 1.5 |  | 3.6
|  |  | 2 | 1.5 | 1.5 |  | 4.5
| NEW BATHS IN ALL WARDS |  | 4*2 | 2.4 | 1.5 |  | 28.8
| counters |  | 5 | 3 | 0.8 |  | 19.2
261.9
deduct
| windows |  | 8 | 1.5 | 0.3 |  | 3.6
| door |  | 2 | 1.5 | 1.5 |  | 4.5
| door |  | 1 | 1.2 | 1.5 |  | 1.8
| total | [5 empty] | 9.9
| TOTAL AFTER DEDUCTIONS | [5 empty] | 252
| SAY | [5 empty] | 255
Providing and laying anti skid ceramic floor tiles of minimum 400x400 mm size for toilets (7.5mm thickness or nearest size) M/s. JOHNSON, KAJARIA, NITCO, SOMANY or equivalent of 1st quality conforming to IS: 15622 of approved make in all colours, shades, except white, ivory, grey, fume red brown laid on 20mm thick bed of cement mortar 1:4 (1 cement : 4 coarse sand) including pointing the joints with white cement and matching pigments etc complete.
| PEDIATRIC WARD |  | 3 | 1.2 | 1.5 |  | 5.4
| IWC IN ALL WARDS |  | 4 | 1.2 | 1.5 |  | 7.2
| TOTAL | [5 empty] | 12.6
| SAY | [5 empty] | 13
12mm cement plaster on rough side of single or half brick wall finished with a floating coat of neat cement of mix 1:4 ( 1 cement : 4 fine sand)
| PEDIATRIC WARD |  | 2 | 12.75 | 1.5 |  | 38.25
|  |  | 2 | 6.75 | 1.5 |  | 20.25
| MAIN PASSAGE |  | 2 | 3.1 | 1.5 |  | 9.3
|  |  | 2 | 12.85 | 1.5 |  | 38.55
|  |  | 1 | 3.5 | 1.5 |  | 5.25
|  |  | 2 | 2.5 | 1.5 |  | 7.5
|  |  | 2 | 3 | 1.5 |  | 9
| LIFT IN SIDE |  | 4 | 1.8 | 3.55 |  | 25.56
|  |  | 4 | 3 | 3.55 |  | 42.6
| TOILET |  | 4 | 1.2 | 1.5 |  | 7.2
|  |  | 4 | 1.5 | 1.5 |  | 9
|  |  | 2 | 1.5 | 1.5 |  | 4.5
|  |  | 2 | 2.5 | 1.5 |  | 7.5
| PEDIATRIC WARD OLD TOILET |  | 2 | 1.2 | 1.5 |  | 3.6
|  |  | 2 | 1.5 | 1.5 |  | 4.5
| NEW BATHS IN ALL WARDS |  | 4*2 | 2.4 | 1.5 |  | 28.8
counters
| COUNTER-PEDIATRIC WARDNEW |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| COUNTER-PEDIATRIC WARD |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| COUNTER-SURGICAL MALE WARD |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| COUNTER-MEDICAL MALE WARD |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| COUNTER-MEDICAL FEMALE WARD |  | 1 | 3 | 0.8 |  | 2.4
|  |  | 4 | 0.6 | 0.8 |  | 1.92
| terrace plastering |  | 1 | 12.85 | 12.85 |  | 165.1225
448.0825
deduct
| door |  | 2 | 1.5 | 1.5 |  | 4.5
| door |  | 1 | 1.2 | 1.5 |  | 1.8
| total | [5 empty] | 6.3
| TOTAL AFTER DEDUCTIONS | [5 empty] | 441.7825
| SAY | [5 empty] | 450
6mm cement plaster to ceiling of mix 1 : 3 (1 cement : 3 fine sand )
| PEDIATRIC WARD |  | 1 | 12.75 | 12.75 |  | 162.5625
| SUNSHADE BOTTOM |  | 2 | 13 | 1.1 |  | 28.6
|  |  | 2 | 13 | 1.1 |  | 28.6
| tank bottom |  | 1 | 3.4 | 3.4 |  | 11.56
| STAIR BOTTOM |  | 1 | 3 | 1.5 |  | 4.5
|  |  | 2 | 5.5 | 1.5 |  | 16.5
|  |  | 2 | 5.5 | 0.5 |  | 5.5
| counter slab bottom |  | 5 | 3 | 0.8 |  | 12
| TOTAL | [5 empty] | 269.8225
| SAY | [5 empty] | 270
15mm cement plaster on rough side of single or half brick wall finished with a floating coat of neat cement of mix 1:5 ( 1 cement :5 fine sand)
| NEW PEDIATRIC WARD |  | 2 | 12.85 | 5.25 |  | 134.925
|  |  | 2 | 12.85 | 5.25 |  | 134.925
| tank out side area |  | 4 | 3.4 | 3.4 |  | 46.24
| sunshade top |  | 4 | 12.85 | 1.1 |  | 56.54
| STAIR HEAD ROOM |  | 2 | 3.2 | 2.8 |  | 17.92
|  |  | 2 | 6.5 | 2.8 |  | 36.4
| LIFT HEAD ROOM |  | 2 | 3.2 | 2.5 |  | 16
|  |  | 2 | 3.6 | 2.5 |  | 18
| total | [5 empty] | 460.95
| DEDUCT |  | 5 | 1.5 | 1.5 |  | 11.25
449.7
| say | [5 empty] | 450
Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade in two or more coats on new work, including finishing walls with Deluxe Multi surface paint system for interiors and exteriors using Primer as per manufacturers specifications: Two or more coats applied on walls @ 1.25 ltr/10 sqm over and including one coat of Special primer applied @ 0.75 ltr / 10 sqm
| quty from plastering | [5 empty] | 720
| say | [5 empty] | 720
Finishing walls with Acrylic Smooth exterior paint of required shade: —New work (Two or more coat applied @ 1.67 ltr/10 sqm over and including basecoat of water proofing cement paint applied @ 2.20 kg/ 10 sqm)
| quty from plastering | [5 empty] | 450
| say | [5 empty] | 450
Steel Work painting- Painting with synthetic enamel paint of approved brand and manufacture to give an even shade. Two or more coats on new work
| window grill painting |  | 12 | 1.5 | 1.5 |  | 27
|  |  | 3 | 0.65 | 0.65 |  | 1.2675
| total |  | sqm |  |  |  | 28.2675
| say | [5 empty] | 30
Extra for providing and mixing water proofing material in cement plaster work in proportion recommended by the manufacturers.
| terrace plastering |  | 1 | 12.85 | 12.85 |  | 165.1225
| for tank slab |  | 1 | 4.8 | 2.9 |  | 13.92
| for tank wall |  | 2 | 4.8 | 1.5 |  | 14.4
|  |  | 2 | 2.9 | 1.5 |  | 8.7
| total | [5 empty] | 202.1425
| @ 5.4 kg/ sqm | [5 empty] | 21.8314
| Say | [5 empty] | 22 bags
Providing and fixing factory made UPVC door frame of Rajashri or equivalent make made of UPVC extruded section having an overall dimension as. Below(tolerance+1mm) with wall thickness 2.0mm+/;0.2mm, corners of the door frame to be jointed with galvanized brackets and stainless steel screws, joint mitred plastic wilded. the hinge side vertical of the frames reinforced by galvanized M.S. tube of size 19x19mm and 1mm +/- 0.1mm wall thickness and 3 nos. stainless steel hinges fixed to the frame complete as per manufacturers specification and direction of Engineer-in-charge:Extruded section Profile size 42x50mm.
| PEDIATRIC WARD |  | 3 | 5.1 |  |  | 15.3
|  |  | 4 | 5.1 |  |  | 20.4
| duct |  | 2 | 5.2 |  |  | 10.4
| total | [5 empty] | 46.1
| SAY | [5 empty] | 47
Providing and fixing to existing door frames.30mm thick factory made Rajashri or equivalent make Polyvinyl Chloride(PVC) door shutter and rails of a UPVC profile section of size 30mmx60mm and wall thickness 2mm+/-0.2mm with inbuilt decorative moulding edging on one side. The styles and rails with plastic brackets of size 75x220mm mitre and welded at the corners. The-stiles of the shutter reinforced by inserting galvanized M.S. tube of size 25x20mm and 1mm+/-0.1mm wall thickness. The lock rail made up of 'H' section, a UPVC profile section of size 30mmx100mm and 2mm+/-0.2mm wall thickness welded to the shutter style with a UPVC profile section single panel of size not less than 620mm,having overall thickness of 20mm and 1mm+/-0.1mm wall thickness with 20mm panel beading of suitable size, as per manufactures specification and direction of Engineer-in-charge.
| PEDIATRIC WARD |  | 3 | 0.9 | 2.1 |  | 5.67
| ALL BATH AND ONE TOILET |  | 4 | 0.9 | 2.1 |  | 7.56
| duct |  | 2 | 1 | 2.1 |  | 4.2
| Total | [5 empty] | 17.43
| SAY | [5 empty] | 18
Providing and fixing 18mm thick gang saw cut mirror polished (premoulded and prepolished) machine cut for kitchen platforms, vanity counters, window sills, facias and similar locations of required size of approved shade, colour and texture laidover 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing moulding and polishing to edge to give high gloss finish etc. complete at all levels. Granite of any colour & Shade
| lift entry wall clading |  | 1 | 4 | 2.5 |  | 10
| COUNTER-PEDIATRIC WARDNEW |  | 1 | 3 | 0.65 |  | 1.95
| COUNTER-PEDIATRIC WARD |  | 1 | 3 | 0.65 |  | 1.95
| COUNTER-SURGICAL MALE WARD |  | 1 | 3 | 0.65 |  | 1.95
| COUNTER-MEDICAL MALE WARD |  | 1 | 3 | 0.65 |  | 1.95
| COUNTER-MEDICAL FEMALE WARD |  | 1 | 3 | 0.65 |  | 1.95
| total | [5 empty] | 19.75
| say | [5 empty] | 20
Providing edge moulding to 18mm thick marble stone counters, Vanities etc. including machine polishing to edge to give high gloss finish etc. complete as per design approved by Engineer-in-Charge.
| COUNTER-PEDIATRIC WARDNEW |  | 2 | 3.7 |  |  | 7.4
| COUNTER-PEDIATRIC WARD |  | 2 | 3.7 |  |  | 7.4
| COUNTER-SURGICAL MALE WARD |  | 2 | 3.7 |  |  | 7.4
| COUNTER-MEDICAL MALE WARD |  | 2 | 3.7 |  |  | 7.4
| COUNTER-MEDICAL FEMALE WARD |  | 2 | 3.7 |  |  | 7.4
| total | [5 empty] | 37
| say | [5 empty] | 38
| Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixed with rawl plugs and screws or with fixing clips, or with expansion hold fasteners including necessary filling up of gaps at junctions, at top, bottom and sides with required PVC/ neoprene felt etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing/panelling. C.P. brass/ stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing and panelling to be paid for separately): For fixed portion Anodised aluminium (anodised transparent or dyed required shade according to IS: 1868, Minimum anodic coating of grade AC 15) | [6 empty] | 35.4
DOORS -(
| 150*210 |  | 3 | 5.6 |  |  | 16.8
| 100*210 |  | 7 | 5.1 |  |  | 35.7
| total | [5 empty] | 52.5
| @ 1.372kg/m | [5 empty] | 72.03
150*150 + elec room
| botttom |  | 14 | 1.5 | 21 | @ 1.042kg/m | 21.882
| top |  | 14 | 4.5 | 63 | @ .926kg/m | 58.338
| total | [5 empty] | 80.22
outer sections
| COUNTER-PEDIATRIC WARDNEW |  | 1 | 14.95 |  |  | 14.95
| COUNTER-PEDIATRIC WARD |  | 1 | 16.15 |  |  | 16.15
| COUNTER-SURGICAL MALE WARD |  | 1 | 16.15 |  |  | 16.15
| COUNTER-MEDICAL MALE WARD |  | 1 | 16.15 |  |  | 16.15
| COUNTER-MEDICAL FEMALE WARD |  | 1 | 16.15 |  |  | 16.15
| total | [5 empty] | 79.55
| @ 1.777kg/m | [5 empty] | 141.3603
intermediate sections
| COUNTER-PEDIATRIC WARDNEW |  | 1 | 11.3 |  |  | 11.3
| COUNTER-PEDIATRIC WARD |  | 1 | 18.85 |  |  | 18.85
| COUNTER-SURGICAL MALE WARD |  | 1 | 18.85 |  |  | 18.85
| COUNTER-MEDICAL MALE WARD |  | 1 | 18.85 |  |  | 18.85
| COUNTER-MEDICAL FEMALE WARD |  | 1 | 18.85 |  |  | 18.85
| Total | [5 empty] | 86.7
| @ 1.439kg/m | [5 empty] | 124.7613
| Total | [5 empty] | 418.3716
| say | [5 empty] | 420
For shutters of doors, windows & ventilators including providing and fixing hinges / pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately).Powder coated aluminium (minimum thickness of powder coating 50 micron
DOORS -
150*210
| vertical |  | 3 | 8.05 | 24.15 | @1.1kg/m | 26.565
| lock |  | 3 | 1.25 | 3.75 | @ 0.904kg/m | 3.39
| bottom |  | 3 | 1.25 | 3.75 | @ 1.504kg/m | 5.64
| top |  | 3 | 1.25 | 3.75 | @ 0.904kg/m | 3.39
| clip |  | 3 | 24.5 | 73.5 | @ 0.124kg/m | 9.114
| c.angle |  | 3 | 1 | 3 | @0 .632kg/m | 1.896
| beading |  | 3 | 5.25 | 15.75 | @ 0.14kg/m | 2.205
100*210
| vertical |  | 7 | 4.5 | 31.5 | @1.1kg/m | 34.65
| lock |  | 7 | 0.85 | 5.95 | @ 0.904kg/m | 5.3788
| bottom |  | 7 | 0.85 | 5.95 | @ 1.504kg/m | 8.9488
| top |  | 7 | 0.85 | 5.95 | @ 0.904kg/m | 5.3788
| clip |  | 7 | 14 | 98 | @ 0.124kg/m | 12.152
| c.angle |  | 7 | 0.75 | 5.25 | @0 .632kg/m | 3.318
| S.total | [5 empty] | 122.0264
windows
150*150 + elec room
| lock |  | 14 | 6 | 84 | @ 0.492kg/m | 41.328
| side |  | 14 | 3 | 42 | @ 0.444kg/m | 18.648
| t&B |  | 14 | 3.12 | 43.68 | @ 0.362kg/m | 15.8122
| clip |  | 14 | 19 | 266 | @ 0.194kg/m | 51.604
| c.angle |  | 14 | 0.52 | 7.28 | @ 0.424kg/m | 3.0867
| beading |  | 14 | 12 | 168 | @ 0.12kg/m | 20.16
| S.total | [5 empty] | 150.6389
for partioions
clip
outer sections
| COUNTER-PEDIATRIC WARDNEW |  | 2 | 14.95 |  |  | 29.9
| COUNTER-PEDIATRIC WARD |  | 2 | 16.15 |  |  | 32.3
| COUNTER-SURGICAL MALE WARD |  | 2 | 16.15 |  |  | 32.3
| COUNTER-MEDICAL MALE WARD |  | 2 | 16.15 |  |  | 32.3
| COUNTER-MEDICAL FEMALE WARD |  | 2 | 16.15 |  |  | 32.3
intermediate sections
| COUNTER-PEDIATRIC WARDNEW |  | 2 | 11.3 |  |  | 22.6
| COUNTER-PEDIATRIC WARD |  | 2 | 18.85 |  |  | 37.7
| COUNTER-SURGICAL MALE WARD |  | 2 | 18.85 |  |  | 37.7
| COUNTER-MEDICAL MALE WARD |  | 2 | 18.85 |  |  | 37.7
| COUNTER-MEDICAL FEMALE WARD |  | 2 | 18.85 |  |  | 37.7
| total | [5 empty] | 332.5
| @ 0.124kg/m | [5 empty] | 41.5625
| grand total | [5 empty] | 314.2278
| say | [5 empty] | 315
Providing and fixing 100mm brass locks (best make of approved quality) for aluminium doors including necessary cutting and making good etc. complete.
| total |  | 10 |  |  |  | 10
Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with PVC/neoprene gasket etc. complete as per the architectural drawings and directions of engineer-in-charge. (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.0 mm thickness
door
| 150*210 |  | 3*2 | 1.1 | 0.75 |  | 4.95
| 100*210 |  | 7 | 1.1 | 1 |  | 7.7
| partitions |  | 5 | 3 | 1.3 |  | 19.5
|  |  | 4 | 1.5 | 1.3 |  | 7.8
| total | [5 empty] | 39.95
| say | [5 empty] | 40
Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with PVC/neoprene gasket etc. complete as per the architectural drawings and directions of engineer-in-charge. (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 4.0 mm thickness
| window glass |  | 14*3 | 0.5 | 1.5 |  | 31.5
| ventlator glass |  | 3 | 0.65 | 0.65 |  | 1.2675
| total | [5 empty] | 32.7675
| say | [5 empty] | 33
Providing and fixing12mm thick prelaminated particle board flat pressed three layer or graded wood particle board conforming to IS12823 Grade 1 type II, in panelling fixed in aluminium doors, windows shutters and partition frames with C.P brass/ stainless steel screws etc. complete as per architectural drawings and directions of engineer in charge Pre laminated particle board with decorative lamination on both sides
door
| 150*210 |  | 3*2 | 1 | 1 |  | 6
| 100*210 |  | 7 | 1 | 1 |  | 7
| partitions |  | 5 | 3 | 1.4 |  | 21
|  |  | 4 | 1.5 | 1.4 |  | 8.4
| Total | [5 empty] | 42.4
| say | [5 empty] | 43
Providing and fixing double action hydraulic floor spring of approved brand andmanufacture IS : 6315 marked, for doors including cost of cutting floors as required,embedding in floors and cover plates with brass pivot and single piece M.S. sheetouter box with slide plate etc. complete as per the direction of Engineer-in-chargse With stainless steel cover plate
| door 150*210 |  | 3*2 |  |  |  | 6
| say | [5 empty] | 6
Providing and fixing IS : 3564 marked Aluminium die cast body tubular type universal hydraulic door closer with necessary accessories and screws etc. complete
| 100*210 |  | 7 |  |  |  | 7
| say | [5 empty] | 7
Providing nad fixing aluminium hanging floor door stopper ISImarked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparant or dyed to required colour and shade with necessary screws etc. complete. Single rubber stopper
| 100*210 |  | 7 |  |  |  | 7
| say | [5 empty] | 7
providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent od dyed to required colour or shade with necessary screws etc. complete: 250 x 10 mm
door
| 150*210 |  | 3*2 |  |  |  | 6
| 100*210 |  | 7 |  |  |  | 7
| total | [5 empty] | 13
| say | [5 empty] | 13
Providing and fixing window handles with necessary screws etc. complete-
| windows |  | 14*3 |  |  |  | 42
| ventilators |  | 3 |  |  |  | 3
| total | [5 empty] | 45
Providing and fixing water closet squatting pan (Indian type W.C. pan ) with 100mm sand cast Iron P or S trap, 10 litre low level white P.V.C. flushing cistern, including flush pipe, with manually controlled device (handle lever) conforming to IS : 7231, with all fittings and fixtures complete including cutting and making good the walls and floors wherever required :White Vitreous china Orissa pattern W.C. pan of size 580x440mm with integral type foot rests.
| in ward toilets |  | 4 |  |  |  | 4
Providing and fixing white vitreous china pedestal type water closet (European type W.C. pan) with seat and lid, 10 litre low level white P.V.C. flushing cistern, including flush pipe, with manually controlled device (handle lever), conforming to IS : 7231, with all fittings and fixtures complete including cutting and making good the walls and floors wherever required :W.C. pan with ISI marked white solid plastic seat and lid
| in pediatric ward |  | 3 |  |  |  | 3
Providing and fixing wash basin with C.I/ M.S brackets, 15mm C.P. brass pillar taps Kingston/ Gem/ Techno/ Parko, 32mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls and floors wherever require: White Vitreous China Wash basin size 550x400 mm with a pair of 15 mm C.P. brass pillar taps
| pediatric ward &wards |  | 4 |  |  |  | 4
| Providing and fixing unplasticised PVC connection pipes with brass unions 30 cm length 15mm nominal bore |  | 4 |  |  |  | 4
| Providing and fixing waste pipe for sink, wash basin or urinals including PVC waste fittings complete:Semi Rigid Pipe-32mm diameter |  | 4 |  |  |  | 4
| Providing and fixing 600x450mm bevelled edge mirror 5mm thick of superior glass(of approved quality) complete with 6mm thick hard board ground fixed to wooden cleats with C.P.brass screws and washers complete. |  | 15 |  |  |  | 15
| Providing and fixing C.P towel rail complete with brackets fixed to wooden cleats with C.P.brass screws with conceiled fittings arrangement of approved quality ,size and make |  | 6 |  |  |  | 6
| Providing and fixing S.S soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements. Weighing not less than 106 gms. |  |  | 15 |  |  | 15
Providing and jointing PVC 63mm PVC pipes of (pressure 6 kg/cm2) for drainage line including testing of joints etc complete. (Sullage Down pipe) 63mm diameter (OD)
| new extension work |  |  | 120
total
Providing and fixing unplasticised-P.V.C pipes clips of approved design to unplasticised-P.V.C rain water pipes by means of 50 x 50 x 50 mm hard wood plugs, screwed with M.S screws of required length including cutting brick work and fixing in cement mortar 1 : 4 (1 cement : 4 coarse sand) and making good the walls etc. complete 110mm
| total |  |  | 60 |  |  | 60
Providing and fixing on wall face unplasticised- Rigid PVC rain water pipes conforming to IS:13592 type A including jointing with seal ring conforming to IS:5382 leaving 10mm gap for thermal expansion (i) Single socketed pipes – 110mm diameter OD
| toilet line |  | 1 | 125 |  |  | 125
| Providing and fixing on wall face unplasticised - PVC moulded fittings/ accessories for unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion: Bend 87.5°. 110 mm bend |  | 25 |  |  |  | 25
| Providing and fixing on wall face unplasticised - PVC moulded fittings/ accessories for unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A, including jointing with seal ring conforming to IS : 5382, leaving 10 mm gap for thermal expansion. Single tee without door:110x110x110mm |  | 12 |  |  |  | 12
Providing and fixing wall face PVC pipe complete including cutting,chasing in walls and making good the walls etc complete.
| 25mm PVC pipe (10kg/sqcm) |  | 1 | 110 |  |  | 110
| 32mm PVC pipe 1(10kg/sqcm) |  | 1 | 125 |  |  | 125
| 50mm PVC pipe (10kg/sqcm) |  | 1 | 250 |  |  | 250
| Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings i/c fixing the pipe with clamps at 1m spacing. This includes jointing of pipes and fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per derection of Engineer in Charge. a. Concealed work including cutting chases and making good the walls 20mm |  | 1 | 75 |  |  | 75
| Providing and fixing CP brass long body bib cock of approved quality confirming to IS standards weighing not less than 690gms 15mm nominal bore |  | 10 |  |  |  | 10
| Providing and fixing brass Bib cock of approved quality - 15mm nominal bore |  | 5 |  |  |  | 5
Providing and fixing gun metal gate valve with CI wheel of approved quality(screwed end) –
| 25mm nominal bore |  | 4 |  |  |  | 4
| 50mm nominal bore |  | 2 |  |  |  | 2
| Providing and fixing C.P. brass shower rose with 15 to 20 mm inlet 100mm diameter |  | 5 |  |  |  | 5
| Providing and fixing C.P brass stop cock (concealed) of standard design of approved make conforming to IS 8931. conforming to IS standards 15 mm nominal bore |  | 5 |  |  |  | 5
| Providing and fixing trap of self cleansing design with screwed down or hinged grating with or without vent arm complete, including cost of cutting and making good the walls and floors: 110mm inlet and 110mm outlet pvc |  | 4 |  |  |  | 4
| Providing and fixing PTMT (an Engineering thermo plastic ) grating of approved quality colour and make 150 mm nominal size square,100mm diameter of the inner hinged round grating. Rectangular type with circular round lid |  | 4 |  |  |  | 4
| Supplying & Erecting pump set of suitable capacity coupled to a electric motor to run on 3 phase electric supply capable of discharging of 7 LPS against a total head of 20m including starter with bronze impeller, stainless steel shaft etc incl. cost of panel Board, voltmeter, ameter etc. |  | 1no |  |  |  | 1no
| Providing and placing on terrace (at all floor levels) poly ethlyne water storage tank ISI: 12701 marked with cover and suitable locking arrangement and making necessary holes for inlet, outlet and over flow pipes but with out fittings and the base support for tank |  | 2000 |  |  |  | 2000