## Fire Alarm & Fighting System
NAME OF WORK-:FIRE PROTECTION SYSTEM, NEW CANTEEN CUM STORAGE BUILDING, HLL LIFE CARE LTD
PART-A :Fire Alarm System
Sl.NO | Item Description | Unit | Qty | Rate (Rs. In words & Figures) | Amount (Rs.)
1 | Supply , Installation , Testing and Commissioining of Addressable standalone Fire Alarm Control panel,Addressable standalone 2 loop Fire Alarm Control,Maximum 636 addressable Points,1 Loop card (FLFSLC2)inbuild which has 318 addressable points(159 detectors and 159 devices),Requires 2nd loop card FLFSLC2 additionally for expansion,Easy mount chassis,Integral 80-character LCD display with backlighting,History file with 1,000-event capacity,Maintenance alert warns when smoke detector dust accumulation is excessive,Automatic device type-code verification,System alarm verification selection per detector point,UL Listed,FM Approved | Nos | 1
2 | Supply , Installation , Testing and Commissioining of Addressable Low-Profile Photoelectric Smoke Detector; includes B501 base,Sleek,low-profile design, Removable cover and insect-resistant screen for simple field cleaning, Built-in tamper-resistant feature,UL Listed(UB-5,Grnd-13,1st-4th-12,LB-12) | Nos | 42
3 | Supply , Installation , Testing and Commissioining of Addressable Heat Detector; includes B501 base,Factory preset at 135°F (57°C),Sleek, low-profile, stylish design,St a te-of-the-art thermistor technology for fast response,Bu i lt-in tamper resistant feature.UL Listed (UB- 7 nos,Ground- 1 no) | Nos | 8
4 | Supply , Installation , Testing and Commissioining of Addressable Manual call point,Unique 'Plug & Play' installation concept, Re-settable operating element option, Semi-Flush or surface Mounting, Backward compatibility,Enhanced aesthetics,UL Listed (one on each floor- 4 for 4 floors) | Nos | 4
5 | Supply , Installation , Testing and Commissioining of Addressable Wall Mount Horn/Strobe, 12/24V, Red, Multi-Candela 15,15/75, 30, 75,110,115 cd, Plain (No Lettering),UL Listed (four on each floor-16 for 4 floors) | Nos | 16
6 | Supply , Installation , Testing and Commissioining of 12 VDC and 5 Amp SMPS power Supply for Hooter | Nos | 1
7 | Supply , Installation , Testing and Commissioining of 2 core 1sqmm FRLS armoured cables with required accessories | Mtrs | 800
8 | Supply and fixing of Water type Fire Extinguisher 9 litres on wall with hook plate and anchor fastening of ISI marked with internal plastic lining and solid drawn body with 60 grams CO2 cartridge with gun metal plunger and 1.0 M long discharge hose confirming to IS 940 and complete in all respects including initial fill with CO2. | Nos | 16
9 | Supply & fixing of of Carbon-dioxide extinguisher on wall of ISI marked 4.5 Kg capacity made of high pressure seamless steel cylinder (CCE marked ) confirming to IS 2878, 8149. complete with wheel type valve with one meter long braided high pressure discharge hose complete in all respects including initial fill with CO2 gas. | Nos | 8
PART-B; Sprinkler & Hydrant System
Supply, Installation,Testing Commissioning of Automatic Sprinkler System and hydrant system comprising of following:
10 | Medium, ‘B’ class G. I. pipes IS 1239 with screwed or welded joints, including all fittings, MS supports, cutting the pipes to correct length jointing with G.I threaded fitting, fixing with clamps to M.S. brackets / hangers including testing to 15 kgs/cm2
All fittings 50 NB and bellow shall be hot dipped socket weld/screwed 3000 psi and fittings above 65 NB shall be hot dipped butt weld
a | 150mmdia ISI | Mtrs | 80
b | 80mm dia ISI | Mtrs | 40
c | 65mm dia ISI | Mtrs | 190
d | 50 mm dia ISI | Mtrs | 72
e | 40mm dia ISI | Mtrs | 72
f | 32mm dia ISI | Mtrs | 120
g | 25mm dia ISI | Mtrs | 570
11 | Supply Installation testing & comissioning of Pendant type sprinkler of 15 NB, Quartzoid bulb type 68 deg.with K 80, and adjustable escutcheon plate (UB - 28 nos,Ground - 31 nos,1s floor - 28 , LB- 31 nos) | Nos | 118
12 | Supply, Installation,Testing Commissioning of Sprinkler Flexible drop pipe(UL Iisted ) to with stand 16 Bar pressure with welded reducer on one end to directly accomadate sprinkler & female checknut on the other end to connect to the branch pipe with supports complete
a | 1000 mm long ( 1/2" ) | Nos | 118
b | 1500 mm Long (1/2") | Nos | 1
13 | Supply, Installation,Testing Commissioning of Cast iron Butterfly valve pressure rating PN 16 kg/sqcm standard pattern (Horizontal / Vertical),with necessary flanged joints by providing necessary pair of M.S. flanges, nuts, bolts, gaskets, etc. all complete for following diameters
a | 65 NB | Nos | 7
b | 150 NB (For Main Buiding Pipe) | Nos | 1
14 | Supply, Installation,Testing Commissioning of Flow Switch pedal type
a | 25 NB | Nos | 7
15 | Supply, Installation,Testing Commissioning of 150 mm dial 0-20 KG/Sq cm Pressure Guage | Nos | 7
16 | Supply, Installation,Testing Commissioning of 65 mm dia Drain Valve | Nos | 7
17 | Supplying and fixing, testing & commissioning of double flanged sluice valve of rating PN 1.6 with non rising spindle, with hand wheel for AG applications, bronze/gun metal seat ISI marked complete with nuts, bolts, washers, gaskets, conforming to IS 780 of following sizes as required.
a | 150 mm | Nos | 1
b | 80 mm | Nos | 1
c | 65 mm | Nos | 7
18 | Supply, installation, testing and commissioning of gun metal fire hydrant valve, single headed oblique type 63 mm instantaneous outlets with female socket for hose connection and inlet side with flange suitable for 100 mm pipe flange, valve conforming to 1S:5290 complete with blank cap chain, etc | Nos | 7
19 | Supplying and fixing First-aid Hose Reel with MS construction spray painted in Post office Red, conforming to IS 884 with up to date amendments, complete with the following as required. (a) 30 m. long 20 mm (nominal internal dia water hose Thermoplastic (Textile reinforced) Type-2 as per IS: 12585 (b) 20 mm (nominal internal ) dia gun metal globe valve & nozzle. (c) Drum and brackets for fixing the equipments on wall. (d) Connections from riser with 40 mm dia stop valve (gun metal) & M.S. Pipe | Nos | 4
20 | Supplying and fixing 63 mm dia, 15 mtr. Long RRL hose pipe with 63 mm dia Male and Female Gun metal couplings duly binded with GI wire, rivets etc. conforming to IS 636 (type-A) as required. | Nos | 14
21 | Supplying & fixing 63 mm dia Gun metal branch pipe with 20 mm (nominal internal diameter) size Gun Metal nozzle conforming to IS 903, suitable for instantaneous connection to inter-connect hose pipe coupling as required. | Nos | 7
22 | Supply, installation, testing and commissioning of hose boxes wall/pedestal type of size 750 x 250 x 600 mm made out of 16 SWG MS sheet steel with front side glass, locking arrangement and painted with approved colour completed as required and as per specifications. | Nos | 7
23 | SITC of Sprinkler Alarm Valve with water motor gong, test valves, drain valves complete with all accessories, set of pressure gauges, supports, etc of following sizes. | Nos | 1
24 | Supply, installation, testing and commissioning of Fire brigade collective breaching with 4 nos. of (twin Siamese) 150 mm flanged out let connection and built in check valves complete as required. | Nos | 1
25 | Supply, and fixing of Air release valve all riser pipes as per specification | Nos | 2
GRAND TOTAL