## PART II A
VERTICAL EXTENSION & ADDITIONAL WORKS AT GENERAL HOSPITAL AT KALPETTA IN WAYANAD DISTRICT.
PART II A -ELECTRICAL WORKS
Sl. No | Item Description | Unit | Detailed Qty | Rate (Rs in figures & words) | Amount
1 | Point wiring in PVC conduit, with Modular type switch: Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5Sq.mm FR PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FR PVC insulated copper conductor single core cable etc as required
| Group C | Point | 80
2 | Twin control point wiring in PVC conduit, with modular type switch: Wiring for twin control light point with 1.5 sq.mm FR PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5sq.mm. FR PVC insulated copper conductor single core cable etc as required. | Point | 4
3 | Power plug wiring in PVC conduit (2x4 sq mm) : Wiring for light/ power plug with 2X4 sq. mm FR PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit along with 1 No 4 sq. mm FR PVC insulated copper conductor single core cable for loop earthing as required | Rm | 265
4 | Circuit Sub main wiring in PVC Conduit : Wiring for circuit sub main wiring alongwith earthwire with the following sizes of PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required.
a | 2x1.5 sq mm +1x1.5 sq. mm earth wire | Rm | 470
b | 2x2.5 sq mm +1x 2. 5 sq.mm earth wire | Rm | 300
c | 4x4 sq mm + 2x4 sq mm earth wire | Rm | 80
d | 4x6 sq mm + 2x6 sq mm earth wire. | Rm | 20
e | 4x10 sq mm + 2x10 sq mm earh wire | Rm | 40
5 | Telephone wiring in existing conduit : Supplying and drawing following pair 0.5 sq mm FR PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required.
a | 2 Pair | Rm | 90
6 | S/F PVC conduit : Supplying and fixing of following sizes of medium class PVC conduit along with accessaries in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
a | 20 mm | Rm | 80
b | 25 mm | Rm | 40
7 | S/F Metal boxes : Supplying and fixing metal box of following sizes (Nominal size ) on surface or recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
a | 250 mm x300 mm x 60 mm deep | Each | 4
8 | S/F Modular type switch/ socket : Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc as required.
a | Telephone socket outlet | Each | 4
9 | Supplying and fixing electronic fan regulator : Supplying and fixing stepped type electronic fan regulator on the existing odular plate and switch box excluding modular plate but including connections etc as required. | Each | 16
10 | S/F Modular type blanking plates : Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | Each | 20
11 | S/F Modular boxes, base & cover plate : Supplying and fixing following size/ modules,GI box along with modular base, cover plate for modular switches in recess etc as required.
a | 1 or 2 module( 75 mmx75 mm) | Each | 4
12 | S/F light plug point modular type accessaries : Supplying and fixing suitable size G. I box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection,painting etc as required, (For light plugs to be used in non residential buildings }. | Each | 30
13 | S/F Power plug point with modular type switch : Supplying and fixing suitable size G. I box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 15/16& 5/6 amps modular socket outlet and 15/16 amps modular switch, connection,painting etc as required. | Each | 25
14 | S/F Ceiling rose : Supplying and fixing 3 pin , 5 amps ceiling rose on the existing junction box / wooden block including connection etc as required. | Each | 46
15 | ITC Fluroscent fitting directly on surface : Installation testing and commissioning of pre- wired, fluroscent fitting / compact fluroscent fitting of all types, complete with all accessories and tube etc. directly on ceiling / wall, including connection with 1.5 sq mm FR PVC insulated,copper conductor, single core cable and earthing etc as required. | Each | 30
16 | ITC Fluroscent fitting with down rod : Installation and testing commissioning of prewired, fluorescent fitting/compact fluorescent fitting of all types, complete with all accessories and tube etc, including supplying and fixing ball and socket arrangement, 2 Nos down rods of 20 mm dia x 1.6 mm thick steel conduit up to 30 cm length, painting and wiring the down rods and connection with 1.5 sq mm FR PVC insulated, copper conductor single core cable and earthing etc as required. | Each | 4
17 | S/F extra down rod : Providing and fixing extra conduit down rod of 20 mm dia, 2 x 10 cm length wiring with2 x 1.5 sq mm FR PVC insulated, copper conductor, single core cable including painting etc as required. ( Note: More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | Each | 10
18 | ITC Ceiling fan: Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length { Up to 30 Cm } with 1.5 sq mm FR PVC insulated, copper conductor, single core cable as required. | Each | 16
19 | Extra down rod 15 mm dia : Supplying and fixing extra down rod of 10 Cm length G. I pipe, 15 mm dia, heavy guage including painting etc. as required ( Note: More than 5 Cm length shall be rounded to the nearest 10 Cm and 5 Cm or less shall be ignored) | Each | 25
20 | ITC Exhaust fan up to 450 mm sweep: Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. | Each | 6
21 | S/F TPMCB DB : Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
a | 4 way ( 4+12 ), Double door | Each | 4
b | 6 way ( 4+18 ), Double door | Each | 1
c | 8 way ( 4+24 ), Double door | Each | 1
22 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's (but without MCB's and incomer) as required.
a | 4 way (4 + 12), Double door | Each | 2
23 | S/F 'C' series, MCB : Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | Single pole | Each | 33
b | Triple Pole | Each | 8
c | Triple Pole and neutral | Each | 8
24 | S/F SP MCB blanking plate : Supplying and fixing single pole blanking plate in the existing MCB DB complete etc as required. | Each | 36
25 | S/F FP MCB isolator : Supplying and fixing following rating, four pole,415 Volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 40 amps | Each | 4
b | 63 amps | Each | 4
26 | S/F FP RCCB : Supplying and fixing following rating, four pole, 415 volts, residual current circuit breaker { RCCB }, having a sensitivity current up to 300 milli amperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 25 amps | Each | 4
b | 40 amps | Each | 4
c | 63 Amps | Each | 2
27 | S/F 20A SPN MCB industrial socket outlet : Supplying and fixing 20 amps, 240 Volts, SPN industril type, socket outlet, with 2 pole and earth, metal enclosed plug top along with 20 amps 'C' series, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket outlet and complete with connections, testing and commissioning etc. as required. | Each | 6
28 | Supplying and fixing 20 amps, 415 volts, TPN industrial type, socket outlet, with 4 pole and earth, metal enclosed plug top along with 20 amps "C" curve, TPMCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | Each | 1
29 | Supplying and fixing 30 amps, 415 volts, TPN industrial type, socket outlet, with 4 pole and earth, metal enclosed plug top along with 30 amps "C" curve, TPMCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | Each | 1
30 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
a | Upto 35 sqmm | Rm | 31
31 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
a | Upto 35 sq. mm (clamped with 1mm thick saddle) | Rm | 364
b | Above 35 sq.mm and upto 95 sq mm (clamped with 25x3mm MS flat clamp). | Rm | 90
32 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
a | 3.5 C x 35 sqmm | Each | 6
b | 3.5 C x 50 sqmm | Each | 4
c | 4 C x 10 sqmm | Each | 10
d | 4 C x 16 sqmm | Each | 12
33 | Supply of following size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Aluminium conductor power cable conforming to IS 7098 (Part 1) amended upto date.
a | 4 C x 10 sqmm | Rm | 130
b | 4 C x 16 sqmm | Rm | 170
c | 3.5 C x 35 sqmm | Rm | 50
d | 3.5 C x 50 sqmm | Rm | 90
34 | Supply of surface mounted 1x28W Fluorescent tube fitting with CRCA body, electronic choke, lamp and all other accessaries as required. (Bajaj BTER 128 / Crompton T5JB1328REB9 / Havells LHIT 12128032) | Each | 20
35 | Supply & fixing of 4x14W Indoor Decorative recessed mounted indirect decorative luminarie with acrylic diffuser complete with all accessories like T5 lamps, suitable ballast, chains, anchor fastner, hooks etc as required. (Bajaj BTTI 414 / Crompton CRTFL 414EBB/MLF) | Each | 12
36 | Supply of surface mounted 2x28W Fluorescent tube fitting with CRCA body, electronic choke, lamp and all other accessaries as required. (Bajaj BTIR 228 / Crompton T5GP228EB / Havells LHIT 11228033) | Each | 10
37 | Supply of ceiling fan 1200 mm sweep, double ball bearing, approved colour and quality with original down rod,suspension shackle,canopy etc with out regulator ( Make: Usha Technix flair star rated or equi) | Each | 18
38 | Supply of 250mm sweep, 1250 rpm, louvered ventilating fan suitable for single phase 230 volt, 50Hz AC supply complete with motor, capacitor, louvers/ shutters and all accessories as required complete. (Make : Usha Crisp Air or equi) | Each | 4
39 | Supply of heavy duty exhaust fan 450 mm sweep, 1400 rpm, of approved colour and quality (Make :Usha - turbo heavy duty or equi.) | Each | 2
40 | S/F PVC Holder : Supplying and fixing PVC batten/ angle holder including 15watts ISI mark CFL lamp, connection etc. as required. | Each | 6
41 | Supplying and fixing of Decorative compact street light luminaire 2x18 watts CFL, complete with epoxy black powder coated sheet steel housing, epoxy powder coated CRCA sheet steel gear tray, clear acrylic cover, aluminium reflector, lamp etc with all required accessories. The light shall be fabricated and fixed with suitable size and length B class GI pipe, 3x1.5sqmm Cu wire from point to the fitting. (Bajaj BJSLF 218 DD / Crompton SCE 13218). | Each | 4
42 | S/L 12 SWG copper wire in ground : Supplying and laying/fixing 12 SWG copper wire along with MV cales in ground/wall surface for conductor earth electrode, including soldering etc as required | Rm | 80
43 | S/L 10 SWG copper wire in ground : Supplying and laying/fixing 10 SWG copper wire along with MV cales in ground/wall surface for conductor earth electrode, including soldering etc as required | Rm | 250
44 | Supply & laying ISI marked 2m x 1m x 6 mm for 415V grade electrical grade chequered type rubber mat. | Each | 6
45 | Supply, fabrication and fixing 3 nos MS Fire buckets on suitable fabricated MS angle iron stand with hook, painting with red paint & filled with dry sand as required with all required accessories. | Each | 1
46 | Supply, Installation, Testing & Commissioning of Sub panel, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP42, free standing, floor / wall mounting, dust and vermin proof, powder coated, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system, including internal wiring with suitable size wires, rotary handle, spreaders, 3mm thick gland plate, hinged type door with neoprene gasket etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification.
Incomer
100A, TPN, MCCB, thermal magnetic having adjustable O/L, SC protection - 1 no.
Busbar
1 Set of 150 A TPN busbars of high conductivity electrolytic quality Aluminium alloy and suitable size earthing conductor through out the panel for its earthing.
Instruments
2A, C curve SP MCB - 3 nos.
RYB indication lamp, LED type - 3 nos.
1 No 3 phase Digital Multi function meter to read V, A, F.
100/5A 5VA class 1 resin cast CT - 1 set
Outgoing.
32A TPN C curve MCB - 4 nos.
| 25A TPN C curve MCB - 6 nos. | Each | 1
TOTAL - PART II A - ELECTRICAL WORKS

## Electrical (EXT detailed) (hidden)
EXTENSION OF GENERAL HOSPITAL, KALPETTA (WAYANAD)
PART II -ELECTRICAL WORKS - Detailed Estimate
SL. No. | DSR No. | Description of item | Unit | Qty
PART B - ELECTRICAL WORKS
COPPER WIRING IN PVC CONDUIT.
1 | 1.1 | Point wiring in PVC conduit, with Modular type switch: Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5Sq.mm FR PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FR PVC insulated copper conductor single core cable etc as required
c | 1.10.3 | Group C | Point | 80
2 | 1.11 | Twin control point wiring in PVC conduit, with modular type switch: Wiring for twin control light point with 1.5 sq.mm FR PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5sq.mm. FR PVC insulated copper conductor single core cable etc as required. | Point
|  | Stair First Floor |  | 2
|  | Stair Second Floor |  | 1
|  | Stair Third Floor |  | 1
|  | Total |  | 4
3 | 1.12 | Power plug wiring in PVC conduit (2x4 sq mm) : Wiring for light/ power plug with 2X4 sq. mm FR PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit along with 1 No 4 sq. mm FR PVC insulated copper conductor single core cable for loop earthing as required | Mt
Ground Floor
|  | Pump Room |  | 10
Second Floor
|  | ICU |  | 100
|  | Lobby |  | 30
Third Floor
|  | Lobby |  | 15
|  | Pediatric ICU |  | 110
|  | Total |  | 265
4 | 1.14 | Circuit Sub main wiring in PVC Conduit : Wiring for circuit sub main wiring alongwith earthwire with the following sizes of PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required.
a | 1.14.1 | 2x1.5 sq mm +1x1.5 sq. mm earth wire | Mt
|  | Pump Room |  | 40
Second Floor
|  | ICU |  | 180
|  | Lobby |  | 50
Third Floor
|  | Lobby |  | 40
|  | Pediatric ICU |  | 160
|  | Total |  | 470
b | 1.14.2 | 2x2.5 sq mm +1x 2. 5 sq.mm earth wire | Mt
|  | Pump Room |  | 30
Second Floor
|  | ICU |  | 120
|  | Lobby |  | 20
Third Floor
|  | Pediatric ICU |  | 110
|  | Lobby |  | 20
|  | Total |  | 300
c | 1.14.8 | 4x4 sq mm + 2x4 sq mm earth wire | Mt
|  | Second Floor |  | 40
|  | Third Floor |  | 40
|  | Total |  | 80
d | 1.14.9 | 4x6 sq mm + 2x6 sq mm earth wire. | Mt | 20
|  | Second Floor |  | 10
|  | Third Floor |  | 10
|  | Total |  | 20
e | 1.14.10 | 4x10 sq mm + 2x10 sq mm earh wire | Mt
|  | Second Floor |  | 20
|  | Third Floor |  | 20
|  | Total |  | 40
5 | 1.18 | Telephone wiring in existing conduit : Supplying and drawing following pair 0.5 sq mm FR PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required.
a | 1.18.2 | 2 Pair | Mt
Second Floor
|  | ICU |  | 40
Third Floor
|  | Pediatric ICU |  | 50
|  | Total |  | 90
STEEL/PVC CONDUIT, METAL BOXES
6 | 1.21 | S/F PVC conduit : Supplying and fixing of following sizes of medium class PVC conduit along with accessaries in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
a | 1.21.1 | 20 mm | Mt
|  | Second Floor |  | 40
|  | Third Floor |  | 40
|  | Total |  | 80
b | 1.21.2 | 25 mm | Mt
|  | Second Floor |  | 20
|  | Third Floor |  | 20
|  | Total |  | 40
7 | 1.22 | S/F Metal boxes : Supplying and fixing metal box of following sizes ( Nominal size ) on surface or recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
b | 1.22.15 | 250 mm x300 mm x 60 mm deep | Each
|  | Second floor |  | 2
|  | Third Floor |  | 2
|  | Total |  | 4
SWITCHES & ACCESSORIES
8 | 1.24 | S/F Modular type switch/ socket : Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc as required.
a | 1.24.6 | Telephone socket outlet | Each
Second Floor
|  | ICU |  | 2
Third Floor
|  | Pediatric ICU |  | 2
|  | Total |  | 4
9 | 1.25 | Supplying and fixing electronic fan regulator : Supplying and fixing stepped type electronic fan regulator on the existing modular plate and switch box excluding modular plate but including connections etc as required. | Each
Ground Floor
|  | Pump Room |  | 2
Second Floor
|  | ICU |  | 7
Third Floor
|  | Pediatric ICU |  | 7
|  | Total |  | 16
10 | 1.26 | S/F Modular type blanking plates : Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | Each
Ground Floor
|  | Pump Room |  | 4
|  | Second Floor |  | 8
|  | Third floor |  | 8
|  | Total |  | 20
11 | 1.27 | S/F Modular boxes, base & cover plate : Supplying and fixing following size/ modules,GI box along with modular base, cover plate for modular switches in recess etc as required.
| 1.27.1 | 1 or 2 module( 75 mmx75 mm) | Each
Second Floor
|  | ICU |  | 2
Third Floor
|  | Pediatric ICU |  | 2
|  | Total |  | 4
12 | 1.31 | S/F light plug point modular type accessaries : Supplying and fixing suitable size G. I box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection,painting etc as required, (For light plugs to be used in non residential buildings }. | Each
Ground Floor
|  | Pump Room |  | 2
Second Floor
|  | ICU |  | 12
Third Floor
|  | Pediatric ICU |  | 16
|  | Total |  | 30
13 | 1.32 | S/F Power plug point with modular type switch : Supplying and fixing suitable size G. I box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 15/16& 5/6 amps modular socket outlet and 15/16 amps modular switch, connection,painting etc as required. | Each
Ground Floor
|  | Pump Room |  | 2
Second Floor
|  | ICU |  | 8
|  | Lobby |  | 1
Third Floor
|  | Lobby |  | 1
|  | Pediatric ICU |  | 13
|  | Total |  | 25
14 | 1.33 | S/F Ceiling rose : Supplying and fixing 3 pin , 5 amps ceiling rose on the existing junction box / wooden block including connection etc as required. | Each
Ground Floor
|  | Pump Room |  | 4
|  | Second Floor |  | 20
|  | Third Floor |  | 22
|  | Total |  | 46
15 | 1.41 | ITC Fluroscent fitting directly on surface : Installation testing and commissioning of pre- wired, fluroscent fitting / compact fluroscent fitting of all types, complete with all accessories and tube etc. directly on ceiling / wall, including connection with 1.5 sq mm FR PVC insulated,copper conductor, single core cable and earthing etc as required. | Each
Second Floor
|  | ICU |  | 14
|  | Stair |  | 2
Third Floor
|  | Pediatric ICU |  | 12
|  | Stair |  | 2
|  | Total |  | 30
16 | 1.42 | ITC Fluroscent fitting with down rod : Installation and testing commissioning of prewired, fluorescent fitting/compact fluorescent fitting of all types, complete with all accessories and tube etc, including supplying and fixing ball and socket arrangement, 2 Nos down rods of 20 mm dia x 1.6 mm thick steel conduit up to 30 cm length, painting and wiring the down rods and connection with 1.5 sq mm FR PVC insulated, copper conductor single core cable and earthing etc as required. | Each
|  | Pump Room |  | 2
|  | Outside |  | 2
|  | Total |  | 4
17 | 1.43 | S/F extra down rod : Providing and fixing extra conduit down rod of 20 mm dia, 2 x 10 cm length wiring with2 x 1.5 sq mm FR PVC insulated, copper conductor, single core cable including painting etc as required. ( Note: More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored)
|  | Total | Each | 10
18 | 1.44 | ITC Ceiling fan : Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length { Up to 30 Cm } with 1.5 sq mm FR PVC insulated, copper conductor, single core cable as required.
Ground Floor
|  | Pump Room |  | 2
Second Floor
|  | ICU |  | 7
Third Floor
|  | Pediatric ICU |  | 7
|  | Total |  | 16
19 | 1.47 | Extra down rod 15 mm dia : Supplying and fixing extra down rod of 10 Cm length G. I pipe, 15 mm dia, heavy guage including painting etc. as required ( Note: More than 5 Cm length shall be rounded to the nearest 10 Cm and 5 Cm or less shall be ignored) | Each
|  | Ground Floor |  | 1
|  | Second floor |  | 12
|  | First Floor |  | 12
|  | Total |  | 25
20 | 1.5 | ITC Exhaust fan up to 450 mm sweep: Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. | Each
|  | Pump Room |  | 3
Third Floor
|  | Pediatric ICU |  | 3
|  | Total |  | 6
MCB DISTRIBUTION BOARDS
21 | 2.4.4 | S/F TPMCB DB : Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
a | 2.4.4.4 | 4 way ( 4+12 ), Double door | Each
|  | Pump Room |  | 1
|  | Second Floor |  | 2
|  | Third Floor |  | 1
|  | Total |  | 4
b | 2.4.4.5 | 6 way ( 4+18 ), Double door | Each
|  | Third Floor |  | 1
|  | Total |  | 1
c | 2.4.4.6 | 8 way ( 4+24 ), Double door | Each
|  | Second Floor |  | 1
22 | 2.5 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's (but without MCB's and incomer) as required.
a | 2.5.4 | 4 way (4 + 12), Double door | Each
|  | Second Floor |  | 1
|  | Third Floor |  | 1
|  | Total |  | 2
MCB's
23 | 2.1 | S/F 'C' series, MCB : Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 2.10.1 | Single pole | Each
|  | Pump Room |  | 7
|  | Second Floor |  | 12
|  | Third Floor |  | 14
|  | Total |  | 33
b | 2.10.4 | Triple Pole | Each
|  | Second Floor |  | 4
|  | Third Floor |  | 4
|  | Total |  | 8
c. | 2.10.5 | Triple pole And neutral | Each
|  | Second floor |  | 4
|  | Third floor |  | 4
|  | Total |  | 8
24 | 2.11 | S/F SP MCB blanking plate : Supplying and fixing single pole blanking plate in the existing MCB DB complete etc as required. | Each | 36
25 | 2.13 | S/F FP MCB isolator : Supplying and fixing following rating, four pole,415 Volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 2.13.1 | 40 amps | Each
|  | Second Floor |  | 2
|  | Third Floor |  | 2
|  | Total |  | 4
b | 2.13.2 | 63 amps | Each
|  | Pump Room |  | 1
|  | Third Floor |  | 3
|  | Total |  | 4
26 | 2.15 | S/F FP RCCB : Supplying and fixing following rating, four pole, 415 volts, residual current circuit breaker { RCCB }, having a sensitivity current up to 300 milli amperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 2.15.1 | 25 amps | Each
|  | Second Floor |  | 2
|  | Third Floor |  | 2
|  | Total |  | 4
b | 2.15.2 | 40 amps | Each
|  | Pump Room |  | 1
|  | Second Floor |  | 2
|  | Third Floor |  | 1
|  | Total |  | 4
c | 2.15.3 | 63 Amps | Each
|  | Second Floor |  | 1
|  | Third Floor |  | 1
|  | Total |  | 2
27 | 2.18 | S/F 20A SPN MCB industrial socket outlet : Supplying and fixing 20 amps, 240 Volts, SPN industril type, socket outlet, with 2 pole and earth, metal enclosed plug top along with 20 amps 'C' series, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket outlet and complete with connections, testing and commissioning etc. as required. | Each
Second Floor
|  | ICU |  | 3
Third Floor
|  | Pediatric ICU |  | 3
|  | Total |  | 6
28 | 2.19 | Supplying and fixing 20 amps, 415 volts, TPN industrial type, socket outlet, with 4 pole and earth, metal enclosed plug top along with 20 amps "C" curve, TPMCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | Each
|  | Pump Room |  | 1
|  | Total |  | 1
29 | 2.2 | Supplying and fixing 30 amps, 415 volts, TPN industrial type, socket outlet, with 4 pole and earth, metal enclosed plug top along with 30 amps "C" curve, TPMCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | Each | 1
31 | 7.6 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
a | 7.6.1 | Upto 35 sqmm | Rm | 31
32 | 7.7 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
a | 7.7.1 | Upto 35 sq. mm (clamped with 1mm thick saddle) | m | 364
b | 7.7.2 | Above 35 sq.mm and upto 95 sq mm (clamped with 25x3mm MS flat clamp). | m | 90
33 | 9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
a | 9.1.21 | 3.5Cx35sqmm | Each | 6
b | 9.1.22 | 3.5C x 50sqmm | Each | 4
c | 9.1.32 | 4 C x 10 sqmm | Each | 10
d | 9.1.33 | 4 C x 16 sqmm | Each | 12
LMR ITEMS
FITTINGS & FIXTURES
1 | LMR | Supply of following size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Aluminium conductor power cable conforming to IS 7098 (Part 1) amended upto date.
a |  | 4 C x 10 sqmm | Rm | 130
b |  | 4 C x 16 sqmm | Rm | 170
c |  | 3.5Cx35sqmm | Rm | 50
d |  | 3.5C x 50sqmm | Rm | 90
2 | LMR | Supply of surface mounted 1x28W Fluorescent tube fitting with CRCA body, electronic choke, lamp and all other accessaries as required. (Bajaj BTER 128 / Crompton T5JB1328REB9 / Havells LHIT 12128032) | Each | 20
Second Floor
|  | Staircase |  | 1
|  | Lobby |  | 5
|  | Nurses Station |  | 4
|  | Total |  | 10
Third Floor
|  | Staircase |  | 1
|  | Lobby |  | 5
|  | Nurses Station |  | 4
|  | Total |  | 10
3 | LMR | Supply & fixing of 4x14W Indoor Decorative recessed mounted indirect decorative luminarie with acrylic diffuser complete with all accessories like T5 lamps, suitable ballast, chains, anchor fastner, hooks etc as required. (Bajaj BTTI 414 / Crompton CRTFL 414EBB/MLF)
|  | ICU | Each | 6
|  | Pediatric ICU |  | 6
|  | Total |  | 12
4 | LMR | Supply of surface mounted 2x28W Fluorescent tube fitting with CRCA body, electronic choke, lamp and all other accessaries as required. (Bajaj BTIR 228 / Crompton T5GP228EB / Havells LHIT 11228033)
|  | Pump Room | Each | 2
|  | Outside lights |  | 8
|  | Total |  | 10
5 | LMR | Supply of ceiling fan 1200 mm sweep, double ball bearing, approved colour and quality with original down rod,suspension shackle,canopy etc with out regulator ( Make: Usha Technix flair star rated or equi) | Each | 18
Ground floor
|  | Pump Room |  | 1
Second Floor
|  | ICU |  | 9
Third Floor
|  | Pediatric ICU |  | 8
|  | Total |  | 18
6 | LMR | Supply of 1250mm sweep, 1250 rpm, louvered ventilating fan suitable for single phase 230 volt, 50Hz AC supply complete with motor, capacitor, louvers/ shutters and all accessories as required complete. (Make : Usha Crisp Air or equi) | Each
Second Floor
|  | ICU |  | 2
Third Floor
|  | Pediatric ICU |  | 2
|  | Total |  | 4
7 | LMR | Supply of heavy duty exhaust fan 450 mm sweep, 1400 rpm, of approved colour and quality (Make :Usha - turbo heavy duty or equivalent) | Each
Ground Floor
|  | Pump Room |  | 2
|  | Total |  | 2
8 | LMR | S/F PVC Holder: Supplying and fixing PVC batten/angle holder including 15 Watts ISI mark CFL Lamp, connection etc as required | Each
Second Floor
|  | ICU |  | 3
Third Floor
|  | Pediatric ICU |  | 3
|  | Total |  | 6
9 | LMR | Supplying and fixing of Decorative compact street light luminaire 2x18 watts CFL, complete with epoxy black powder coated sheet steel housing, epoxy powder coated CRCA sheet steel gear tray, clear acrylic cover, aluminium reflector, lamp etc with all required accessories. The light shall be fabricated and fixed with suitable size and length B class GI pipe, 3x1.5sqmm Cu wire from point to the fitting. (Bajaj BJSLF 218 DD / Crompton SCE 13218). | Each | 4
10 | LMR | S/L 12 SWG copper wire in ground : Supplying and laying/fixing 12 SWG copper wire along with MV cales in ground/wall surface for conductor earth electrode, including soldering etc as required | Metre | 80
11 | LMR | S/L 10 SWG copper wire in ground : Supplying and laying/fixing 10 SWG copper wire along with MV cales in ground/wall surface for conductor earth electrode, including soldering etc as required | Metre | 250
12 | LMR | Supply & laying ISI marked 2m x 1m x 6 mm for 415V grade electrical grade chequered type rubber mat. | Nos | 6
13 | LMR | Supply, fabrication and fixing 3 nos MS Fire buckets on suitable fabricated MS angle iron stand with hook, painting with red paint & filled with dry sand as required with all required accessories. | Nos | 1
14 |  | Supply, Installation, Testing & Commissioning of Sub panel, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP42, free standing, floor / wall mounting, dust and vermin proof, powder coated, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system, including internal wiring with suitable size wires, rotary handle, spreaders, 3mm thick gland plate, hinged type door with neoprene gasket etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification. | No | 1
Incomer
100A, TPN, MCCB, thermal magnetic having adjustable O/L, SC protection - 1 no.
Busbar
1 Set of 150 A TPN busbars of high conductivity electrolytic quality Aluminium alloy and suitable size earthing conductor through out the panel for its earthing.
Instruments
2A, C curve SP MCB - 3 nos.
RYB indication lamp, LED type - 3 nos.
1 No 3 phase Digital Multi function meter to read V, A, F.
100/5A 5VA class 1 resin cast CT - 1 set
Outgoing.
32A TPN C curve MCB - 4 nos.
25A TPN C curve MCB - 6 nos.

## Electrical (Ren Detailed) (hidden)
RENOVATION OF GENERAL HOSPITAL, KALPETTA (WAYANAD)
PART II -ELECTRICAL WORKS- Detailed Estimate
SL. No | DSR/ LMR | Item Description | Unit | Detailed Qty
COPPER WIRING IN PVC CONDUIT.
1 | 1.1 | Point wiring in PVC conduit, with Modular type switch: Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5Sq.mm FR PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FR PVC insulated copper conductor single core cable etc as required
a | 1.10.1 | Group C | Point | 150
2 | 1.15 | Rewiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FR PVC insulated copper conductor single core cable and 1.5 sq.mm. FR PVC insulated copper conductor single core cable as earth wire in existing surface/ recessed steel conduit including dismantling as required.
a | 1.15.2 | Group C | Point
Ground Floor
|  | Waiting |  | 3
|  | Casualty |  | 3
|  | Injection Room |  | 2
|  | OP Ticket Counter |  | 2
First Floor
|  | Gynec 1st Stage Nurse Station |  | 1
Second Floor
|  | Holding |  | 2
|  | Scrub |  | 1
|  | OT Passage |  | 4
Third Floor
|  | Medical Male Ward |  | 2
|  | Surgical Male Ward |  | 1
|  | Pediatric |  | 3
|  | Total |  | 24
3 | 1.12 | Power plug wiring in PVC conduit (2x4 sq mm) : Wiring for light/ power plug with 2X4 sq. mm FR PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit along with 1 No 4 sq. mm FR PVC insulated copper conductor single core cable for loop earthing as required | Mt
|  | Medical Gas Room |  | 25
Ground Floor
|  | Casuality |  | 20
First Floor
|  | Labour Room |  | 80
Second Floor
|  | Operation Theatre 1 |  | 105
|  | Operation Theatre 2 |  | 105
|  | Operation Theatre 3 |  | 105
|  | Sterile Store |  | 20
|  | Holding |  | 20
|  | OT Passage |  | 15
|  | Neonatal ICU |  | 55
|  | Total |  | 550
4 | 1.14 | Circuit Sub main wiring in PVC Conduit : Wiring for circuit sub main wiring alongwith earthwire with the following sizes of PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required.
a | 1.14.1 | 2x1.5 sq mm +1x1.5 sq. mm earth wire | Mt
|  | Medical Gas Room |  | 40
|  | Ground Floor |  | 90
|  | First Floor |  | 40
|  | Second Floor |  | 120
|  | Third Floor |  | 60
|  | Total |  | 350
b | 1.14.2 | 2x2.5 sq mm +1x 2. 5 sq.mm earth wire | Mt
|  | Medical Gas Room |  | 20
|  | Ground Floor |  | 20
|  | First Floor |  | 20
|  | Second Floor |  | 170
|  | Third Floor |  | 10
|  | Total |  | 240
c | 1.14.8 | 4x4 sq mm + 2x4 sq mm earth wire | Mt
|  | First Floor |  | 30
|  | Total |  | 30
d | 1.14.9 | 4x6 sq mm + 2x6 sq mm earth wire. | Mt
|  | First Floor |  | 30
|  | Second Floor |  | 35
|  | Total |  | 65
e | 1.14.10 | 4x10 sq mm + 2x10 sq mm earh wire | Mt
|  | Second Floor |  | 10
|  | Total |  | 10
5 | 1.18 | Telephone wiring in existing conduit : Supplying and drawing following pair 0.5 sq mm FR PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required.
a | 1.18.2 | 2 Pair | Mt
Ground Floor
|  | Injection Room |  | 10
First Floor
|  | Labour Room Nurse Station |  | 20
|  | Gynec 1st Stage Nurse Station |  | 30
|  | Gynec 2nd Stage Nurse Station |  | 30
|  | Gynec 3rd Stage Nurse Station |  | 30
Second Floor
|  | Female Post Operative Ward Nurse Station |  | 35
|  | Male Post Operative Ward Nurse Station |  | 35
Third Floor
|  | Medical Male Ward |  | 45
|  | Surgical Male Ward |  | 45
|  | Pediatric Ward |  | 50
|  | Medical Female Ward |  | 45
|  | Surgical Female Ward |  | 45
|  | Total |  | 420
6 | 1.19 | T.V. Cable in existing conduit : Supplying and drawing co-axial TV cable RG-6 grade, 0.7 mm solid copper conductor PE insulated, shielded with fine tinned copper braid and protected with PVC sheath in the existing surface/ recessed steel/ PVC conduit as required. | Mt
Ground Floor
|  | OP counter |  | 50
|  | Total |  | 50
STEEL/PVC CONDUIT, METAL BOXES
7 | 1.21 | S/F PVC conduit : Supplying and fixing of following sizes of medium class PVC conduit along with accessaries in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
a | 1.21.1 | 20 mm | Mt | 210
b | 1.21.2 | 25 mm | Mt | 50
8 | 1.22 | S/F Metal boxes : Supplying and fixing metal box of following sizes ( Nominal size ) on surface or recess with suitable size of phenolic laminated sheet cover in front including painting etc as required.
a | 1.22.14 | 200 mm x300 mm x 100 mm deep | Each
|  | Second Floor |  | 5
|  | Total |  | 5
SWITCHES & ACCESSORIES
9 | 1.24 | S/F Modular type switch/ socket : Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc as required.
a | 1.24.6 | Telephone socket outlet | Each
Ground Floor
|  | Injection Room |  | 1
First Floor
|  | Labour Room Nurse Station |  | 1
|  | Gynec 1st Stage Nurse Station |  | 1
|  | Gynec 2nd Stage Nurse Station |  | 1
|  | Gynec 3rd Stage Nurse Station |  | 1
Second Floor
|  | Female Post Operative Ward Nurse Station |  | 1
|  | Male Post Operative Ward Nurse Station |  | 1
|  | Neonatal ICU |  | 2
Third Floor
|  | Medical Male Ward |  | 1
|  | Surgical Male Ward |  | 1
|  | Pediatric Ward |  | 1
|  | Medical Female Ward |  | 1
|  | Surgical Female Ward |  | 1
|  | Total |  | 14
b | 1.24.7 | TV antena socket outlet | Each
Ground Floor
|  | OP counter |  | 1
|  | Total |  | 1
10 | 1.25 | Supplying and fixing electronic fan regulator : Supplying and fixing stepped type electronic fan regulator on the existing modular plate and switch box excluding modular plate but including connections etc as required. | Each
|  | Medical Gas Room |  | 1
Ground Floor
|  | Casuality |  | 3
|  | OP Ticket Counter |  | 3
First Floor
|  | Labour Room Nurse Station |  | 1
|  | Gynec 1st Stage Nurse Station |  | 2
|  | Gynec 2nd Stage Nurse Station |  | 2
|  | Gynec 3rd Stage Nurse Station |  | 2
Second Floor
|  | Female Post Operative Ward Nurse Station |  | 1
|  | Holding |  | 1
|  | Male Post Operative Ward Nurse Station |  | 1
Third Floor
|  | Medical Male Ward |  | 1
|  | Surgical Male Ward |  | 1
|  | Pediatric Ward |  | 1
|  | Medical Female Ward |  | 1
|  | Surgical Female Ward |  | 1
|  | Total |  | 22
11 | 1.26 | S/F Modular type blanking plates : Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | Each | 20
12 | 1.27 | S/F Modular boxes, base & cover plate : Supplying and fixing following size/ modules,GI box along with modular base, cover plate for modular switches in recess etc as required.
| 1.27.1 | 1 or 2 module( 75 mmx75 mm) | Each
Ground Floor
|  | Injection Room |  | 1
|  | OP Counter |  | 1
First Floor
|  | Labour Room Nurse Station |  | 1
|  | Gynec 1st Stage Nurse Station |  | 1
|  | Gynec 2nd Stage Nurse Station |  | 1
|  | Gynec 3rd Stage Nurse Station |  | 1
Second Floor
|  | Female Post Operative Ward Nurse Station |  | 1
|  | Male Post Operative Ward Nurse Station |  | 1
|  | Neonatal ICU |  | 2
Third Floor
|  | Medical Male Ward |  | 1
|  | Surgical Male Ward |  | 1
|  | Pediatric Ward |  | 1
|  | Medical Female Ward |  | 1
|  | Surgical Female Ward |  | 1
|  | Total |  | 15
13 | 1.31 | S/F light plug point modular type accessaries : Supplying and fixing suitable size G. I box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection,painting etc as required, (For light plugs to be used in non residential buildings }. | Each
|  | Medical Gas Room |  | 3
Ground Floor
|  | Waiting |  | 1
|  | Casuality |  | 4
|  | OP Ticket Counter |  | 3
|  | Injection Room |  | 2
First Floor
|  | Labour Room Nurse Station |  | 2
|  | Labour Room |  | 3
|  | Gynec 1st Stage Nurse Station |  | 2
|  | Gynec 2nd Stage Nurse Station |  | 2
|  | Gynec 3rd Stage Nurse Station |  | 2
Second Floor
|  | Operation Theatre 1 |  | 12
|  | Operation Theatre 2 |  | 12
|  | Operation Theatre 3 |  | 12
|  | Female Post Operative Ward Nurse Station |  | 2
|  | Sterile Store |  | 2
|  | Holding |  | 2
|  | Male Post Operative Ward Nurse Station |  | 2
|  | Scrub |  | 1
|  | Neonatal ICU |  | 3
Third Floor
|  | Medical Male Ward |  | 2
|  | Surgical Male Ward |  | 2
|  | Medical Female Ward |  | 2
|  | Surgical Female Ward |  | 2
|  | Total |  | 80
14 | 1.32 | S/F Power plug point with modular type switch : Supplying and fixing suitable size G. I box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 15/16& 5/6 amps modular socket outlet and 15/16 amps modular switch, connection,painting etc as required. | Each
|  | Medical Gas Room |  | 3
Ground Floor
|  | Casuality |  | 1
First Floor
|  | Labour Room |  | 4
Second Floor
|  | Operation Theatre 1 |  | 13
|  | Operation Theatre 2 |  | 13
|  | Operation Theatre 3 |  | 13
|  | Sterile Store |  | 1
|  | Holding |  | 2
|  | OT Passage |  | 1
|  | Neonatal ICU |  | 4
|  | Total |  | 55
15 | 1.33 | S/F Ceiling rose : Supplying and fixing 3 pin , 5 amps ceiling rose on the existing junction box / wooden block including connection etc as required. | Each
|  | Medical Gas Room |  | 4
|  | Ground Floor |  | 16
|  | First Floor |  | 9
|  | Second Floor |  | 33
|  | Third Floor |  | 18
|  | Total |  | 80
16 | 1.38 | S/F call bell/ buzzer : Supplying and fixing call bell / buzer suitable for D.C / A.C single phase, 230 volts, complete as required. | Each
|  | Ground Floor |  | 1
|  | First Floor |  | 1
|  | Second Floor |  | 1
|  | Third Floor |  | 1
|  | Total |  | 4
17 | 1.41 | ITC Fluroscent fitting directly on surface : Installation testing and commissioning of pre- wired, fluroscent fitting / compact fluroscent fitting of all types, complete with all accessories and tube etc. directly on ceiling / wall, including connection with 1.5 sq mm FR PVC insulated,copper conductor, single core cable and earthing etc as required. | Each
|  | Electrical Room |  | 4
|  | Pump Room |  | 4
|  | Medical Gas Room |  | 2
Ground Floor
|  | Casuality |  | 2
|  | OP Ticket Counter |  | 4
|  | Injection Room |  | 1
|  | Medical Gas Room |  | 2
First Floor
|  | Labour Room Nurse Station |  | 2
|  | Passage |  | 2
|  | Gynec 1st Stage Nurse Station |  | 2
|  | Gynec 2nd Stage Nurse Station |  | 2
|  | Stair |  | 2
|  | Gynec 3rd Stage Nurse Station |  | 2
Second Floor
|  | Female Post Operative Ward Nurse Station |  | 1
|  | Sterile Store |  | 1
|  | Holding |  | 2
|  | Male Post Operative Ward Nurse Station |  | 1
|  | Stair |  | 2
Third Floor
|  | Medical Male Ward |  | 2
|  | Surgical Male Ward |  | 2
|  | Pediatric Ward |  | 1
|  | Medical Female Ward |  | 1
|  | Surgical Female Ward |  | 1
|  | Total |  | 45
18 | 1.42 | ITC Fluroscent fitting with down rod : Installation and testing commissioning of prewired, fluorescent fitting/compact fluorescent fitting of all types, complete with all accessories and tube etc, including supplying and fixing ball and socket arrangement, 2 Nos down rods of 20 mm dia x 1.6 mm thick steel conduit up to 30 cm length, painting and wiring the down rods and connection with 1.5 sq mm FR PVC insulated, copper conductor single core cable and earthing etc as required. | Each
|  | Medical Gas Room |  | 5
|  | Total |  | 5
19 | 1.44 | ITC Ceiling fan : Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length { Up to 30 Cm } with 1.5 sq mm FR PVC insulated, copper conductor, single core cable as required.
|  | Medical Gas Room |  | 1
Ground Floor
|  | Casuality |  | 2
|  | OP Ticket Counter |  | 2
First Floor
|  | Labour Room Nurse Station |  | 1
Labour Room
|  | Gynec 1st Stage Nurse Station |  | 1
|  | Gynec 2nd Stage Nurse Station |  | 1
|  | Gynec 3rd Stage Nurse Station |  | 1
Second Floor
|  | Female Post Operative Ward Nurse Station |  | 1
|  | Holding |  | 1
|  | Male Post Operative Ward Nurse Station |  | 1
Third Floor
|  | Medical Male Ward |  | 1
|  | Surgical Male Ward |  | 1
|  | Pediatric Ward |  | 1
|  | Medical Female Ward |  | 1
|  | Surgical Female Ward |  | 1
|  | Total |  | 22
20 | 1.47 | Extra down rod 15 mm dia : Supplying and fixing extra down rod of 10 Cm length G. I pipe, 15 mm dia, heavy guage including painting etc. as required ( Note: More than 5 Cm length shall be rounded to the nearest 10 Cm and 5 Cm or less shall be ignored) | Each | 25
21 | 1.5 | ITC Exhaust fan up to 450 mm sweep: Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. | Each
|  | Medical Gas Room |  | 2
Ground Floor
|  | Blood Bank Toilet |  | 1
Third Floor
|  | Medical Male Ward |  | 1
|  | Surgical Male Ward |  | 1
|  | Waste shaft |  | 2
|  | Pediatric |  | 1
|  | Total |  | 8
MCB DISTRIBUTION BOARDS
22 | 2.3 | S/F SPMCB DB : Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
a | 2.3.7 | 8 way, Double door | Each | 2
23 | 2.4.4 | S/F TPMCB DB : Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
a | 2.4.4.5 | 6 way, Double door | Each | 3
24 | 2.5 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's (but without MCB's and incomer) as required.
a | 2.5.4 | 4 way, Double door | Each | 1
b | 2.5.5 | 8 way, Double door | Each | 1
25 | 2.1 | S/F 'C' series, MCB : Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 2.10.1 | Single pole | Each | 50
b | 2.10.3 | Double Pole | Each | 2
c | 2.10.4 | Triple Pole | Each | 8
d | 2.10.5 | Triple Pole and neutral | Each | 4
26 | 2.11 | S/F SP MCB blanking plate : Supplying and fixing single pole blanking plate in the existing MCB DB complete etc as required. | Each | 24
27 | 2.13 | S/F FP MCB isolator : Supplying and fixing following rating, four pole,415 Volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 2.13.1 | 40 amps | Each | 4
b | 2.13.2 | 63 amps | Each | 2
28 | 2.14 | S/F DP RCCB : Supplying and fixing following rating, double pole, 240 volts, residual current circuit breaker { RCCB }, having a sensitivity current up to 300 milli amperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 2.14.2 | 40 amps | Each | 2
29 | 2.15 | S/F FP RCCB : Supplying and fixing following rating, four pole, 415 volts, residual current circuit breaker { RCCB }, having a sensitivity current up to 300 milli amperes in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 2.15.2 | 40 amps | Each | 6
b | 2.15.3 | 63 Amps | Each | 4
30 | 2.16 | Supplying and fixing DP sheet steel enclosure on surface/ recess along with 25/32amps 240 volts "C" curve DP MCB complete with connections, testing and commissioning etc. as required. | Each | 2
31 | 2.17 | Supplying and fixing TP sheet steel enclosure on surface/ recess along with 16/25/32amps 415 volts "C" curve TP MCB complete with connections, testing and commissioning etc. as required. | Each | 2
32 | 2.18 | S/F 20A SPN MCB industrial socket outlet : Supplying and fixing 20 amps, 240 Volts, SPN industril type, socket outlet, with 2 pole and earth, metal enclosed plug top along with 20 amps 'C' series, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket outlet and complete with connections, testing and commissioning etc. as required. | Each | 4
33 | 2.19 | Supplying and fixing 20 amps, 415 volts, TPN industrial type, socket outlet, with 4 pole and earth, metal enclosed plug top along with 20 amps "C" curve, TPMCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | Each | 2
33 | 7.1 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
a | 7.1.2 | Above 35 sq. mm and upto 95 sq. mm | Rm | 40
34 | 7.6 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
a | 7.6.2 | Above 35 sq. mm and upto 95 sq. mm | Rm | 20
35 | 7.7 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
a | 7.7.1 | Upto 35 sq. mm (clamped with 1mm thick saddle) | Rm | 445
b | 7.7.2 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | Rm | 30
36 | 9.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
a | 9.1.22 | 3.5 C x 50 sqmm | Each | 2
b | 9.1.21 | 3.5 C x 35 sqmm | Each | 4
c | 9.1.32 | 4 C x 10 sqmm | Each | 10
d | 9.1.33 | 4 C x 16 sqmm | Each | 6
LMR ITEMS
FITTINGS & FIXTURES
1 |  | Supply of following size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Aluminium conductor power cable conforming to IS 7098 (Part 1) amended upto date.
c | LMR | 3.5 C x 50 sqmm | Rm | 90
d | LMR | 3.5 C x 35 sqmm | Rm | 80
e | LMR | 4 C x 16 sqmm | Rm | 65
f | LMR | 4 C x 10 sqmm | Rm | 300
2 | LMR | Supply of surface mounted 1x28W Fluorescent tube fitting with CRCA body, electronic choke, lamp and all other accessaries as required. (Bajaj BTER 128 / Crompton T5JB1328REB9 / Havells LHIT 12128032) | Each
|  | Outside Area |  | 5
|  | Electrical Room |  | 4
|  | Pump Room |  | 4
|  | Medical Gas Room |  | 2
Ground Floor
|  | Casualty |  | 2
|  | OP Ticket Counter |  | 4
|  | Injection Room |  | 1
First Floor
|  | Labour Room Nurse Station |  | 1
|  | Passage |  | 1
|  | Gynec 1st Stage Nurse Station |  | 1
|  | Gynec 2nd Stage Nurse Station |  | 1
|  | Gynec 3rd Stage Nurse Station |  | 1
Second Floor
|  | Female Post Operative Ward Nurse Station |  | 1
|  | Sterile Store |  | 1
|  | Holding |  | 2
|  | Male Post Operative Ward Nurse Station |  | 1
Third Floor
|  | Medical Male Ward |  | 2
|  | Surgical Male Ward |  | 2
|  | Pediatric Ward |  | 1
|  | Medical Female Ward |  | 2
|  | Surgical Female Ward |  | 1
|  | Total |  | 40
3 | LMR | Supply and installation of 3x36W, indoor clean room, recess mounted light fixture with CRCA housing, reflector and control gear tray duly powder coated, clear acrylic diffuser, non-hygroscopic gasket to ensure dust proofing, 36 W lamp, ballast, chains, anchor fastner, hooks etc prewired complete with all necessary accessories suitable for operation on 230V, 50Hz AC supply as required (Bajaj BPRF 336 C LHD / Crompton CRFW 12336EB / Havells LHHC02336127). | Each
|  | Operation Theatre 1 |  | 4
|  | Operation Theatre 2 |  | 4
|  | Operation Theatre 3 |  | 4
|  | Total |  | 12
4 | LMR | Supply & installation of 2X18 W recess mounted CFL low glare luminarie with P5 paralite louvers & decorative perforations including all accessories like 18W CFL lamp, ballast, chains, anchor fastner, hooks etc ( Bajaj BMLA 01 218 CFL D W2EB / Crompton TLE218EB/P5 / Havells LHCC25218325) | Each
|  | OT Passage |  | 7
|  | Total |  | 7
5 | LMR | Supply & fixing of 4x14W Indoor Decorative recessed mounted indirect decorative luminarie with acrylic diffuser complete with all accessories like T5 lamps, suitable ballast, chains, anchor fastner, hooks etc as required. (Bajaj BTTI 414 / Crompton CRTFL 414EBB/MLF) | Each | 2
|  | Total |  | 2
6 | LMR | Supply & fixing 15 W recess mounted white LED fitting with high efficient reflector providing efficient glare free lighting with all accessories like LED lamp , drive etc (Bajaj BZSLO 15W WH / Crompton LCDV-12-CDL / Havells LHEBJNP5PN1W015) | Each
|  | Operation Theatre 1 |  | 4
|  | Operation Theatre 2 |  | 4
|  | Operation Theatre 3 |  | 4
|  | Total |  | 12
7 | LMR | Supply & fixing 15 W square recess mounted white LED fitting with high efficient reflector providing efficient glare free lighting with all accessories like LED lamp , drive etc (Bajaj BZSLO 15W SQ WH / Crompton LCDSQ-12-CDL / Havells LHCDO1116674) | Each
|  | OT Passage |  | 6
|  | Total |  | 6
8 | LMR | Supply of surface mounted 2x28W Fluorescent tube fitting with CRCA body, electronic choke, lamp and all other accessaries as required. (Bajaj BTIR 228 / Crompton T5GP228EB / Havells LHIT 11228033) |  | 8
|  | Electrical room |  | 4
|  | Pump Room |  | 4
|  | Total |  | 8
9 | LMR | Supply of ceiling fan 1200 mm sweep, double ball bearing, approved colour and quality with original down rod,suspension shackle,canopy etc with out regulator ( Make: Usha Technix flair star rated or equi) | Each
|  | Medical Gas Room |  | 2
Ground Floor
|  | Casualty |  | 2
|  | OP Ticket Counter |  | 2
First Floor
|  | Labour Room Nurse Station |  | 2
|  | Gynec 1st Stage Nurse Station |  | 2
|  | Gynec 2nd Stage Nurse Station |  | 2
|  | Gynec 3rd Stage Nurse Station |  | 2
Second Floor
|  | Female Post Operative Ward Nurse Station |  | 1
|  | Holding |  | 1
|  | Male Post Operative Ward Nurse Station |  | 1
Third Floor
|  | Medical Male Ward |  | 1
|  | Surgical Male Ward |  | 1
|  | Pediatric Ward |  | 1
|  | Medical Female Ward |  | 1
|  | Surgical Female Ward |  | 1
|  | Total |  | 22
10 | LMR | Supply of 1250mm sweep, 1250 rpm, louvered ventilating fan suitable for single phase 230 volt, 50Hz AC supply complete with motor, capacitor, louvers/ shutters and all accessories as required complete. (Make : Usha Crisp Air or equi) | Each
Ground Floor
|  | Blood Bank Toilet |  | 1
Third Floor
|  | Medical Male Ward |  | 1
|  | Surgical Male Ward |  | 1
|  | Pediatric |  | 1
2
|  | Total |  | 6
11 | LMR | Supply of heavy duty exhaust fan 450 mm sweep, 1400 rpm, of approved colour and quality (Make :Usha - turbo heavy duty or equi.) | Each
|  | Electrical Room |  | 1
|  | Pump Room |  | 1
|  | Total |  | 2
12 | LMR | Supply and fixing 400 mm sweep wall fan, swinging type with speed control and necessary adapter, of approved quality and colour. (Make : Usha - Maxx Air or equivalent model in CG) | Each
|  | OP Ticket Counter |  | 4
13 | LMR | S/F PVC Holder : Supplying and fixing PVC batten/ angle holder including 15watts ISI mark CFL lamp, connection etc. as required. | Each | 25
14 | LMR | Supply, installation, testing and commissioning of 10 pair telephone terminal box. The terminal box shall be with sheet steel enclosure and krone type. | Each | 4
15 | LMR | S/L 12 SWG copper wire in ground : Supplying and laying/fixing 12 SWG copper wire along with MV cables in ground/wall surface for conductor earth electrode, including soldering etc as required | Metre | 450
16 | LMR | S/L 10 SWG copper wire in ground : Supplying and laying/fixing 10 SWG copper wire along with MV cales in ground/wall surface for conductor earth electrode, including soldering etc as required | Metre | 300
17 | LMR | Dismantling the existing switch, socket, regulator etc with switch box, wiring and stacking the same to the place as per the direction of engineer in charge. The item shall be measured per switch box. | Point | 50
18 | LMR | Dismantling the existing light fixing, ceiling fan, exhaust fan, wall fan, industrial socket etc. and stacking the same to the place as per the direction of engineer in charge. | Each
|  | Ground Floor |  | 7
|  | First Floor |  | 7
|  | Second Floor |  | 18
|  | Third Floor |  | 18
|  | Total |  | 50
19 | LMR | Supply, Installation, testing & Commissioning of 63 A TPN 415Volts, Switch Disconnector Fuse Unit including Rotary Handle, 63A HRC Fuse, in existing Cubicle type panel with copper connecting links to busbar, and all allied accessories as required. | Each | 5
20 | LMR | Dismantling the existing SDF Units upto 63A from the exisitng cubicle and stacked at a place as directed by Engineer-in-charge. | Each | 5