TENDER DOCUMENT

FOR

SUPPLY INSTALLATION TESTING AND COMMISSIONING OF ELEVATOR SYSTEM FOR INSTITUTE OF MENTAL HEALTH AND NEUROSCIENCES IMHANS CALICUT.

PART-II

GCC

TENDER NO. HLL/ID/13/2

January - 2013

HLL LIFECARE LIMITED.

INFRASTRUCTURE DEVELOPMENT DIVISION

| INDEX |  |  |
| --- | --- | --- |
| SL.NO | DETAILS | PAGE |
| 1 | Notice Inviting Tender | 3 |
| 2 | Tender (Form HLL. W - 8) | 6 |
| 3 | Proforma of Schedules A to F | 9 |
| 4 | Additional Conditions | 14 |
| 5 | Proforma |  |
|  | - Proforma for Agreement | 15 |
| 6 | - Form for Bank Guarantee for Performance Security | 18 |
| 7 | iii) Form for Bank Guarantee for Earnest Money Deposit | 21 |
| 8 | Clauses Of Contract | 21 |
| 9 | Technical Specification for Elevators | 94 |
| 10 | List of Approved Makes | 101 |

HLL LIFECARE LIMITED

(A Government of India Enterprise)

NOTICE INVITING TENDER

- Item rate tenders are invited by HLL Lifecare Ltd on from Qualified and Registered Contractors for the Supply Installation Testing and Commissioning of Elevator system for Institute of Mental Health and Neurosciences (IMHANS),Calicut

- The estimated cost of the work is Rs.69,06,000/- (Rupees Sixty nine lakhs and Six Thousand Only). This estimate is however, is given merely as a rough guide. The estimated cost of each component is given below.

| 1. | Elevator | Rs.69,06,000/- |
| --- | --- | --- |

- Agreement shall be drawn with the successful tenderer and the entire tender document, shall form part of the contract.

- The time allowed for carrying out the work will be 4 months from the date of handing over of the site

- Tender documents shall be downloaded from the website www.lifecarehll.com from 21.02.2013.

- Tenders, which should be placed in sealed envelope, with the name of the work and due date written on the envelopes, will be received by the Deputy General Manager (Technical), HLL Lifecare Limited, “Adarsh”, Vettamukku, T.C.6/1718(1), Thirumala PO, Thiruvananthapuram- 695006 or his authorized representative up to 3.00 pm on 05.02.13 and will be opened by him or his authorized representative in this office the same day at                          3.30 Pm.

- Earnest Money of Rs.1,38,120/-in the form of a Demand Draft or Fixed Deposit Receipt or in the form of an irrevocable guarantee bond of any scheduled bank or State Bank of India and its associates issued in favour of HLL Lifecare Limited, which should be placed in a separate sealed cover marked “Earnest Money” shall be submitted along with the tenders

- The contractor shall be required to deposit an amount equal to 5% of the tendered value of the work as performance guarantee in the form of an irrevocable bank guarantee of any scheduled bank or State Bank of India in accordance with the form prescribed or in the form of Fixed Deposit Receipt etc within 30 days of issue of letter of intent / acceptance.

- HLL Lifecare Ltd does not bind itself to accept the lowest or any other tender and reserves to itself the authority to reject any or all the tenders received without assigning any reason. All tenders in which any of the prescribed condition is not fulfilled or with any condition including conditional rebate shall be summarily rejected.

- “The evaluation of the Price Bid shall however be governed by the Purchase Preference Policy of the Government for products and services of Central Public Sector Enterprises”.

- Canvassing whether directly or indirectly, in connection with tenders is strictly prohibited and the tenders submitted by the contractors who resort to canvassing will be liable for rejection.

- HLL Lifecare Ltd does not bind itself to accept the whole or any part of the tender.  The tenderer shall be bound to perform the contract at the rates quoted.

The firm or contractor shall not be permitted to tender for work in case his near relative (s) (directly recruited or on deputation in HLL Lifecare Ltd) is/are posted in any capacity either as non-executive or executive employee. The contractor shall also intimate the names of persons who are working with him in any capacity or are subsequently employed by him and who are near relative to any executive employee/ gazetted officer in HLL Lifecare Ltd or in NRHM.

- No Engineer of Gazetted rank or other Gazetted Officer employed in engineering or administrative duties in an Engineering Department of the Government of India/State Government or PSU’s is allowed to work as a contractor for a period of two years after his retirement from Govt. service, without previous permission of the Govt. of India or State Government or PSU’s as the case may be in writing. This contract is liable to be cancelled if either the contractor or any of his employees is found any time to be such a person who had not obtained the permission of the Govt. of India/State Government or PSU’s as aforesaid before submission of the tender or engagement in the contractor’s service.

- The tender for the work shall remain open for acceptance for a period of 120 days from the date of opening of the tenders. If any tenderer withdraws his tender before the said period or issue of letter of acceptance/indent, whichever is earlier, or, makes any modifications in the terms and conditions of the tender which are not acceptable to HLL Lifecare Ltd, then HLL Lifecare Ltd shall, without prejudice to any other right or remedy, be at liberty to forfeit 50% of the said earnest money as aforesaid.

- This Notice Inviting Tender shall form a part of the Contract Document. In accordance with clause 1 of the contract, the letter of intent/acceptance shall be issued first in favour of the successful Tenderer. After submission of the performance guarantee, the letter for commencement of work shall be issued. The contract shall be deemed to have come into effect on issue of communication of acceptance of the tender. On such communication of acceptance, the successful Tenderer/Contractor shall, within 30 days from such date, formally sign the agreement consisting of: -

a) The Notice Inviting Tender, all the documents including additional conditions, specifications and drawings, forming part of the tender, and, as issued at the time of invitation of tender and acceptance there of together with any correspondence leading there to.

b) Agreement signed on non-judicial stamp paper as per Proforma annexed to the tender document.

The successful tenderer shall submit the work programme bar chart with milestones along with weightage for each activity within 10 days of letter of intent / acceptance before signing of contract agreement.

Deputy General Manager (Technical)

HLL Lifecare Limited.

### HLL Lifecare Ltd  W – 8

### HLL LIFECARE LTD                                                                                                                                                                                (A GOVERNMENT OF INDIA ENTERPRISE)

# Item Rate Tender & Contract for Works

Tender for the Supply, Installation, Testing and Commissioning of Elevator system for Institute of Mental Health and Neurosciences (IMHANS),Calicut to be submitted by 15:00 hours on 05.02.2013  to Deputy General Manager (Technical), HLL Lifecare Ltd, Trivandrum – 695 006.

- To be opened in presence of tenderer who may be present at 15.30 hours on 05.02.2013 in the office of  Deputy General Manager (Technical), HLL Lifecare Ltd., Trivandrum – 695 006

Issued to:__________________________________________________________

(Contractor)

Signature of officer issuing the documents________________________________

Designation________________________________________________________

Date of Issue ______________________________________________________.

# T  E  N  D  E  R

I/We have read and examined notice inviting tender, schedule, A, B, C, D, E & F. specifications applicable, Drawings & Design, General Rules and Directions, Conditions of Contract, Clauses of Contract, Special conditions, Schedule of Rate & other documents and Rules referred to in the Conditions of Contract and all other contents in the tender document for the work.

I/We hereby tender for the execution of the work specified for the HLL Lifecare Ltd within the time specified in schedule ‘F’, in accordance in all respects with the specifications, designs, drawings and instructions in writing referred to in Rule-1 of General Rules and Directions and in Clause 11 of the Conditions of the contract and with such materials as are provided for, by and in respect in accordance with, such conditions so far as applicable.

We agree to keep the tender open for 120 days from the due date of submission thereof and not to make any modifications in its terms and conditions. If any tenderer withdraws his tender before the said period or issue of letter of acceptance/intent, whichever is earlier, or, makes any modifications in the terms and conditions of the tender which are not acceptable to HLL Lifecare Ltd., then HLL Lifecare Ltd shall, without prejudice to any other right or remedy, be at liberty to forfeit 50% of the said earnest money as aforesaid.

A sum of Rs. 1,38,120/- (Rupees One lakh Thirty eight Thousand one hundred and twenty only) has been deposited in the form of a Demand Draft or Fixed Deposit Receipt  or in the form of an irrevocable guarantee bond of any scheduled bank or State Bank of India and its associates issued in favour of HLL Lifecare Ltd as earnest money. If I/We fail to commence the work specified I/We agree that the said HLL Lifecare Ltd shall without prejudice to any other right or remedy, be at liberty to forfeit the said earnest money absolutely otherwise the said earnest money shall be retained by competent authority on behalf of the HLL Lifecare Ltd towards Security Deposit to execute all the works referred to in the tender documents upon the terms and conditions contained or referred to therein and carry out such deviations as may be ordered, upto maximum of the percentage mentioned in Schedule ‘F’ and those in excess of that limit at the rates to be determined in accordance with the provision contained in Clause 12.2 and 12.3 of the tender form.

I/We agree to deposit an amount equal to 5% of tendered value of the work as performance guarantee in the form of bond of any Scheduled Bank of India in accordance with the proforma prescribed  within 30 days of the issue of letter of acceptance of Tender by HLL Lifecare Ltd. I/We am/are aware that in the event of failure on my/our part to furnish the Bank Guarantee within 30 days, the earnest money will be forfeited and tender cancelled.

I/We hereby intimate that for receiving payments I/we have an account in  __________________ Bank with account No. _____________________ where the ECS/EFT facility of e-payment is available.

I/We hereby declare that I/We shall treat the tender documents drawings and other records connected with the work as secret/confidential documents and shall not communicate information derived there-from to any person other than a person to whom I/We am/are authorized to communicate the same or use the information in any manner prejudicial to the safety of the State.

I/We agree that should I/We fail to commence the work specified in the above memorandum, an amount equal to the amount of the earnest money mentioned in the form of invitation of tender shall be absolutely forfeited to the HLL Lifecare Ltd and the same may at the option of the competent authority on behalf of the HLL Lifecare Ltd be recovered without prejudice to any right or remedy available in law out of the deposit in so far as the same may extend in terms of the said bond and in the event of deficiency out of any other money due to me/us under this contract or otherwise.

The information in respect of works in hand is as per proforma enclosed.

Dated………………….

Witness:								     (___________________)

Address: 								       Signature of Contractor

Occupation:				Postal Address: -

****************************************

A C C E P T A N C E

The above tender (as modified by you (Contractor) and as provided in the letters mentioned hereunder) is accepted by me for and on behalf of the HLL Lifecare Ltd for a sum of

Rs.__________________________ (Rupees_________________________________________

______________________________________________________________________________)

The letters referred to below shall form part of this Contract Agreement:-

(a)

(b)

For & on behalf of the HLL Lifecare Ltd

Dated……………                  			                 Signature___________________________

Designation_________________________

| # PROFORMA OF SCHEDULES |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| (Operative Schedules to be supplied separately to each of the intending tenderer) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SCHEDULE “A” |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Schedule of Quantities (as per Part – II) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SCHEDULE “B” |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Schedule of Materials to be issued to the contractor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| S. No. |  | Description of Item |  |  |  |  |  | Quantity |  |  |  |  |  |  | Rates in figures & words at which the materials will be charged from the contractor |  |  |  |  |  |  |  |  |  |  | Place of issue |
| 1 |  | 2 |  |  |  |  |  | 3 |  |  |  |  |  |  | 4 |  |  |  |  |  |  |  |  |  |  | 5 |
| NIL |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| #### SCHEDULE “C” |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Tools and Plants to be hired to the contractor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| S. No. |  |  | Description of Item |  |  |  |  |  |  |  |  |  |  | Hire charges per day |  |  |  |  |  |  |  |  |  |  | Place of issue |  |
| 1 |  |  | 2 |  |  |  |  |  |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  |  |  | 4 |  |
| NIL |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SCHEDULE “D” |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Extra schedule for specific requirements/documents for the work. If any. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SCHEDULE “E” |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Schedule of component of Materials, Labour etc. for escalation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| CLAUSE 10 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Component of Materials expressed as percent of Total Value of Work |  |  |  |  |  |  |  |  |  |  | ### “X” |  |  |  |  |  |  |  |  |  |  | 75 % |  |  |  |  |
| Component of Labour expressed as percent of Total Value of Work |  |  |  |  |  |  |  |  |  |  | ### “Y” |  |  |  |  |  |  |  |  |  |  | 25 % |  |  |  |  |
| Component of POL expressed as percent of Total Value of Work |  |  |  |  |  |  |  |  |  |  | ### “Z” |  |  |  |  |  |  |  |  |  |  | 0 % |  |  |  |  |
| ## SCHEDULE “F” |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Reference to General Conditions of Contract |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Name of Work |  |  |  |  |  |  | Supply Installation Testing and Commissioning of Elevator system for Institute of Mental Health and Neurosciences (IMHANS),Calicut |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Estimated cost of Work |  |  |  |  |  |  |  |  |  | Rs.69,06,000/- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Earnest Money |  |  |  |  |  |  |  |  |  | Rs.1,38,120/- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Performance Guarantee (5% of the tendered value in the form of an irrevocable bank guarantee of any scheduled bank or State Bank of India in accordance with the form prescribed or in the form of Fixed Deposit Receipt etc within 30 days of issue of letter of indent / acceptance.) |  |  |  |  |  |  |  |  |  |  |  | Rs.____________________(Rupees____________ __________________________________________ ________________________________________________________________________________only) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Security Deposit (5 % of the tendered value to be submitted in the form of Bank Guarantee from Scheduled Bank or SBI by way of recovery from RA bills) |  |  |  |  |  |  |  |  |  |  |  | Rs.____________________(Rupees____________ __________________________________________ ________________________________________________________________________________only) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| #### GENERAL RULES AND DIRECTIONS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Officer inviting tender |  |  |  |  |  |  |  |  | Deputy General Manager (Technical), HLL Lifecare Ltd Trivandrum – 695 006. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Maximum percentage for quantity of items of work to be executed beyond which rates are to be determined in accordance with Clause 12.2 & 12.3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ----- 50% |  |  |  |  |  |  |  |
| Definitions |  |  |  |  |  |  |  |  |  |  |  |  | # See below |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2(v) |  | Engineer-in charge |  |  |  |  |  |  |  |  |  |  | Project Engineer or any officer nominated by HLL Lifecare Ltd |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2(viii) |  | Accepting Authority |  |  |  |  |  |  |  |  |  |  | Deputy General Manager (Technical), HLL Lifecare Ltd |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2(x) 2 (xi) |  | Percentage on cost of materials and labour to cover all overheads and profit Standard schedule of rates |  |  |  |  |  |  |  |  |  |  |  |  |  |  | … 10 % … CPWD SR 2012 for Building work CPWD SR 2012 for Internal Electrical Installation |  |  |  |  |  |  |  |  |  |
| 9(ii) |  | Standard HLL Lifecare Ltd Contract Form |  |  |  |  |  |  |  |  |  |  |  |  |  | … HLL Lifecare Ltd W - 8 form as modified and corrected upto date |  |  |  |  |  |  |  |  |  |  |
| ##### Clause 2 &2A |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Authority for fixing compensation under Clause 2 & 2A |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Competent Authority of HLL Lifecare Ltd |  |  |  |  |  |  |
| ##### Clause 5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| i) | Time allowed for execution of work. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 4 months |  |  |  |  |  |  |
| ii) | Authority to give fair and reasonable extension of time for completion of work. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Competent Authority of HLL Lifecare Ltd |  |  |  |  |  |  |
| ##### Clause 7 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Gross value of work to be done together with net payment /adjustment of advances for materials collected, if any, since the last such payment for being eligible to interim payment. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Rs. NA |  |  |  |  |  |  |
| ##### Clause 11 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Specification to be followed for execution of work. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CPWD 1996 (Civil) Vol. I to VII CPWD 2005 & 2007 (Electrical) |  |  |  |  |  |  |
| ##### Clause 12 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 12.1.2(iii) |  |  |  | Schedule of rates for determining the rates for additional, altered or substituted items that cannot be determined under 12.1.2(i) and (ii). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | CPWD SR 2012 (Civil) CPWD SR 2012 (Electrical) |  |  |  |  |  |  |
| 12.1.2(iii) |  |  |  | Plus/ minus the % over the rate entered in the schedule of rates. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 12.2 & 12.3 |  |  |  | Limit for value of any item of any individual trade beyond which sub clauses (i) to (v) shall not apply and clauses 12.2.& 12.3 shall apply |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ---- 50% |  |  |  |  |  |  |
| ##### Clause 16 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Competent authority for deciding reduced rates. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Competent Authority of HLL Lifecare Ltd |  |  |  |  |  |  |
| ##### Clause 25 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Competent authority for conciliation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Competent Authority of HLL Lifecare Ltd |  |  |  |  |  |  |
| ##### Clause 36(i) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| a) |  | Minimum qualification and experience of Principle Technical Representative for civil works with estimated cost put to tender. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| i) |  | Above Rs. 5 lakhs but less than Rs. 10 lakhs. |  |  |  |  |  |  |  |  |  |  |  |  | Recognized Diploma Holder in Civil Engineering |  |  |  |  |  |  |  |  |  |  |  |
| ii) |  | Rs. 10 lakhs and above but upto Rs. 60 lakhs. |  |  |  |  |  |  |  |  |  |  |  |  | Graduate Civil Engineer or retired AE (Civil) possessing at least recognized Diploma in Civil Engineering |  |  |  |  |  |  |  |  |  |  |  |
| iii) |  | Rs. 60 lakhs and above. |  |  |  |  |  |  |  |  |  |  |  |  | Principle Technical Representative supported by requisite organization. The Principle Technical Representative shall be at least a Graduate Civil Engineer with 5 years of minimum experience of works or retired Executive Engineer (Civil) possessing at least recognized Diploma in Civil Engineering |  |  |  |  |  |  |  |  |  |  |  |
| b) |  | Recovery to be affected from the contractor in the event of not fulfilling the provisions of clause 36(i). |  |  |  |  |  |  |  |  |  |  |  |  | Rs. 4000 per month for Graduate Engineer. Rs. 2000 per month for Diploma Holder. |  |  |  |  |  |  |  |  |  |  |  |
| Clause 42 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| i) (a) |  | Schedule / statement for determining theoretical quantities of cement on the basis of Delhi Schedule of Rates 2007 printed by CPWD. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ii) |  | Variation permissible on theoretical quantities |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| a) |  | Cement for works with estimated costs put to tender |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | i) not more than Rs. 5 lakhs |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 3 % minus |  |  |
|  |  | ii) more than 5 lakhs |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2 % minus |  |  |
| b) |  | Steel reinforcement and structural steel sections for each diameter, section and category. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2 % minus |  |  |

ADDITIONAL CONDITIONS

- The intending tenderers has to satisfy the provisions of EPF & Misc. Provisions Act 1952 & Employees’ Provident Fund Scheme 1952, by the contractors in respect of labourers/Employees engaged by them for performing the works of HLL.

- Each claim bill of contractors must accompany the (I) list showing the details of labourers/employees engaged.  (II) duration of their engagement (III) the amount of wages paid to such labourers/employees for the duration in question, (IV) amount of EPF contributions (both employer’s & employees’ contribution) for the duration of engagement in question, paid to the EPF authorities, (V) copies of authenticated documents of payments of such contribution to EPF authorities and (VI) a declaration from the contractors regarding compliance of the conditions of EPF Act, 1952.

- The contractors claim will be passed by the bill passing authority only if the contractor complies with the terms and conditions of EPF Act, 1952.

- “Cess under Building and Other Construction Workers’ Welfare Cess Act, 1996 and Building and Other Construction Workers Cess Rules 1998

Notwithstanding anything contained in this contract, Cess at the rate stipulated under Clause 3(1) of the Building and other construction workers’ Welfare Cess Act 1996, shall be recovered from the gross amount of the bill/bills payable under this Contract”.

- Work Contract Tax, Service Tax and Income Tax at the rate applicable shall be recovered from the gross amount of the bill/bills payable under the contract.

##### CONTRACTOR                                      	  Deputy General Manager (Technical)

#### HLL Lifecare Limited

THIRUVANANTHAPURAM – 695 006

PROFORMA FOR AGREEMENT

(ON NON-JUDICIAL STAMP PAPER OF APPROPRIATE VALUE)

CONTRACT AGREEMENT FOR THE WORK OF ----------------------------------------DATED--------- Between M/s------------------------------------------------------ (refer note) in the town of ___________ hereinafter called the contractor (which term shall unless excluded by or repugnant to be subject or context include its successors and permitted assigns) of the one part and the HLL Lifecare Limited hereinafter called the HLL (which term shall unless excluded by or repugnant to the subject or context include its successes and assigns) of the other part.

WHEREAS

  - The HLL is desirous that the ………. of ___________________ ___________ at __________ should be executed as mentioned, enumerated or referred to in the tender including Press Notice Inviting Tender, General Conditions of the Contract, Special Conditions of the Contract, Specifications, Drawings, Plans, Time Schedule of completion of jobs, Schedule of Quantities and Rates, Agreed Variations, other documents, has called for Tender.

  - The contractor has inspected the site and surroundings of the work specified in the tender documents and has satisfied himself by carefully examination before submitting his tender as to the nature of the surface, strata, soil, sub-soil and grounds, the form and nature of the site and local conditions the quantities, nature and magnitude of the work the availability of labour and materials necessary for the execution of work, the means of access to site, the supply of power and water thereto and the accommodation he may require and has made local and independent enquiries and obtained complete information as to the matters and things referred to or implied in the tender documents or having any connection therewith, and has considered the nature and extent of all the probable and possible situations, delays, hindrances or interferences to or with the execution and completion of the work to be carried out under the contract, and has examined and considered all other matters, conditions and things and probable and possible contingencies, and generally all matters incidental thereto  and ancillary thereof affecting the execution and completion of the work and which might have influenced him in making his tender.

  - The tender documents including the HLL’s Press Notice Inviting Tender, General conditions of contract, Special Conditions of Contract, Schedule of Quantities and rates, General obligations, Specifications, Drawings, plan, time schedule for completion of work.  Letter of Acceptance of tender and any statement of agreed variations with its enclosures copies of which are hereto annexed form part of this contract though separately set out herein and are included in the expression Contract wherever herein used.

AND WHEREAS

The HLL accepted the tender of M/s -----------------------------------------(refer note below) (Contractor) for the----------------- of ----------------------------------------------- at ---------------and conveyed vide letter No.--------------------------dated --------------at the rates stated in the Schedule of quantities for the work and accepted by the HLL (hereinafter called the Schedule of Rates) upon the terms and subject to the conditions of the contract.

NOW THIS AGREEMENT WITNESSTH & IT IS HEREBY AGREED AND DECLARED AS FOLLOWS.

- In consideration of the payment to be made to the contract for the work to be executed by him, the contractor hereby covenant with the HLL that the contractor shall and will duly provide, execute, complete and maintain the said work and shall do and perform all other acts and things in the contract mentioned or described or which are to be implied and there-from or may be reasonably necessary for the completion of the said works and at the said times and in the manner and subject to the terms and conditions or stipulations mentioned  in the contract,  AND

- In consideration of the due provisions execution, completion and maintenance of the said work, the HLL does hereby agree with the contractor that the HLL will pay to contractor the respective amounts for the work actually done by him and approved by the HLL at the Schedule or Rates and such other sum payable to the contractor under provision of the contract, such payment to be made at such time in such manner as prescribed for in the contract.

It is specifically and distinctly understood and agreed between the HLL and the contractor that the contractor shall have no right, title or interest in the site made available by the HLL for execution of the works or in the building, structures or works executed on the said site by the contractor or in the goods, articles, materials, etc. brought on the said site (unless the same specifically belongs to the contractor) and the contractor shall not have or deemed to have any lien whatsoever charge for unpaid bills will not be entitled to assume or retain possession or control of the site or structures and the HLL shall have an absolute and unfettered right to take full possession of site and to remove the contractor, their servants, agents and materials belonging to the contractor and lying on the site.

In Witness whereof the parties hereto have here-into set their respective hands and seals in the day and the year first above written.

| Signed and delivered for and on behalf of HLL | Signed and delivered for and on behalf of the contractor |
| --- | --- |
| (HLL LIFECARELIMITED) | (Contractor) |
| OFFICIAL ADDRESS |  |
| Date | Date |
| Place | Place |
| IN PRESENCE OF TWO WITNESSES |  |
| SIGNATURE | SIGNATURE |
| NAME | NAME |
| SIGNATURE | SIGNATURE |
| NAME | NAME |

NOTE

For Proprietary Concern

Shri……………………s/o…………………………r/o……………………..carrying on business under the name and style of………………at………………. (hereinafter called the said Contractor which expression shall unless the context requires otherwise include his heirs, executors, administrators  and legal representatives).

For Partnership Concern

M/s ………………………………….a partnership firm having its registered office at ………………………..(hereinafter called the said Contractor which expression shall unless the context requires otherwise include his heirs, executors, administrators and legal representatives).  The partners of the firms are:

- Shri ………………………………….s/o………………………… , And

- Shri ……………………………..s/o………………………..etc..

For Companies

# M/s …………………………………a company duly incorporated under the Indian Companies Act, 1956 and having its registered office at …………………………..in the state of ………………………….(hereinafter called the said Contractor which expression shall unless the context requires otherwise include its successors and assign).

FORM OF PERFORMANCE SECURITY

BANK GUARANTEE BOND

      - In consideration of the HLL Lifecare Limited (hereinafter called “HLL”) having agreed under the terms and conditions of agreement NO…………….. dated…………. made between ………………………… and ……………………….. (herein after called “the said contractor(s)”) for the …………….. work (herein after called “the said agreement”) for compliance of his obligation in accordance with the terms and conditions in the said agreement.

We …………….. (indicate the name of the Bank) (herein after referred to as “as Bank) hereby undertake to pay to the HLL and amount not exceeding Rs….. (Rupees………….. only) on demand by the HLL.

      - We …………………………….. (Indicate the name of the Bank) do hereby undertake to pay the amount due and payable under this Guarantee without any demure, merely on a demand from the HLL stating that the amount claimed is required to meet the recoveries due or likely to be due from the said contractor(s).  any such demand made on the Bank shall be conclusive as regards the amount due and payable by the bank under this Guarantee.  However, our liability under this guarantee shall be restricted to an amount not exceeding Rs…………… (Rupees………………………… only).

      - We undertake to pay to the HLL any money so demanded notwithstanding any dispute or disputes raised by the contractor (s) in any suit or proceeding pending before any court or Tribunal relating therto our liability under this present being absolute and unequivocal.

The payment made by us under this bond shall be valid discharge of our liability for payment to there-under and the contractor(s) shall have no claim against us making such payment.

      - We …………….. (Indicate the name of Bank) further agree that the guarantee herein contained shall remain in full force and effect during the period that would be taken for the performance of the said agreement and that it shall continue to be enforceable till all the dues of the HLL under or by virtue of the said agreement have been fully paid and it is claims satisfied or discharged or till Engineer-in-charge on behalf of the HLL. Certified that he terms and conditions of the said Agreement have been fully and properly carried out by the said contractor(s) accordingly discharges this guarantee.

      - We……………. (Indicate the name of Bank) further agree with the HLL that he HLL shall have the fullest liberty without our consent and without affecting any manner our obligations hereunder to vary any of the terms and conditions of the said agreement or to extend time of performance by the said contractor(s) from time to time or to postpone for any of the powers exercisable by the HLL against the said contractor(s) and to forebear or enforce any of the terms and conditions relating to the said agreement we shall not be relieved from our liability by reasons of any such variation or extension being granted to the said contractor(s) or for ay forbearance act to omission on that part of the HLL or any indulgence by HLL to the said contract(s) or by any such matter or thing whatsoever which under the law relating to sureties would, but for this provision, have effected or so relieving us.

      - The guarantee will not be discharged due to the change in the constitution of the Bank or the contractor(s).

      - We…………………………… (indicate the name of Bank) lastly undertake not to revoke this guarantee except with the previous consent of the HLL in writing.

      - This guarantee shall be valid upto ……….. unless extended on demand by HLL.  Not withstanding any thing mentioned above our liability against this Guarantee is restricted to Rs…………. (Rupees…………………only) and unless a claim in writing is lodged with us within six months of the date of expiry or the extended date of expiry of this guarantee, all our liabilities under the Guarantee shall stand discharged.

Dated the ………….. day of 20….

For ………………………………

(Indicate the name of Bank)

# AFFIDAVIT

I/We have submitted a bank guarantee for the work …………………………………. ……………………………. (Name of Work), Agreement No…………………. .. Dated:………….. from………………………………………………………………….. (Name of the bank with full address)

TO THE DEPUTY GENERAL MANAGER (TECHNICAL)……………………………………………… with a view to seek exemption from payment of performance guarantee in cash. This Bank guarantee expired on ……………………………

I /We undertake to keep the validity of the bank guarantee intact by getting it extended from time to time at my/our own initiative upto a period of ………………………….. months after the recorded date of completion of the work or as directed by the Engineer in charge.

I / WE also indemnify the HLL Lifecare Limited against any losses arising out of non-encashment of the bank guarantee if any.

(Deponent)

signature of Contractor

note : The affidavit is to be given by the Executants before a first class Magistrate.

FORM OF BANK GUARANTEE FOR EARNEST MONEY DEPOSIT

1.	KNOW ALL MEN by these presents that we ………………………………….…... (Name of Bank) having our registered office at ……………………… (Name of country) (hereinafter called “the Bank”) are bound unto HLL Lifecare Limited (hereinafter called “HLL”) in the sum of Rs. ____ for which payment will and truly to be made to the said HLL, the Bank binds itself, its successors and assigns by these presents.

2.	WHEREAS…………………………(Name of Tenderer) (hereinafter called “the Tenderer”) has submitted its tender dated__________for (Name of the work as mentioned under Clause 1 of NIT) hereinafter called the tender.

AND WHEREAS the Tenderer is required to furnish a Bank Guarantee for the sum of Rs _____ (____) as Tender Security against the Tenderer’s offer as aforesaid.

AND WHEREAS_______________(Name of Bank) have, at the request of the Tenderer, agreed to give this guarantee as hereinafter contained.

3.	We further agree as follows:

a.	That HLL may without affecting this guarantee grant time or other indulgence to or negotiate further with the Tenderer in regard to the conditions contained in the said tender and thereby modify these conditions or add thereto any further conditions as may be mutually agreed upon between HLL and the Tenderer.

b.	That the guarantee hereinbefore contained shall not be affected by any change in the constitution of our Bank or in the constitution of the Tenderer.

c.	That any account settled between HLL and the Tenderer shall be conclusive evidence against us of the amount due hereunder and shall not be questioned by us.

d.	That this Guarantee commences from the date hereof and shall remain in force till       _________(date to be filled up)  (up to 150 days from the last date of submission of tender).

- That the expression ‘the Tenderer’ and ‘the Bank’ herein used shall, unless such an interpretation is repugnant to the subject or context, include their respective successors and assigns.

4.	THE CONDITIONS OF THIS OBLIGATION ARE:

a.	if the Tenderer withdraws his Tender during the period of Tender validity specified in Clause 16 of Notice Inviting Tender, or

b.	if the Tenderer having been notified of the acceptance of his tender by HLL during the period of tender validity :

i.	fails or refuses to furnish the Performance Security in accordance with Clause 9 of Notice Inviting Tender and/or

ii.	fails or refuses to enter into a Contract within the time limit specified in Clause 17 of Notice Inviting Tender.

We undertake to pay to HLL upto the above amount upon receipt of his first written demand, without HLL having to substantiate his demand provided that in his demand HLL will note that the amount claimed by him is due to him owing to the occurrence of any one or more of the conditions (a) & (b), mentioned above, specifying the occurred condition or conditions.

|  | Signature of …………………………. Authorized Official of the Bank |
| --- | --- |
| Signature of the witness ……………………………………. | Name of Official …………………….. Designation ………………………….. |
| Name of the Witness ……………………………………. | Stamp/Seal of the Bank …………………………… |
| Address of the Witness ……………………………………. |  |

CLAUSES OF CONTRACT

CLAUSE 1

  - The contractor shall submit an irrevocable Performance Guarantee of 5% (Five percent) of the tendered amount in addition to other deposits mentioned elsewhere in the contract for his proper performance of the contract agreement, (not withstanding and/or without prejudice to any other provisions in the contract) within period specified in Schedule F from the date of issue of letter of acceptance. This period can be further extended by the Engineer-in-Charge upto a maximum period as specified in Schedule F on written request of the contractor stating the reason for delays in procuring the Bank Guarantee, to the satisfaction of the Engineer-in-Charge. This guarantee shall be in the form of a Bank Guarantee of a Scheduled Bank or State Bank of India.

  - The Performance Guarantee shall be initially valid upto the stipulated date of completion plus 60 days beyond that. In case the time for completion of work gets enlarged, the contractor shall get the validity of the Performance Guarantee extended to cover such enlarged time for completion of work. After recording the completion certificate for the work by the competent authority, the performance guarantee shall be returned to the contractor, without any interest.

  - The Engineer-in- Charge shall not make a claim under the performance guarantee except for amounts to which HLL is entitled under the contract (not withstanding and/or without prejudice to any other provisions in the contract agreement) in the event of:

a) Failure by the contractor to extend the validity of the Performance Guarantee as described herein above, in which event the Engineer-in-Charge may claim the full amount of the Performance Guarantee.

  - Failure by the contractor to pay HLL any amount due, either as agreed by the contractor or determined under any of the Clauses/Conditions of the agreement, within 30 days of the service of notice to this effect by the Engineer-in-Charge.

- In the event of the contract being determined or rescinded under provision of any of    the Clause/Condition of the Agreement, the performance guarantee shall stand forfeited in full and shall be absolutely at the disposal of the President of India.

CLAUSE 1 A

Recovery of Security Deposit

DELETED

CLAUSE 2

If the contractor fails to maintain the required proportionate progress of the work at the stages specified in Clause 5 or to complete the work and fails to clear the site on or before the contract or extended date of completion, he shall, without prejudice to any other right or remedy available under the law to the HLL on account of such breach, pay as agreed compensation the amount calculated at the rates stipulated below or such smaller amount as the authority specified in Schedule ‘F’ may decide on the  amount of tendered value of work for every completed day/week (as applicable)in which the progress remains below than the specified in Clause 5 or that the work remains incomplete.  The decision of the aforesaid authority in writing shall be final and binding on the contractor.

Compensation for Delay

This will also apply to items or group of items for which separate period of completion has been specified.

| (i) Compensation for delay of work | @1.5% per month of delay to be computed on per day basis |
| --- | --- |
| The table of milestones has to be jointly prepared by the Engineer in Charge and the contractor within 20 days of issue of LOA and this table showing milestones will form part of agreement. Wherever physical milestones are not specified, the financial milestone table shown below will be in force. TABLE SHOWING PHYSICAL MILE STONES S. No.; Description of Milestone (Physical); Time allowed in days (from date of start); Amount to be with-held in case of non achievement of milestone. 1.; In the event of not achieving a milestone in time, 1.25% of the tendered value of work will be withheld for failure of achieving each mile stone.. 2.. Etc... OR (In cases where physical milestones are not specified) TABLE SHOWING FINANCIAL MILE STONES S. No.; Financial Progress; Time Allowed (From date of Start); Amount to be with-held in case of non achievement of milestone. 1; 1/8th (of the whole work); 1/4th (of the completion period); In the event of not achieving the necessary progress as assessed from the running payments, 1.25% of the tendered value of work will be withheld for failure of each mile stone.. 2; 3/8th (-do-); 1/2 (-do-). 3; 3/4th (-do-); 3/4th (-do-). 4; full; full. |

Provided always that the total amount of compensation for delay to be paid under this condition shall not exceed 10 % of the tendered value of work or of the Tendered Value of the item or group of items of work for which a separate period of completion is originally given. In case, the contactor does not achieve a particular milestone, or the re-scheduled milestone(s) in terms of Clause 5.4 the amount shown against that milestone shall be withheld, to be adjusted against the compensation levied at the finial grant of Extension of Time. With-holding of this amount on failure to achieve a milestone, shall be automatic without any notice to the contractor. However, if the contractor catches up with the progress of work on the subsequent milestone(s), the withheld amount shall be released. In case the contractor fails to make up for the delay in subsequent milestone(s), amount mentioned against each milestone missed subsequently also shall be withheld. However, no interest whatsoever, shall be payable on such withheld amount. The amount of compensation may be adjusted or set-off against any sum payable to the Contractor under this or any other contract with the HLL.

CLAUSE 3

If the Contractor:

When Contract can be Determined

- Having been given by the Engineer-in-Charge a notice in writing to rectify, reconstruct or replace any defective work or that the work is being performed in an inefficient or otherwise improper or unworkmanlike manner, shall omit to comply with the requirements of such notice for a period of seven days thereafter; or,

- has without reasonable cause suspended the progress of the work or has failed to proceed with the work so that in the opinion of the Engineer-in-Charge(which shall be final and binding) that he will be unable to secure completion of the work by the date for completion and continues to do so after a notice in writing of seven days from the Engineer-in-Charge; or

- persistently neglects to carry out his obligations under the contract and/or commits default in complying with any of the terms and conditions of the contract and does not remedy it or take effective steps to remedy it within 7 days after a notice in writing is given to him in that behalf by the Engineer-in-Charge; or

- fails to complete the work within the stipulated date or items of work with individual date of completion, if any, stipulated on or before such date(s)of completion and does not complete them within the period specified in the notice given in writing in that behalf by the Engineer-in-Charge; or

- being a company shall pass a resolution or the court shall make an order that the company shall be wound up or if a receiver or a manager on behalf of a creditor shall be appointed or if circumstances shall arise which entitle the court or the creditor to appoint a receiver or a manager or which entitles the court to make a winding up order; or

vi)	Commits any act/acts mentioned in Clause 21 hereof:

THEN the Engineer-in-Charge may, without prejudice to his rights against the Contractor in respect of any delay or inferior workmanship or otherwise or to any claims for damage in respect of any breach of the Contract and in addition to any right or remedies under any of the provisions of the Contract or otherwise and whether the date for completion has or has not elapsed, shall by a notice in writing, has powers to take recourse to any one or more of the following.

- To determine or rescind the contract (of which termination or rescission notice in writing to the contractor under the hand of the Engineer-in–Charge shall be conclusive evidence). Upon such determination or rescission, the security deposit of the contractor shall be liable to be forfeited and shall be absolutely at the disposal of the HLL.

- To employ labour and to supply materials to carry out the work or any part of the work debiting the contractor with the cost of the labour and the price of the materials (of the amount of which cost and price certified by the Engineer-in-Charge shall be final and conclusive against the contractor) and crediting him with the value of the work done in all respects in the same manner and at the same rates as if it had been carried out by the Contractor under the terms of his contract. The certificate of the Engineer-in-Charge as to the value of the work done shall be final and conclusive against the contractor provided always that action under the sub clause shall only be taken after giving notice in writing to the contractor. Provided also that if the expenses incurred by the HLL are less than the amount payable to the contractor at his agreement rates, the difference shall not be paid to the contractor.

- After giving notice to the contractor to measure up the work of the contractor and to take such part thereof as shall be unexecuted out of his hands and to give it to another contractor to complete, in which case any expenses which may be incurred in excess of the sum which would have been paid to the original contractor if the whole work had been executed by him (the certificate in writing of the Engineer-in-Charge for the amount which exceeds the amounts contracted for the unexecuted/imperfectly executed items shall be final and conclusive) shall be borne and paid by the original contractor and may be deducted from any money due to him by the HLL under the contract or on any other account whatsoever or from his Security Deposit or the proceeds of sales thereof, or a sufficient part thereof as the case may be. If the expenses incurred by the HLL are less than the amount payable to the contractor at his agreement rates, the difference shall not be paid to the contractor.

In the event of anyone or more of the above course or courses being adopted by the Engineer-in-charge, the contractor shall have no claim to compensation for any loss sustained by him by reasons of his having purchased or procured any materials or entered into any engagements or made any advances on account or with a view to the execution of the work or the performance of the contract. In case action is taken under any of the provisions aforesaid, the contractor shall not be entitled or be paid any sum for any work unless and until the Engineer-in-Charge has certified in writing the performance of such work and the value payable in respect thereof and he shall only be entitled to be paid the value so certified.

Provided further that, if any of the recoveries to be made, while taking action as per (b) and/or (c) above, are in excess of the Security Deposit, these shall be limited to the amount by which the excess cost incurred by the HLL exceeds the Security Deposit so forfeited.

CLAUSE 4

Contractor Liable to pay Compensation even if action not taken under Clause 3

In case in which any of the powers conferred upon the Engineer-in-Charge by Clause-3 thereof, shall have become exercisable and the same are not exercised, the non-exercise thereof, shall not constitute a waiver of any of the conditions hereof and such powers shall notwithstanding be exercisable in the event of any future case of default by the contractor and the liability of the contractor for compensation shall remain unaffected. In the event of the Engineer-in-Charge putting in force all or any of the powers vested in him under the preceding clause he may, if he so desires after giving a notice in writing to the contractor, take possession of (or at the sole discretion of the Engineer-in-Charge which shall be final and binding on the contractor) use as on hire (the amount of the hire money being also in the final determination of the Engineer-in-Charge) all or any tools, plants, materials and stores, in or upon the works, or the site thereof belonging to the contractor, or procured by the contractor and intended to be used for the execution of the work or any part thereof, paying or allowing for the same in account at the contract rates, or in the case of these not being applicable, at current market rates to be certified by the Engineer-in-Charge, whose certificate thereof shall be final and binding on the contractor, otherwise the Engineer-in-Charge by notice in writing may order the contractor or his clerk of the works, foreman or other authorised agent to remove such tools, plants, materials or stores from the premises (within a time to be specified in such  notice) in the event of the contractor failing to comply with any such requisition, the Engineer-in-Charge may remove them at the contractor’s expense or sale them by auction  or private sale on account of the contractor and his risk in all respects and the certificate of the Engineer-in-Charge, as to the expenses of any such removal and the amount of the proceeds and expense of any such sale, shall be final and conclusive against the contractor.

CLAUSE 5

Time and Extension for Delay

The time allowed for execution of the works specified in the Schedule ‘F’ or the extended time in accordance with these conditions shall be the essence of the contract. The execution of the work shall commence from the 15th day or such time period, as mentioned in letter of award, after the date of acceptance of the tender, if the contractor commits default in commencing the execution of the work as aforesaid, HLL shall without prejudice to any other right or remedy available in law, be at liberty to forfeit the Earnest Money absolutely.

  - To ensure good progress during the execution of the work, the contractor shall in all cases in which the time allowed for any work, exceeds one month (save for special jobs for which a separate programme has been agreed upon) complete 1/8th of the whole of work before 1/4th of the whole time allowed in the contract has elapsed, 3/8th of the work before one half of such time has elapsed and 3/4th of the work before 3/4th of such time has elapsed.

    - Further, in case of works estimated to cost above Rs.10 Lakhs, the contractor shall, as soon as the contract is awarded, submit a time and progress chart and get it approved by the Engineer-in-Charge. The chart shall be prepared in direct relation to the time stipulated in the contract document and to achieve proportionate progress at the stages specified above and shall indicate the forecast of the dates of the commencement and completion of various trade sections of the work. The progress chart may be amended as necessary by agreement between the Engineer-in-Charge and the contractor within the aforesaid limitations of the time allowed for completion of the work and proportionate progress.

  - If the work(s) be delayed by:-

- force majeure, or

- abnormally bad weather, or

- serious loss or damage by fire, or

- civil commotion, local commotion of workmen, strike or lockout, affecting any of the trades employed on the work, or

- delay on the part of other contractors or tradesmen engaged by the Engineer-in-Charge in executing work not forming part of the Contract, or

- non-availability of stores, which are the responsibility of the HLL to supply, or

- non-availability or break down of tools and Plant to be supplied or supplied by HLL, or

- any other cause which, in the absolute discretion of the authority mentioned in the Schedule ‘F’, is beyond the Contractor’s control,

Then upon the happening of any such event causing delay, the Contractor shall immediately give notice thereof, in writing to the Engineer-in-Charge, but shall nevertheless use constantly his best endeavours to prevent or make good the delay and shall do all that may be reasonably required to the satisfaction of the Engineer-in-Charge to proceed with the works.

  - Request for extension of time, to be eligible for consideration, shall be made by the Contractor in writing within fourteen days of the happening of the event causing delay on the prescribed form. The Contractor may also, if practicable, indicate in such a request the period for which extension is desired.

  - In any such case the authority mentioned in Schedule ‘F’ may give a fair and reasonable extension of time for completion of work. Such extension shall be communicated to the Contractor by the Engineer-in-Charge in writing, within 3 months of the date of the receipt of such request. Non application by the contractor for extension of time shall not be a bar for giving a fair and reasonable extension by the Engineer-in-Charge and this shall be binding on the contractor.

CLAUSE 6

Engineer-in-Charge shall, except as otherwise provided, ascertain and determine by measurements the value of work done in accordance with the contract. The measurements of all items (having financial value) shall be entered in Measurement Book and/or level field book so that a complete record is maintained of all works performed under the contract.

Measurements of Work Done

All measurements and levels shall be taken jointly by the Engineer-in-Charge or his authorised representative and by the contractor or his authorised representative from time to time during the progress of the work and such measurement shall be signed and dated by the Engineer-in-Charge and the contractor(s) or his/their representative in token of their acceptance. If the contractor objects to any of the measurements recorded, a note shall be made to that effect with reasons and signed by both the parties.

If for any reason the contractor or his authorised representative is not available and the work of recording measurements is suspended by the Engineer-in-Charge or his representative, the Engineer-in-Charge and the HLL shall not entertain any claim from contractor for any loss or damages on this account. If the contractor or his authorised representative does not remain present at the time of such measurements after the contractor or his authorised representative has been given a notice in writing three (3) days in advance or fails to countersign or to record objection within a week from the date of the measurement, then such measurements recorded in his absence by the Engineer-in-Charge or his representative shall be deemed to be accepted by the Contractor.

The contractor shall, without extra charge, provide all the assistance with every appliance, labour and other things necessary for measurements and recording levels. Except where any general or detailed description of the work expressly shows to the contrary, measurements shall be taken in accordance with the procedure set forth in the specifications notwithstanding any provision in the relevant Standard Method of the measurement or any general or local custom. In the case of items, which are not covered by specifications, measurements shall be taken in accordance with the relevant standard method of measurement issued by the Bureau of Indian Standards and if for any item no such standard is available then a mutually agreed method shall be followed. The contractor shall give not less than seven day’s notice to the Engineer-in-Charge or his authorised representative in-charge of the work before covering up or otherwise placing beyond the reach of measurement any work in order that the same may be measured and correct dimensions thereof be taken before the same is covered up or placed beyond the reach of measurements and shall not cover-up and place beyond reach of measurement any work without consent in writing of the Engineer-in-Charge or his authorised representative in-charge of the work who shall within the aforesaid period of seven days inspect the work, and if any work shall be covered up or placed beyond the reach of the measurements without such notice having been given or the Engineer-in-Charge’s consent being obtained in writing, the same shall be uncovered at the Contractor’s  expense, or in default thereof, no payment or allowance shall be made for extra work or the materials with which the same was executed.

Engineer-in-Charge or his authorised representative may cause, either themselves or through another Officer of the HLL, to check the measurements recorded, jointly or otherwise, as aforesaid, and all provisions stipulated herein above shall be applicable to such checking of measurements or levels.

It is also a term of this contract that recording of measurements of any item of work in the measurement book and/or its payment in the interim, on account or final bill, shall not be considered as conclusive evidence as to the sufficiency of any work or material to which it relates nor shall it relieve the contractor from liabilities from any over measurement or defects noticed till completion of the defects liability period.

CLAUSE 7

Payment on Intermediate Certificate to be regarded as Advances

Interim or running account bills shall be submitted by the contractor for the work executed on the basis of such recorded measurements on the format of the HLL in triplicate on or before the date of every month fixed for the same by the Engineer-in-Charge. The contractor shall not be entitled to be paid any such interim payment if the gross work done together with net payment/adjustment of advances for material collected, if any, since the last such payment is less than the amount specified in Schedule “F’, in which case the interim bill shall be prepared on the appointed date of the month after the requisite progress is achieved. Engineer-in-Charge shall arrange to have the bill verified by taking or causing to be taken, where necessary, the requisite measurements of the work. In the event of the failure of the contractor to submit the bills, Engineer-in-Charge shall prepare or cause to be prepared such bills in which event no claims whatsoever due to delays on payment including that of interest shall be payable to the contractor. Payment on account of amount admissible shall be made by the Engineer-in- Charge certifying the sum to which the contractor is considered entitled by way of interim payment at such rates as decided by the Engineer-in-Charge. The amount admissible will as far as possible be paid by 10th working day after the day of presentation of the bill by the Contractor to the Engineer-in-Charge or his Asstt. Engineer together with the account of the material issued by the HLL, or dismantled materials, if any. In the case of works outside the headquarter of the Engineer-in-Charge, the period of ten working days will be extended to fifteen working days.

All such interim payments shall be regarded as payment by way of advances against final payment only, and shall not preclude the requiring of bad, unsound and imperfect or unskilled work to be rejected, removed, taken away and reconstructed or re-erected. Any certificate given by the Engineer-in-Charge relating to the work done or materials delivered forming part of such payment, may be modified or corrected by any subsequent such certificate(s) or by the final certificate and shall not by itself be conclusive evidence that any work or materials to which it relates is/are in accordance with the contract and specifications. Any such interim payment, or any part thereof shall not in any respect conclude, determine or affect in any way powers of the Engineer-in-Charge under the contract or any of such payments be treated as final settlement and adjustment of accounts or in any way vary or affect the contract.

Pending consideration of extension of date of completion interim payments shall continue to be made as herein provided, without prejudice to the right of the HLL to take action under the terms of this contract for delay in the completion of work, if the extension of date of completion is not granted by the competent authority.

The Engineer-in-Charge in his sole discretion, on the basis of a certificate from the Site Engineer to the effect, that the work has been completed upto the level in question may make interim advance payments without detailed measurements for work done (other than foundations, items to be covered under finishing items) upto lintel level (including sunshade etc.) and slab level, for each floor working out at 75% of the assessed value. The advance payments so allowed shall be adjusted in the subsequent interim bill by taking detailed measurements thereof.

CLAUSE 8

Completion Certificate & Completion Plans

With in ten days of the completion of the work, the contractor shall give notice of such completion to the Engineer-in-Charge and within thirty days of the receipt of such notice the Engineer-in-Charge shall inspect the work and if there is no defect in the work, shall furnish the contractor with a final certificate of completion, otherwise a provisional certificate of physical completion indicating defects (a) to be rectified by the contractor and/or (b) for which payment will be made at reduced rates, shall be issued. But no final certificate of completion shall be issued, nor shall the work be considered to be complete until the contractor shall have removed from the premises on which the work shall be executed all scaffolding, surplus materials, rubbish and all huts and sanitary arrangements required for his/their work people on the site in connection with the execution of the works as shall have been erected or constructed by the contractor(s) and cleaned off the dirt from all wood work, doors, windows, wall, floor or other parts of the building,  in, upon, or about which the work is to be executed or of which he may have had possession, for the purpose of the execution thereof, and not until the work shall have been measured by the Engineer-in-Charge. If the contractor shall fail to comply with the requirements of this clause, as to removal of scaffolding, surplus materials and rubbish and all huts and sanitary arrangements as aforesaid and cleaning off dirt on or before the date fixed for the completion of work, the Engineer-in-Charge may at the expense of the contractor remove such scaffolding, surplus materials and rubbish etc., and dispose of the same as he thinks fit and clean off such dirt as aforesaid, and the contractor shall have no claim whatsoever in this regard except for any sum actually realised by the sale thereof.

CLAUSE 8 A

Contractor to Keep Site Clean

When the annual repairs and maintenance of works are carried out, the splashes and dropping from white washing, colour-washing, painting etc, on walls, floor, windows, etc. shall be removed and the surface cleaned simultaneously with the completion of these items of work in the individual rooms, quarters or premises etc where the work is done without waiting for the actual completion of all the other items of work in the contract. In case the contractor fails to comply with the requirement of this clause, the Engineer-in-Charge shall have the right to get this work done at the cost of the contractor either by HLL or through any other agency. Before taking such action, the Engineer-in-Charge shall give 10 days notice in writing to the contractor.

CLAUSE 8 B

The Contractor shall within one month of the date of completion of the work submit

Completion Plans to be Submitted by the Contractor

- completion plan as required vide General Specification for Electrical works (Part I Internal) 1972 and (Part-II External) 1974, as applicable,

- completion plans of internal and external sanitary, water supply and drainage installations by marking on a set of drawings , the route, position and details of the pipes, fixtures, fittings in the manner specified by the Engineer-in-Charge.

The Contractor shall also arrange statutory inspection and certification of the aforesaid installation by local authorities in conformity with the bylaws, if any.

If the contractor fails to submit the completion plans and obtain necessary statutory certificates from the local authority as aforesaid he shall be liable to indemnify by a sum equivalent to, spent by the HLL for preparation of the completion plans and in obtaining necessary statutory certificates as aforesaid.

CLAUSE 9

Payment of Final Bill

The contractor shall submit the final bill in the same manner as specified in interim bills within one month of the date of the final certificate of completion furnished by the Engineer-in-Charge. No further claims shall be made by the contractor after submission of the final bill and these shall be deemed to have been waived and extinguished. Payments of those items of the bill in respect of which there is no dispute and of items in dispute, for quantities and rates as approved by the Engineer-in-Charge, will, as far as possible, be made within six months, the period being reckoned from the date of receipt of the bill by the Engineer-in-Charge, complete with account of materials issued by the HLL and dismantled materials.

CLAUSE 9A

Payments due to the contractor may, if so desired by him, be made to his bank instead of direct to him provided that the contractor furnishes to the Engineer-in-Charge

Payment of Contractor’s Bill to Banks

- an authorisation in the form of a legally valid document such as a power of attorney conferring authority on the bank to receive payments, and,

- his own acceptance of the correctness of the amount made out as being due to him by HLL or his signature on the bill or other claim preferred against HLL before settlement by the Engineer-in-Charge of the account or claim by payment to the bank.  While the receipt given by such banks shall constitute a full and sufficient discharge for the payment, the contractor shall wherever possible present bills duly receipted and discharged through his bankers.

Nothing herein contained shall operate to create in favour of the bank any rights or equities vis-à-vis the HLL LifecareLtd.

CLAUSE 10

The contractor shall, at his own expense, provide all materials, required for the works.

Materials to be provided by the Contractor

The contractor shall, at his own expense and without delay, supply to the Engineer-in-Charge samples of materials to be used on the work and shall get these approved in advance. All such materials to be provided by the Contractor shall be in conformity with the specifications laid down or referred to in the contract. The contractor shall, if requested by the Engineer-in-Charge, furnish proof, to the satisfaction of the Engineer-in-Charge that the materials so comply. The Engineer-in-Charge shall within thirty days of supply of samples or within such further period as he may require, intimate to the Contractor in writing whether samples are approved by him or not. If samples are not approved, the Contractor shall forthwith arrange to supply to the Engineer-in-Charge for his approval fresh samples complying with the specifications laid down in the contract. When materials are required to be tested in accordance with the specifications, approval of the Engineer-in-Charge shall be issued after the test results are received.

The Contractor shall at his risk and cost submit the samples of materials to be tested or analyzed and shall not make use of or incorporate in the work any materials represented by the samples until the required tests or analysis have been made and materials finally accepted by the Engineer-in-Charge. The Contractor shall not be eligible for any claim or compensation either arising out of any delay in the work or due to any corrective measures required to be taken on account of and as a result of testing of materials.

The contractor shall, at his risk and cost, make all arrangements and shall provide all facilities as the Engineer-in-Charge may require for collecting, and preparing the required number of samples for such tests at such time and to such place or places as may be directed by the Engineer-in-Charge and bear all charges and cost of testing unless specifically provided for otherwise elsewhere in the contract or specifications. The Engineer-in-Charge or his authorised representative shall, at all time, have access to the works and to all workshops and places where work is being prepared or from where materials, manufactured articles or machinery are being obtained for the works and the contractor shall afford every facility and every assistance in obtaining the right to such access.

The Engineer-in-Charge shall have full powers to require the removal, from the premises, of all materials which in his opinion are not in accordance with the specifications and in case of default the Engineer-in-Charge shall be at liberty to employ at the expenses of the contractor, other persons to remove the same without being answerable or accountable for any loss or damage that may happen or arise to such materials. The Engineer-in-Charge shall also have full powers to require other proper materials to be substituted thereof and in case of default the Engineer-in-Charge may cause the same to be supplied and all costs, which may attend such removal, and substitution shall be borne by the Contractor

CLAUSE 10 A DELETED

CLAUSE 10 B DELETED

CLAUSE 10 C DELETED

CLAUSE 10 D

Dismantled Materials Govt. Property

The contractor shall treat all materials obtained during dismantling of a structure, excavation of the site for a work, etc as HLL’s property and such materials shall be disposed off to the best advantage of HLL according to the instructions in writing issued by the Engineer-in-Charge.

CLAUSE 11

The contractor shall execute the whole and every part of the work in the most substantial and workmanlike manner both as regards materials and otherwise in every respect in strict accordance with the specifications. The contractor shall also conform exactly, fully and faithfully to the design, drawings and instructions in writing in respect of the work signed by the Engineer-in-Charge and the contractor shall be furnished free of charge one copy of the contract documents together with specifications, designs, drawings and instructions as are not included in the standard specifications of Central Public Works Department specified in Schedule ‘F’ or in any Bureau of Indian Standard or any other, published standard or code or , Schedule of Rates or any other printed publications referred to elsewhere in the contract.

Work to be Executed in Accordance with Specifications, Drawings, Orders, etc.

The contractor shall comply with the provisions of the contract and with the care and diligence execute and maintain the works and provide all labour and materials, tools and plants including for measurements and supervision of all works, structural plans and other things of temporary or permanent nature required for such execution and maintenance in so far as the necessity for providing these, is specified or is reasonably inferred from the contract. The contractor shall take full responsibility for adequacy, suitability and safety of all the works and methods of construction.

CLAUSE 12

Deviations, Variations Extent and Pricing

The Engineer-in-Charge shall have power to make alteration in, omission from, additions to, or substitutions for the original specifications, drawings, designs and instructions that may appear to him to be necessary or advisable during the progress of the work, and contractor shall be bound to carry out the work in accordance with any instructions given to him in writing signed by the Engineer-in-Charge and alterations/omissions, additions or substitutions shall form part of the contract as if originally provided therein and any altered, additional or substituted work which the contractor may be directed to do in the manner specified above as part of the works, shall be carried out by the contractor on the same conditions in all respects including price on which he agreed to do the main work except as hereafter provided.

    - The time for completion of the work shall, in the event of any deviations resulting in additional cost over the tendered value, be extended if requested by the contractor, as follows:

- In the proportion which the additional cost of the altered, additional or substituted work, bears to the original tendered value(+) plus

- 25% of the time calculated in (i) above or such further additional time as may be considered reasonable by the competent authority under Clause-5.

    - Rates for such altered, additional or substituted work shall be determined by the Engineer-in-Charge as follows:

- If the rate for altered, additional or substituted item of work is specified in the schedule of quantities, the contractor shall carry out the altered, additional or substituted items at the same rate. In the case of composite tenders, where two or more schedules of quantities may form part of the contract, the applicable rate shall be taken from the schedule of quantities of that particular part in which the deviation is involved, failing that at the lowest applicable rates for the same item of work in the other schedules of quantities.

- If the rate for any altered, additional, or substituted item of work is not specified in the schedule of quantities, the rate for that item shall be derived from the rate for the nearest similar item specified therein. In case of composite tender where two or more schedule of quantities form part of the contract the rate shall be derived from the nearest similar item in the schedule of quantities of the particular part of works in which the deviation is involved failing that from the lowest of the nearest similar item in other schedule of quantities.

- If the rate for altered, additional or substituted item of work cannot be determined in the manner specified in sub-paras (i) and (ii) above, then such item of work shall be carried out at the rate entered in Schedule of Rates mentioned in Schedule ‘F’ plus/minus the percentage by which the tendered amount of the works actually awarded is higher or lower than the corresponding estimated amount of the works actually awarded.

- If the rate for any altered, additional or substituted item of work cannot be determined in the manner specified in sub-para (i) to (iii) above, then the rate for such item of work shall be derived from the schedule of rates specified in sub-para (iii) above plus/minus the percentage mentioned in that sub-para. In the case of	materials issued by the HLL, issue rates of materials, with storage charges recovered, enhanced by two and a half percent for profits and overheads shall be adopted in place of schedule rate plus percentage specified in sub-para (iii). Provided always that if rate(s) or part(s) of the item(s) are not available in the schedule of the rate specified above, rate or part(s) of such item(s) shall be determined on the basis of market rate(s) prevailing during the fortnight following the date of the order plus ten per cent for profit and overhead.

- If the rate for any altered, additional or substituted item of work cannot be determined in the manner specified in sub-para (i) to (iv) above, the contractor shall, within 15 days of the date of receipt of the order to carry out the said work, inform the Engineer-in-Charge of the rate which he proposes to claim for such item of work, supported by analysis of the rate claimed and the Engineer-in-Charge shall, within three months thereafter, after giving due consideration to the rate claimed by the contractor, determine the rate on the basis of  market rate(s). In the event of the contractor failing to inform, the Engineer-in-Charge within the stipulated period of time, the rate, which he proposes to claim, the rate for such items shall be determined by the Engineer-in-Charge on the basis of market rate(s).

  - In the case of contract items, substituted items, contract cum substituted items or additional items which individually exceeds the limits laid down in Schedule ‘F’ the contractor shall within fifteen days of receipt of order or occurrence of the excess, claim revision of the rates, supported by proper analysis, for the work in excess of the above mentioned limit provided that if the rate so claimed are in excess of the rates specified in the Schedule of Quantities of those derived in accordance with the provisions of sub-para (i) to (iv) of conditions 12.1.2 and the Engineer-in-Charge shall, after giving consideration to the analysis of the rates submitted by the contractor, determine the rates on the basis of market rates and the contractor shall be paid in accordance with the stipulated rates so determined. In the event of the contractor failing to claim the revision of rates within the stipulated period, the Engineer-in-Charge shall make payment at the rates as specified in the Schedule of Quantities or those already determined under sub-paras (i) to (iv) of condition 12.1.2 for the quantities in excess of the deviation limit laid down in Schedule ‘F’.

  - All the provisions of the preceding paragraph shall also apply to the decrease in the rates of items for the work in excess of the deviation limit and the Engineer-in-Charge may after giving notice to the contractor and after taking into consideration any reply received from him, revise the rates for the work in question having regard to the market rates.

  - The Engineer-in-Charge shall intimate to the contractor the sanctioned rates of items falling under the sub–clauses 12.1.2(i) to (iv) above within three months of written orders to carry out the work and in case item falling under sub-clauses 12.1.2 (v) and clauses 12.2 within three months of intimation of rate claimed by the contractor. The reduced rates of items falling under clause 12.3 shall be intimated within three months of the receipt of order by the contractor. Under no circumstances the contractor shall suspend the work on the plea of non-settlement of rates or disputes in the rates fixed by the Engineer-in-Charge of the items falling under the above clauses.

  - Any operation incidental to or necessarily has to be in contemplation of tenderer while filing tender, or necessary for proper execution of the item included in the Schedule of Quantities or in the schedule of rates mentioned above, whether or not, specifically indicated in the description of the item and the relevant specifications, shall be deemed to be included in the rates quoted by the tenderer or the rate given in the said schedule of rates, as the case may be. Nothing extra shall be admissible for such operations.

CLAUSE 13

If at any time after acceptance of the tender HLL shall decide to abandon or reduce the scope of the work for any reason whatsoever, the Engineer-in-Charge shall give notice in writing to that effect to the contractor and the contractor shall act accordingly in the matter. The contractor shall have no claim to any payment of compensation or otherwise whatsoever, on account of any profit or advantage which he might have derived from the execution of the work. Further, the contractor shall not have any claim for compensation by reasons of an alteration having been made in the original specifications, drawings, designs and instructions which shall involve any curtailment of the work as originally contemplated.

Foreclosure of Contract due to Abandonment or Reduction in Scope of Work

The contractor shall be paid at contract rates full amount for works executed at site and, in addition, a reasonable amount as certified by the Engineer-in-Charge for the items hereunder mentioned which could not be utilised on the work to full extent due to curtailment in the scope of the work or foreclosure of the contract.

- Proportionate expenditure, incurred on preliminary site work (e.g. temporary access roads, temporary labour huts, staff quarters and site offices, storage accommodation and water storage tanks) and tool and plants.

- The Engineer-in-Charge shall have the option to take over contractor’s materials or any part thereof brought to site. For materials taken over or to be taken over by the Engineer-in-Charge, the cost of such materials shall however, take into account purchase price, cost of transportation and deterioration or damage which may have been caused to materials whilst in the custody of the contractor.

- For contractor’s materials not retained by the Engineer-in-Charge, reasonable cost of transporting such materials and tools and plants from site to contractor’s permanent stores or to his other works, whichever is less, shall be payable.

- If any materials supplied by the HLL are rendered surplus, the same except normal wastage shall be returned by the contractor to HLL. at rates not exceeding those at which these were originally issued less allowances for any deterioration or damage which may have been caused whilst the materials were in the custody of the contractor. In addition, cost of transporting such materials from site to HLL stores, if so required by the HLL, shall be paid.

The contractor shall, if required by the Engineer-in-Charge, furnish to him books of account, wage books, time sheets and other relevant documents as may be necessary to enable him to assess and certify the reasonable amount payable.

CLAUSE 14

Suspension of work

i)	The contractor shall, on receipt of the order in writing of the Engineer-in-Charge (whose decision shall be final and binding on the contractor) suspend the progress of the works or any part thereof for such time and in such manner as the Engineer-in-Charge may consider necessary so as not to cause any damage or injury to the work already done or endanger the safety thereof for any of the following reasons:

- On account of any default on the part of the contractor or ;

- For proper execution of the works or part thereof for reasons other than the default of the contractor; or

- For safety of works or part thereof.

The contractor shall, during such suspension, properly protect and secure the works to the extent necessary and carry out the instructions given in that behalf by the Engineer-in-Charge.

(ii)	If the suspension is ordered for reasons (b) and (c) in sub-para (i) above:

- The contractor shall be entitled to an extension of time equal to the period of every such suspension PLUS 25%, for completion of the item or group of items of work for which a separate period of completion is specified in the contract and of which the suspended work forms a part, and;

- If the total period of all such suspensions in respect of an item or group of items or work for which a separate period of completion is specified in the contract exceeds thirty days, the contractor shall, in addition, be entitled to such compensation as the Engineer-in-Charge may consider reasonable in respect of salaries and/or wages paid by the contractor to his employees and labour at site, remaining idle during the period of suspension, adding thereto 2% to cover indirect expenses of the contractor, provided the contractor submits his claim supported by details to the Engineer-in-Charge within 15 days of the expiry of the period of 30 days,

- If the works or part thereof is suspended on the orders of the Engineer-in-Charge for more than three months at a time, except when suspension is ordered for reason (a) in sub-para (i) above, the contractor may after receipt of such order serve a written notice on the Engineer-in-Charge requiring permission within 15 days from receipt by the Engineer-in-Charge of the said notice, to proceed with the work or part thereof in regard to which progress has been suspended and if such permission is not granted within that time, the contractor, if he intends to treat the suspension, where it affects only a part of the work as an omission or such part by HLL or where it affects whole of the works, as an abandonment of the works by HLL, shall within ten days of expiry of such period of 15 days give notice in writing of his intention to the Engineer-in-Charge.  In the event of the contractor treating the suspension as an abandonment of the contract by the HLL., he shall have no claim to payment of any compensation  on account of any profit or advantage which he might have derived from the execution of the work in full but which he could not derive  in consequence of the abandonment.  He shall, however, be entitled to such compensation, as the Engineer-in-Charge may consider reasonable, in respect of salaries and /or wages paid by him to his employees and labour at site, remaining idle in consequence adding to the total thereof 2% to cover indirect expenses of the contractor provided the contractor submits his claim supported by details to the Engineer-in-Charge within 30 days of the expiry of the period of three months.

Provided, further, that the contractor shall not be entitled to claim any compensation from the HLL for the loss suffered by him on account of delay by HLL in the supply of materials in schedule ‘B’ where such delay is covered by difficulties relating to the supply of wagons, force majeure including non allotment of such materials by controlling authorities, acts of God, acts of enemies of the State/Country or any reasonable cause beyond the control of the HLL.

CLAUSE 15

Inspection and supervision of work

All works under or in course of execution or executed in pursuance of the contract shall at all times be opened and accessible to the inspection and supervision of Engineer-in-Charge, his authorised subordinates in charge of the work and all the superior officers, Officer of the Quality Control Organisation of the HLL, and contractor shall at all times, during the usual working hours and at all other times at which reasonable notice of the visit of such officers has been given to the contractor, either himself be present to receive orders and instructions or have a responsible agent duly accredited in writing, present for that purpose.  Orders given to the contractor’s agent shall be considered to have the same force as if they had been given to the contractor himself.

CLAUSE 16

Rectification of defects

If it shall appear to the Engineer-in-Charge or his authorised subordinates in-charge of the work, that any work has been executed with unsound, imperfect, or unskillful workmanship or with materials or articles provided by him for the execution of work which are unsound or of a quality inferior to that contracted or otherwise not in accordance with the contract, the contractor shall, on demand in writing which shall be made within six months of the completion of the work from the Engineer-in-Charge specifying the work, materials or articles complained of not withstanding that the same may have been passed, certified and paid for forthwith rectify or remove and   reconstruct the work so specified in whole or in part, as the case may require or as the case may be, remove the materials or articles so specified and provide other  proper and suitable materials  or articles at his own charge and cost.  In the event of the failing to do so, within a period specified by the Engineer-in-Charge in his demand aforesaid, the contractor shall be liable to pay compensation at the same rate as under clause 2 of the contract (for non-completion of the work in time) for this default.

In such case, the Engineer-in-Charge may not accept the item of work at the rates applicable under the contract but may accept such items at reduced rates as the competent authority may consider reasonable during the preparation of on account bills or final bill if the item is so acceptable without detriment to the safety and utility of the item and the structure or he may reject the work out right without any payment and/or get it and other connected and incidental items rectified or removed and re-executed at the risk and  cost of the contractor. Decision of the Engineer-in-Charge to be conveyed in writing in respect of the same will be final and binding on the contractor.

CLAUSE 17

If the contractor or his working people or servants shall break, deface, injure or destroy any part of building in which they may be working, or any building, road, road kerb, fence, enclosure, water pipe, cables, drains, electric or telephone post which the work or any part is being executed, or if any damage shall happen to the work while in progress from any cause whatever or if any defect, shrinkage or other faults appear in the work within twelve months (6 months in the case of any work other than road work cost Rs. 10,00,000/-and below) after a certificate final or otherwise of its completion shall have been given by the Engineer-in-Charge as aforesaid arising out of defect or improper materials or workmanship the contractor shall upon receipt of a notice in writing on that behalf make the same good at his own expense or in default the Engineer-in Charge cause the same to be made good by other workmen and deduct the expense from any sums that may be due  or at any time thereafter may become due to the contractor, or from his security deposit or the proceeds of sale thereof or of a sufficient portion thereof.  The security deposit of the contractor shall not be refunded before the expiry of twelve months (six months in the case of any work other than road work cost Rs. 10,00,000/- and below) after the issue of the certificate final or otherwise, of completion of work, or till the final bill has been prepared and passed whichever is later.  Provided that in the case of road work if in the opinion of the Engineer-in-Charge, half of the security deposit is sufficient, to meet all liabilities of the contractor under this contract, half of the security deposit will be refundable after six months and the remaining half after twelve months of the issue of the said certificate of completion or till the final bill has been prepared and passed whichever is later.

Contractor liable for damages, defects during maintenance period

CLAUSE 18:

Contractor to supply Tools and Plants etc.

The contractor shall provide at his own cost all materials (except such special materials, if any, as may in accordance with the contract be supplied from the Engineer-in-Charge’s 	stores), plant, tools, appliances, implements, ladders, cordage, tackle, scaffolding and temporary works required for the proper execution of the work, whether original, altered or substituted and whether included in the specification or other documents forming part of the contract or referred to in these conditions or not, or which may be necessary for the purpose of satisfying or complying with the requirements of the Engineer-in-Charge as to any matter as to which under these conditions he is entitled to be satisfied, or which he is entitled to require together with carriage therefor to and from the work. The contractor shall also supply without charge the requisite number of persons with the means and materials, necessary for the purpose of setting out works, and counting weighing and assisting the measurement for examination at any time and from time to time of the work or materials. On his failing to do so, the same may be provided by the Engineer-in-Charge at the expense of the contractor and the expenses may be deducted, from any money due to the contractor, under this contract or otherwise and/or from his security deposit or the proceeds of sale thereof, or a sufficient portions thereof.

CLAUSE 18 A

Recovery of compensation paid to workman

In every case in which by virtue of the provisions sub-section (1) of Section 12, of the Workmen’s Compensation Act, 1923, HLL is obliged to pay compensation to a workman employed by the contractor, in execution of the works, HLL will recover from the contractor the amount of the compensation so paid; and, without prejudice to the rights of the HLL under sub-section (2) of Section 12, of the said Act, HLL shall be at liberty to recover such amount or any part thereof by deducting it from the security deposit or from any sum due by HLL to the contractor whether under this contract or otherwise. HLL shall not be bound to contest any claim made against it under sub-section (1) Section 12, of the said Act, except on the written request of the contractor and upon his giving to HLL full security for all costs for which HLL might became liable in consequence of contesting such claim.

CLAUSE 18 B

Ensuring Payment & Amenities to Workers, if Contractor Fails

In every case in which by virtue of the provisions of the Contract Labour (Regulation and Abolition) Act, 1970, and of the Contract Labour (Regulation and Abolition) Central Rules, 1971, HLL is obliged to pay any amounts of wages to a workman employed by the contractor in execution of the works, or to incur any expenditure in providing welfare and health amenities required to be provided under the above said Act and the rules under Clause 19H or under the Contractor’s Labour Regulations, or under the Rules framed by the HLL / HLL from time to time for the protection of health and sanitary arrangements for workers employed by the Contractor, HLL will recover from the contractor the amount of wages so paid or the amount of expenditure so incurred ; and without prejudice to the rights of the HLL under Sub-Section (2) of Section 20, and sub-section (4) of Section 21, of the Contract Labour (Regulation and Abolition) Act, 1970, HLL shall be at liberty to recover such amount or any part thereof by deducting it from the security deposit or from any sum due by the HLL to the contractor whether under this contract or otherwise HLL shall not be bound to contest any claim made against it under sub-section (1) of Section 20, sub-section (4) of Section 21, of the said Act, except on the written request of the contractor and upon his giving to the HLL full security for all costs for which HLL might become liable in contesting such claim.

CLAUSE 19

Labour Laws to be Complied by the Contractor

The contractor shall obtain a valid Licence under the Contract Labour (R&A) Act 1970, and the Contract Labour (Regulation and Abolition) Central Rules 1971, before the commencement of the work and continue to have a valid license until the completion of the work.

Any failure to fulfill this requirement shall attract the penal provisions of this contract arising out of the resultant non-execution of the work.

CLAUSE 19 A

No labour below the age of eighteen years shall be employed on the work.

CLAUSE 19 B

Payment of wages:

Payment of wages

- The contractor shall pay to labour employed by him either directly or through sub-contractors, wages not less than fair wages as defined in the contractor’s Labour Regulation or as per the provisions of the contract labour (Regulation and Abolition) Act 1970, and the contract labour (Regulation and Abolition) Central Rules, 1971, wherever applicable.

- The contractor shall, not withstanding the provisions of any contract to the contrary, cause to be paid fair wage to labour indirectly engaged on the work, including any labour engaged by his sub-contractors in connection with the said work, as if the labour had been immediately employed by him.

- In respect of all labour directly or indirectly employed in the works for performance of the contractor’s part of this contract, the contractor shall comply with or cause to be complied with the contractor’s Labour Regulations made by the HLL / HLL from time to time in regard to payment of wages, wage period, deductions from wages recovery of wages not paid and deductions unauthorisedly made, maintenance of wage books or wage slips, publication of scale of wages and other terms of employment, inspection and submission of periodical returns and all other matters of the like nature or as per the provisions of the contract labour(Regulation & Abolition) Act, 1970, and the Contract Labour (Regulation and Abolition) Central Rules, 1971,  wherever applicable.

iv)         a)	The Engineer-in-Charge concerned shall  have the right to deduct  from the moneys due to the contractor any sum required or estimated  to be required for making good the loss suffered  by a worker or workers by reason of non-fulfillment of the conditions of the contract for the benefit of the workers, non-payment of wages or of deductions made from his or their wages which are not justified by their terms of the contract or non-observance of the Regulations.

b) 	Under the provisions of Minimum Wages (Central) Rules, 1950, the contractor is bound to allow to the labours directly or indirectly employed in the works one day rest for six days continuous work and pay wages at the same rate as for duty. In the event of default the Engineer-in-Charge shall have the right to deduct the sum or sums not paid on account of wages for weekly holidays to any labours and pay the same to the persons entitled thereto from any money due to the contractor by the Engineer-in-Charge concerned.

In the case of Union Territory of Delhi, however, as the all inclusive minimum daily wages fixed under Notification of the Delhi Administration No.F.12 (162) MWO/DAB/43884-91, dated 31.12.1979 as amended from time to time are inclusive of wages for the weekly day of rest, the question of extra payment for weekly holiday would not arise.

v)	The contractor shall comply with the provisions of the Payment of Wages Act, 1936, Minimum Wages Act, 1948, Employees Liability Act 1938, workmen’s compensation Act, 1923, industrial disputes Act, 1947, Maternity benefits act, 1961, and the contractor’s labour (Regulation and Abolition) Act, 1970, or the modifications their of or any other laws relating their to and the rules made their under from time to time.

vi)	The contractor shall indemnify and keep indemnified HLL against payments to be made under and for the observance of the Laws aforesaid and the contractor’s Labour Regulations without prejudice to his right to claim indemnity from his sub-contractors.

- The laws aforesaid shall be deemed to be a part of this contract and any breach thereof shall be deemed to be a breach of this contract.

- Whatever is the minimum wage for the time being, or if the wage payable is higher than such wage, such wage shall be paid by the contractor to the Workmen directly without the intervention of Jamadar and that Jamadar shall not be entitled to deduct or recover any amount from the minimum wage payable to the workmen as and by way of commission or otherwise.

- The contractor shall ensure that no amount by way of commission or otherwise is deducted or recovered by the Jamadar from the wage of workmen.

CLAUSE 19 C

In respect of all labour directly or indirectly employed in the work for the performance of the contractor’s part of this contract, the contractor shall, at his own expense, arrange for the safety provisions as per Safety Code framed from time to time and shall, at his own expense, provide for all facilities in connection therewith. In case the contractor fails to make arrangements and provide necessary facilities as aforesaid he shall be liable to pay a penalty of Rs.200/- for each default and in addition the Engineer-in-Charge shall be at liberty to make arrangement and provide facilities as aforesaid and recover the costs incurred in that behalf from the contractor.

CLAUSE 19 D

The contractor shall submit by the 4th and 19th of every month, to the Engineer-in-Charge a true statement showing in respect of the second half of the preceding month and the first half of the current month respectively:-

- the number of labourers employed by him on the work,

- their working hours,

- the wages paid to them,

- the accidents that occurred during the said fortnight showing the circumstances under which they happened and the extent of the damages and injury caused by them, and,

- the number of female workers who have been allowed maternity benefit according to Clause 19 F and the amount paid to them.

Failing which the contractor shall be liable to pay to HLL a sum not exceeding Rs.200/- for each default or materially incorrect statement. The decision of the Engineer-in-Charge shall be final in deducting from any bill due to the contractor the amount levied as fine and be binding on the Contractor.

CLAUSE 19 E

In respect of all labour directly or indirectly employed in the works for the performance of the contractor’s part of this contract, the contractor shall comply with or cause to be complied with all the rules framed by HLL from time to time for the protection of health and sanitary arrangements for workers employed by the Deptt.of Telecommunications and its contractors.

CLAUSE 19 F

Leave and pay during leave shall be regulated as follows:-

- Leave:

- in the case of delivery-maternity leave not exceeding 8 weeks, 4 weeks, upto and including the day of delivery and 4 weeks following that day,

- in case of miscarriage-upto 3 weeks from the date of miscarriage.

- Pay:

- in case of delivery- leave pay during maternity leave will be at the rate of the women’s average daily earnings, calculated on total wages earned on the days when full time work was done during the period of three months immediately preceding the date on which she gives notice that she expects to be confined or at the rate of Rupee one only a day whichever is greater.

- in the case of miscarriage – leave pay at the rate of average daily earning calculated on the total wages earned on the days when full time work  was done during a period of three months immediately preceding the date of such miscarriage.

- Conditions for  the grant of Maternity Leave:

No maternity leave benefit shall be admissible to a woman unless she has been employed for a total period of not less than six months immediately preceding the date on which she proceeds on leave,

- The contractor shall maintain a register of Maternity (Benefit) in the prescribed form as shown in Appendix-I and II, and the same shall be kept at the place of work.

CLAUSE 19 G

In the event of the contractor(s) committing a default or breach of any of the provisions of the Contractor’s Labour Regulation and Model Rules for the protection of health and sanitary arrangements for the workers as amended from time to time or furnishing any information or submitting or filing any statement under the provisions of the above Regulation and Rules which is materially incorrect, he/they shall, without prejudice to any other liability, pay to the HLL a sum not exceeding Rs.200/- for every default, breach or furnishing, making, submitting , filing such materially incorrect statements and in the event of  the contractor (s) defaulting continuously in this respect, the penalty may be enhanced to Rs.200/- per day for each day of default subject to a maximum of 5 percent of the estimated cost of the work put to tender. The decision of the Engineer-in-Charge shall be final and binding on the parties.

Should it appear to the Engineer-in-Charge that the contractor(s) is/ are not properly observing and complying with the provisions of the Contractor’s Labour Regulations and Model Rules and the provisions of the Contract labour (Regulation and Abolition) Act, 1970, and the Contract Labour (R&A) Central Rules 1971, for the protection of health and sanitary arrangements for the work-people employed by the contractor(s)(hereinafter referred as”the said Rules”) the Engineer-in-Charge shall have  power to give notice in writing to the contractor(s) requiring that the said Rules to be complied with and the amenities prescribed therein be provided to the work-people within a reasonable time to be specified in the notice. If the contractor(s) shall fail within the period specified in the notice to comply with and/or observe the said Rules and to provide the amenities to the workpeople as aforesaid, the Engineer-in-Charge shall have the power to provide the amenities herein before mentioned at the cost of the contractor(s).  The contractor(s) shall erect, make and maintain at his/their own expense and to approved standards all necessary huts and sanitary arrangements required for his/their work-people on the site in connection with the execution of the works, and if the same shall not have been erected or constructed, according to approved Standards, the Engineer-in-Charge shall have power to give notice in writing to the contractor(s) requiring that the said huts and sanitary arrangements be re-modelled and/ or reconstructed according to approved standards, and if the contractor(s) shall fail to remodel or reconstruct such huts and sanitary arrangements according to approved standards within the period specified in the notice, the Engineer-in-Charge  shall have the power to remodel or reconstruct such huts and sanitary arrangements according to approved standards at the cost of the contractor(s).

CLAUSE 19 H

The contractor(s) shall at his/their own cost provide his /their labour with a sufficient number of huts (hereinafter referred to as the camp) of the following specifications on a suitable plot of land to be approved by the Engineer-in-Charge.

i)

- The minimum height of each hut at the eaves level shall be 2.10m  (7 ft.) and floor area to be provided will be at the rate of 2.7 Sq.ms. (30 Sq.Ft.) for each member of the workers family staying with the labourers.

- The contractor(s) shall in addition construct suitable cooking places having a minimum area of 1.80m X 1.50m(6’X5’) adjacent to the hut for each family.

- The contractor(s) shall also construct temporary latrines and urinals for the use of the labourers each on the scale of not less than four per each one hundred of the total strength, separate latrines and urinals being provided for women.

- The contractor(s) shall construct sufficient number of bathing and washing places, one unit for every 25 persons residing in the camp. These bathing and washing places shall be suitably screened.

- All the huts shall have walls of sun-dried or burnt-bricks laid in mud mortar or other suitable local materials as may be approved by the Engineer-in-Charge. In case of sun-dried bricks, the walls should be plastered with mud gobri on both sides. The floor may be kutcha but plastered with mud gobri and shall be atleast 15 cm (6”) above the surrounding ground. The roofs shall be laid with thatch or any other materials as may be approved by the Engineer-in-Charge and the contractor shall ensure that through out the period of their occupation the roofs remain watertight.

- The contractor(s) shall provide each hut with proper ventilation.

- All doors, windows, and ventilators shall be provided with suitable leaves for security purposes.

- There shall be kept an open space of at least 7.2m(8yds.) between the rows of huts which may be reduced to 6m(20ft.) according to the availability of site with the approval of the Engineer-in-Charge. Back to back construction will be allowed.

- Water Supply- The contractor(s) shall provide adequate supply of water for the use of labourers. The provisions shall not be less than two gallons of pure and wholesome water per head per day for drinking purposes and three gallons of clean water per head per day for bathing and washing purpose. Where piped water supply is available, supply shall be at stand posts and where the supply is from wells or river, tanks, which may be of metal or masonry, shall be provided. The contractor(s) shall also at his/their own cost make arrangements for laying pipe lines for water supply to his/their labour camp from the existing mains wherever available, and shall pay all fees and charges therefor.

- The site selected for the camp shall be high ground, removed from jungle.

- Disposal of Excreta- The contractor(s) shall make necessary arrangements for the disposal of excreta from the latrines by trenching or incineration, which shall be according to the requirements laid down by the Local Health Authorities. If trenching or incineration is not allowed the contractor(s) shall make arrangements for the removal of the excreta through the Municipal Committee/Authority and inform it about the number of labourers employed so that arrangements may be made by such Committee/authority for removal of the excreta. All charges on this account shall be borne by the contractor and paid direct by him to the Municipality/authority. The contractor shall provide one sweeper for every eight seats in case of dry system.

- Drainage:- The contractor(s) shall provide efficient arrangements for draining away sullage water so as to keep the camp neat and tidy.

- The Contractor(s) shall make necessary arrangements for keeping the camp area sufficiently lighted to avoid accidents to the workers.

- Sanitation:- The contractor(s) shall make arrangements for conservancy and sanitation in the labour camps according to the rules of the Local Public Health and Medical Authorities.

CLAUSE 19 I

The Engineer-in-Charge may require the contractor to dismiss or remove from the site of the work any person or persons in the contractor’s employment upon the work who may be incompetent or misconducts himself and the contractor shall forthwith comply with such requirements.

CLAUSE 19 J

It shall be the responsibility of the contractor to see that the building under construction is not occupied by any body unauthorisedly during construction, and is handed over to the Engineer-in-Charge with vacant possession of complete building. If such building though completed is occupied illegally, then the Engineer-in-Charge shall have the option to refuse to accept the said building/buildings in that position. Any delay in acceptance on this account will be treated as the delay in completion and for such delay a levy upto 5% of the tendered value of work may be imposed by the Executive Director(ID), HLL  whose decision shall be final both with regard to the justification and quantum and be binding on the contractor.

However, the Executive Director(ID), HLL, through a notice, may require the contractor to remove the illegal occupation any time on or before construction and delivery.

CLAUSE 20

Minimum wages Act to be Compiled with

The contractor shall comply with all the provisions of the Minimum Wages Act, 1948, and Contract Labour (Regulation and Abolition) Act, 1970, amended from time to time and rules framed thereunder and other labour laws affecting contract labour that may be brought into force from time to time.

CLAUSE 21

The contract as a whole or part thereof shall not be assigned or sublet or transferred either directly or indirectly whether by creating agent on the basis of General Power of Attorney or in any other manner or given on general power of attorney without the written approval of the Engineer-in-Charge. If the contractor shall assign or sublet or give on general power of attorney or transferred either directly or indirectly whether by creating agent on the basis of General Power of Attorney or in any other manner, his contract, or attempt to do so, or become insolvent or commence any insolvency proceedings or make any composition with his creditors or attempt to do so, or if any bribe, gratuity, gift, loan, perquisite, reward or advantage pecuniary or otherwise, shall either directly or indirectly, be given, promised or offered by the contractor, or any of his servants or agent to any public officer or person in the employment of HLL in any way relating to his office or employment or if any such officer or person shall become in any way  directly or indirectly interested in the contractor, or if the contractor shall obtain a contract with the HLL as a result of wrong tendering or by non bonafide methods, the Engineer-in-Charge on behalf of the HLL LifecareLimited shall have  powers to adopt any or all of the courses specified in Clause 3 hereof as he may deem best suited to the interest of HLL and in the event of any or all of these courses being adopted the consequences specified in the said Clause 3 shall ensue.

Work not to be sublet, Action in case of Insolvency

CLAUSE 22

All sums payable by way of compensation under any of these conditions shall be considered as reasonable compensation to be applied to use of HLL without reference to the actual loss or damage sustained and whether or not any damage shall have been sustained.

CLAUSE 23

Where the contractor is a partnership firm, the previous approval in writing of the Engineer-in-Charge shall be obtained before any change is made in the constitution of the firm. Where the contractor is an individual or a Hindu undivided family business concern such approval as aforesaid shall likewise be obtained before the contractor enters into any partnership agreement where-under the partnership firm would have the right to carry out the works hereby undertaken by the contractor. If previous approval as aforesaid is not obtained, the contract shall be deemed to have been assigned in contravention of Clause 21 hereof and the same action may be taken, and the same consequences shall ensue as provided in the said Clause 21.

Changes in Firm’s Constitution to be intimated

CLAUSE 24

All works to be executed under the contract shall be executed under the direction and subject to the approval in all respects of the Engineer-in-Charge who shall be entitled to direct at what point or points and in what manner they are to be commenced, and from time to time carried on.

CLAUSE 25

Except where otherwise provided in the contract all questions and disputes relating to the meaning of the specifications, design, drawings and instructions herein before mentioned and as to the quality of workmanship or materials used on the work or as to any other question, claim, right, matter or thing whatsoever in any way arising out of or relating to the contract, designs, drawings, specifications, estimates, instructions orders or these conditions or otherwise concerning the works or the execution or failure to execute the same whether arising during the progress of the work or after the cancellation, termination, completion or abandonment thereof shall be dealt with as mentioned hereinafter:-

Settlement of Disputes & Arbitration

- If the contractor considers that he is entitled to any extra payment or compensation in respect of the works over and above the amounts admitted as payable by the HLL or in case the contractor wants to dispute the validity of any deductions or recoveries made or proposed to be made from the contract, the contractor shall forthwith give notice in writing of his claim, in this behalf to the Engineer-in-Charge within 30 days from the date of disallowance thereof for which the contractor claims such additional payment or compensation or disputes the validity of any deduction or recovery. The said notice shall give full particulars of the claim, grounds on which it is based and detailed calculations of the amount claimed and the contractor shall not be entitled to raise any claim nor shall the HLL be in any way liable in respect of any claim by the contractor unless notice of such claim shall have been given by the contractor to the Engineer-in-Charge in the manner and within the time as aforesaid. The contractor shall be deemed to have waived and extinguished all his rights in respect of any claims not notified to the Engineer-in-Charge in writing in the manner and within the time aforesaid.

- The Engineer-in-Charge shall give his decision in writing on the claims notified by the contractor within 30 days of the receipt of the notice thereof. If the contractor is not satisfied with the decision of the Engineer-in-Charge, the contractor may within 15 days of the receipt of the decision of the Engineer-in-Charge submit his claims to the conciliating authority named in Schedule ‘F’ for conciliation along with all details and copies of correspondence exchanged between him and the Engineer-in-Charge.

- If the conciliation proceedings are terminated without settlement of the disputes, the contractor shall, within a period of 30 days of termination thereof shall give a notice, in the form prescribed by the HLL, to the Chairman & Managing Director, HLL Lifecare Limited for appointment of an arbitrator to adjudicate the notified claims failing which the claims of the contractor shall be deemed to have been considered absolutely barred and waived.

- Except where the decisions have become final, binding and conclusive in terms of the contract, all disputes arising out of the notified claims of the contractor as aforesaid and all claims of the HLL shall be referred for adjudication through the arbitration by the Sole Arbitrator appointed by the Chairman & Managing Director, HLL Lifecare Ltd. It will also be no objection to any such appointment that the Arbitrator so appointed is a HLL Employee and that he had to deal with the matters to which the Contract relates in the course of his duties as HLL Employee. If the arbitrator so appointed is unable or unwilling to act or resigns his appointment or vacates his office due to any reason whatsoever another sole arbitrator shall be appointed in the manner aforesaid by the said Chairman & Managing Director. Such person shall be entitled to proceed with the reference from the stage at which it was left by his predecessor.

It is a term of this contract that the party invoking arbitration shall give a list of disputes with amounts claimed in respect of each dispute along-with the notice for appointment of arbitrator.

It is also a term of this contract that no person other than a person appointed by such Chairman & Managing Director, HLL Lifecare Ltd as aforesaid should act as arbitrator and if for any reasons that is not possible, the matter shall not be referred to arbitration at all.

The conciliation and arbitration shall be conducted in accordance with the provisions of the Arbitration & Conciliation Act 1996 or any statutory modification or re-enactment thereof and the rules made thereunder and for the time being in force shall apply to the arbitration proceeding under this clause

It is also a term of this contract that the arbitrator shall adjudicate on only such disputes as are referred to him by the appointing authority and give separate award against each disputes and claim referred to him. The arbitrator shall give reasons for the award.

It is also a term of the contract that if any fees are payable to the arbitrator these shall be paid equally by both the parties.

It is also a term of the contract that the arbitrator shall be deemed to have entered on the reference on the date he issues notice to both the parties calling them to submit their statement of claims and counter statement of claims. The venue of the arbitration shall be such place as may be fixed by the arbitrator in his sole discretion. The fees, if any, of the arbitrator shall, if required to be paid before the award is made and published, be paid half and half by each of the parties. The cost of the reference and of the award (including the fees, if any, of the arbitrator) shall be in the discretion of the arbitrator who may direct to any, by whom and in what manner, such costs or any part thereof, shall be paid and fix or settle the amount of costs to be so paid.

CLAUSE 26

Contractor to Indemnify HLL against Patent Rights

The contractor shall fully indemnify and keep indemnified the HLL Lifecare Limited against any action, claim or proceeding relating to infringement or use of any patent or design or any alleged patent or design rights and shall pay any royalties which may be payable in respect of any article or part thereof included in the contract. In the event of any claims made under or action brought against HLL in respect of any such matters as aforesaid the contractor shall be immediately notified thereof and the contractor shall be at liberty, at his own expense, to settle any dispute or to conduct any litigation that may arise therefrom, provided that the contractor shall not be liable to indemnify the HLL Lifecare Limited if the infringement of the patent or design or any alleged patents or design right is the direct result of an order passed by the Engineer-in-Charge in this behalf.

CLAUSE 27

Lumpsum Provisions in Tender

When the estimate on which a tender is made includes lumpsum in respect of parts of the work, the contractor shall be entitled to payment in respect of the items of work involved or the part of the work in question at the same rates as are payable under this contract for such items, or if the part of the work in question is not, in the opinion of the Engineer-in-Charge, payable by measurement, the Engineer-in-Charge may at his discretion pay the lumpsum amount entered in the estimate, and the certificate in writing of the Engineer-in-Charge shall be final and conclusive against the contractor with regard to any sum or sums payable to him under the provisions of this clause.

CLAUSE 28

Action where no Specifications are specified

In case of any class of work for which there are no such specifications as referred to in Clause 11,such work shall be carried out in accordance with the Bureau of Indian Standards specifications. In case there is no such specifications in Bureau of Indian Standards, the work shall be carried out as per manufacturer’s specifications. In case no such manufacturer’s specifications is available then as per District Specifications. In case there are no such specifications as required above, the work shall be carried out in all respects in accordance with the instructions and requirements of the Engineer-in-Charge.

CLAUSE 29

Withholding and lien in respect of sum due from the Contractor

i)	Whenever any claim or claims for payment of a sum of money arises out of or under the contract or against the contractor, the Engineer-in-Charge or the HLL shall be entitled to withhold and also have a lien to retain such sum or sums in whole or in part from the security, if any, deposited by the contractor and for the purposes aforesaid, the Engineer-in-Charge or HLL shall be entitled to withhold the security deposit, if any, furnished as the case may be and also have lien over the same pending finalisation or adjudication of any such claim. In the event of the security being insufficient to cover the claimed amount or amounts or if no security has been taken from the contractor, the Engineer-in-Charge or the HLL shall be entitled to withhold and have a lien to retain such claimed amount or amounts referred to above, from any sum or sums found payable or which may at any time thereafter become payable to the contractor under the same contract or any other contract with the Engineer-in-Charge or the HLL or any contracting person through the Engineer-in-Charge pending finalisation of adjudication of any such claim.

It is an agreed term of the contract that the sum of money or moneys so withheld or retained under the lien referred to above by the Engineer-in-Charge or HLL will be kept withheld or retained as such, by the Engineer-in-Charge, till the claim arising out of or under the contract is determined by the arbitrator (if the contract is governed by the arbitration clause) or by the competent court, as the case may be and that the contractor will have no claim for interest or damages whatsoever on any account in respect of such withholding or retention under the lien referred to above and duly notified as such to the contractor. For the purpose of this clause, where the contractor is a partnership firm or a limited company, the Engineer-in-charge or the HLL shall be entitled to withhold and also have a lien to retain towards such claimed amount or amounts in whole or in part from any sum found payable to any partner/limited company as the case may be , whether in his individual capacity or otherwise.

ii)	HLL shall have the right to cause an audit and technical examination of the works and the final bills of the contractor including all supporting vouchers, abstract, etc., to be made after payment of the final bill and if as a result of such audit and technical examination any sum is found to have been overpaid in respect of any work done by the contractor under the contract or any work claimed to have been done by him under the contract and found not to have been executed, the contractor shall be liable to refund the amount of over-payment and it shall be lawful for HLL to recover the same from him in the manner prescribed in sub-clause (i) of this clause or in any other manner legally permissible; and if it is found that the contractor was paid less than what was due to him under the contract in respect of any work executed by him under it, the amount of such under payment shall be duly paid by the HLL to the contractor, without any interest thereon whatsoever.

Provided that the HLL shall not be entitled to recover any sum overpaid, nor the contractor shall be entitled to payment of any sum paid short where such payment has been agreed upon between the Engineer-in-charge on the one hand and the contractor on the other under any term of the contract permitting payment for work after assessment by the Engineer-in-charge.

CLAUSE 29 A

Lien in respect of claims in other contracts

Any sum of money due and payable to the contractor (including the security deposit returnable to him) under the contract may be withheld or retained by way of lien by the Engineer-in-Charge or the HLL or any other contracting person or persons or through Engineer-in-Charge against any claim of the Engineer-in-Charge of HLL or such other person or persons in respect of payment of a sum of money arising out or under any other contract made by the contractor with the Engineer-in-Charge or of the HLL or with such other person or persons.

It is an agreed term of the contract that the sum of money so withheld or retained under this clause by the Engineer-in-Charge or the HLL will be kept withheld or retained as such by the Engineer-in-Charge or the HLL or till his claim arising out of the same contract or any other contract is either mutually settled or determined by the arbitration clause or by the competent court, as the case may be and that the contractor shall have no claim for interest or damages whatsoever on this account or on any other ground in respect of any sum of money withheld or retained under this clause and duly notified as such to the contractor.

CLAUSE 30

Employment of coal mining or controlled area labour not permissible

The contractor shall not employ coal mining or controlled area labour falling under any category whatsoever on or in connection with the work or recruit labour from area within a radius of 32 Km (20 miles) of the controlled area. Subject as above the contractor shall employ imported labour only i.e., deposit imported labour or labour imported by contractors from area, from which import is permitted. Where ceiling price for imported labour has been fixed by State or Regional Labour Committees not more than that ceiling price shall be paid to the labour by the contractor.

The contractor shall immediately remove any labourer who may be pointed out by the Engineer-in-Charge as being a coal mining or controlled area labourer. Failure to do so shall render the contractor liable to pay to HLL a sum calculated at the rate of Rs.10/- per day per labourer. The certificate of the Engineer-in-Charge about the number of coal mining or controlled area labourer and the number of days for which they worked shall be final and binding upon all parties to this contract.

It is declared and agreed between the parties that the aforesaid stipulation in this clause is one in which the public are interested within the meaning of the exception in Section 74 of Indian Contract Act, 1872.

Explanation:- Controlled Area means the following areas:-

Districts of Dhanbad, Hazaribagh, Jamtara- a Sub-Division under Santhal Pargana Commissionery, Districts of Bankuara, Birbhum Burdwan, District of Bilaspur.

Any other area, which may be, declared a Controlled Area by or with the approval of the Central HLL.

CLAUSE 31

The Contractor (s) shall make his/their own arrangements for water and power supply required for the work and nothing extra will be paid for the same. This will be subject to the following conditions:

Water Supply and Power Supply

- That the water used by the contractor(s) shall be fit for construction purposes to the satisfaction of the Engineer-in-Charge.

- The Engineer-in-charge shall make alternative arrangements for water supply at the risk and cost of the contractor (s) if the arrangements made by the contractor (s) for procurement of water are in the opinion of the Engineer-in-Charge, unsatisfactory.

- The contractor shall make his own arrangement for temporary electric connection and shall make necessary payment for it direct to the concerned authority. On completion of the work he shall furnish a no dues certificate from the concerned authority failing which the claims/dues of the concerned authority shall be settled by the Engineer-in-Charge at the contractor’s risk and cost.

CLAUSE 31A

Departmental power & water supply, if available

Water and power supply if available may be supplied to the contractor by the HLL subject to the following conditions:

- The water charges @ 1 % shall be recovered on gross amount of the work done.

- The contractor (s) shall make his/their own arrangement of water connection and laying of pipelines from existing main source of supply

- The contractor shall make his own arrangement to extend the power supply from the tapping point and install a sub meter for recording consumption of power in the work. The consumption charges thereof shall be recovered from the contractor by deduction from his bills or from any other dues.

- The HLL do not guarantee to maintain uninterrupted supply of water and power and it will be incumbent on the contractor (s) to make alternative arrangements for water and power at his/their own cost in the event of any break down in the supply so that the progress of his/their work is not held up. No claim of damage or refund  of water and power charges will be entertained on account of such break down.

CLAUSE 32

Alternate water arrangements

i)	Where there is no piped water supply arrangement and the water is taken by the contractor from the wells or hand pump constructed by the HLL no charge shall be recovered from the contractor on that account. The contractor shall, however, draw water at such hours of the day that it does not interfere with the normal use for which the hand pumps and wells are intended. He will also be responsible for all damage and abnormal repairs arising out of his use, the cost of which shall be recoverable from him. The Engineer-in-Charge shall be the final authority to determine the cost recoverable from the contractor on this account and his decision shall be binding on the contractor.

ii)	The contractor shall be allowed to construct temporary wells in HLL land for taking water for construction purposes only after he has got the permission of the Engineer-in-Charge in writing. No charges shall be recovered from the contractor on this account, but the contractor shall be required to provide necessary safety arrangements to avoid any accidents or damage to adjacent buildings, roads and service lines. He shall be responsible for any accidents or damage caused due to construction and subsequent maintenance of the wells and shall restore the ground to its original condition after the wells are dismantled on completion of the work.

CLAUSE 33

Return of Surplus Materials

Notwithstanding anything contained to the contrary in this contract, where any materials for the execution of the contract are procured with the assistance of HLL either by issue from HLL stocks or purchase made under orders or permits or license issued by HLL, the contractor shall hold the said materials economically and solely for the purpose of the contract and not dispose off them without the written permission of the Government/HLL and return, if required by the Engineer-in-Charge, all surplus or unserviceable materials that may be left with him after the completion of the contract or at its termination for any reason whatsoever on being paid or credited such price as the Engineer-in-Charge shall determine having due regard to the condition of the materials. The price allowed to the contractor however shall not exceed the amount charged to him excluding the element of storage charges. The decision of the Engineer-in-Charge shall be final and conclusive. In the event of breach of the aforesaid condition the contractor shall in addition to throwing himself open to action for contravention of the terms of the license or permit and/or for criminal breach of trust, be liable to HLL for all moneys, advantages or profits resulting or which in the usual course would have resulted to him by reason of such breach.

CLAUSE 34

Hire of Plant & Machinery

- The contractor shall arrange at his own expense all tools, plant, machinery and equipment (hereinafter referred to as T & P) required for execution of the work except for the plant & Machinery listed in Schedule ‘C’ and stipulated for issue to the Contractor. If the contractor requires any item of T & P on hire from the T & P available with the HLL over and above the T&P stipulated for issue, the HLL will, if such item is available, hire it to the contractor at rates to be agreed upon between him and the Engineer-in-Charge. In such a case all the conditions hereunder for issue of T&P, shall also be applicable to such T&P as is agreed to be issued.

- Plant and Machinery when supplied on hire charges shown in Schedule ‘C’ shall be made over and taken back at the HLL equipment yard/shed shown in Schedule ‘C’ and the contractor shall bear the cost of carriage from the place of issue to the site of work and back. The contractor shall be responsible to return the plant and machinery with the same condition in which it was handed over to him, and he shall be responsible for all damage caused to the said plant & machinery at the site of work or elsewhere in operation and otherwise during transit including damage to or loss of plant and for all losses due to his failure to return the same soon after the completion of the work for which it was issued. The Engineer–in-Charge shall be the sole judge to determine the liability of the contractor and its extent in this regard and his decision shall be final and binding on the contractor.

- The plant and machinery as stipulated above will be issued as and when available and if required by the contractor. The contractor shall arrange his programme of work according to the availability of the plant and machinery and no claim, whatsoever, will be entertained from him for any delay in supply by the HLL.

- The hire charges shall be recovered at the prescribed rates from and inclusive of the date the plant and machinery made over upto and inclusive of the date of the return in good order even though the same may not have been working for any cause except major breakdown due to no fault of the contractor or faulty use requiring more than three working days continuously  (excluding intervening holidays and Sundays) for bringing the plant in order. The contractor shall immediately intimate in writing to the Engineer-in-Charge when any plant or machinery gets out of order requiring major repairs as aforesaid. The Engineer-in-Charge shall record the date and time of receipt of such intimation in the log sheet of the plant or machinery. Based on this if the breakdown before lunch period or major breakdown will be computed considering half a day’s breakdown on the day of complaint. If the breakdown occurs in the post lunch period of major break down will be computed starting from the next working day. In case of any dispute under this clause the decision of the Superintending Engineer shall be final and binding on the contractor.

- The hire charges shown above are for each day of 8 hours (inclusive of the one-hour lunch break) or part thereof.

- Hire charges will include service of operating staff as required and also supply of lubricating oil and stores for cleaning purposes. Power fuel of approved type, firewood, kerosene oil etc. for running the plant and machinery and also the full time chowkidar for guarding the plant and machinery against any loss or damage shall be arranged by the contractor who shall be fully responsible for the safeguard and security of plant and machinery. The contractor shall on or before the supply of plant and machinery sign an agreement indemnifying the HLL against any loss or damage caused to the plant and machinery either during transit or at site of work.

- Ordinarily, no plant and machinery shall work for more than 8 hours a day inclusive of one-hour lunch break. In case of an urgent work however, the Engineer-in-Charge may, at his discretion, allow the plant and machinery to be worked for more than normal period of 8 hours a day. In that case the hourly hire charges for overtime to be borne by the contractor shall be 50 % more than the normal proportionate hourly charge (1/8th of the daily charges) subject to a minimum of half day’s normal charges on any particular day. For working out hire charges for over time a period of half an hour and above will be charged as one hour and a period of less than half an hour will be ignored.

- The contractor shall release the plant and machinery every seventh day for periodical servicing and/or wash out which may take about three to four hours or more. Hire charges for full day shall be recovered from the contractor for the day of servicing/wash out irrespective of the period employed in servicing.

- The plant and machinery once issued to the contractor shall not be returned by him on account of lack of arrangements of labour and materials, etc. on his part, the same will be returned only when they are required for major repairs or when in the opinion of the Engineer-in-Charge the work or a portion of work for which the same was issued is completed.

- Logbook for recording the hours of daily work for each of the plant and machinery supplied to the contractor will be maintained by the HLL and will be countersigned by the contractor or his authorised agent daily. In case the contractor contests the correctness of the entries and/or fails to sign the Log Book the decision of the Engineer-in-Charge shall be final and binding on him. Hire charges will be calculated according to the entries in the Log Book and will be binding on the contractor. Recovery on account of  hire charges for road rollers shall be made for the minimum number of days worked out on the assumption that a roller can consolidate per day and maximum quantity of  materials or area surfacing as noted against each in the annexed statement (see attached annexure)

- In the case of concrete mixers, the contractors shall arrange to get the hopper cleaned and the drum washed at the close of the work each day or occasion.

- In case rollers for consolidation are employed by the contractor himself, log book for such rollers shall be maintained in the same manner as is done in case of HLL rollers, maximum quantity of any items to be consolidated for each roller-day shall also be same as in Annexure to Clause 34(x). For less use of roller recovery for the less roller days shall be made at the stipulated issue rate.

- The contractor shall be responsible to return the plant and machinery in the condition in which it was handed over to him and he shall be responsible for all damage caused to the said plant and machinery at the site of work or elsewhere in operation or otherwise or during transit including damage to or loss of parts, and for all losses due to his failure to return the same soon after the completion of the work for which it was issued. The Engineer–in-Charge shall be the sole judge to determine the liability of the contractor and its extent in this regard and his decision shall be final and binding on the contractor.

- The contractor will be exempted from levy of any hire charges for the number of days he is called upon in writing by the Engineer-in-Charge to suspend execution of the work, provided HLL plant and machinery in question have, in fact, remained idle with the contractor because of the suspension.

- In the event of the contractor not requiring any item of plant and machinery issued by HLL though not stipulated for issue in Schedule ‘C’ any time after taking delivery at the place of issue, he may return it after two days written notice or at any time without notice if he agrees to pay hire charges for two additional days without, in any way, affecting the right of the Engineer-in-Charge to use the said plant and machinery during the said period of two days as he likes including hiring out to a third party.

CLAUSE 35

Conditions relating to use of Asphaltic Materials

- The contractor undertakes to make arrangement for the supervision of the work by the firm supplying the tar or bitumen used.

ii)	The contractor shall collect the total quantity of tar or bitumen required for the work as per standard formula, before using the same, and shall hypothecate it to the Engineer-in-Charge. If any bitumen or tar remains unused on completion of the work on account of lesser use of materials in actual execution for reasons other than authorised changes of specification and abandonment of portion of work, a corresponding deduction equivalent to the cost of unused materials as determined by the Engineer-in-Charge shall be made and the material returned to the contractor. Although the materials are hypothecated to HLL, the contractor undertakes the responsibility for their proper watch, safe custody and protection against all risks. The materials shall not be removed from site of work without the consent of the Engineer-in-Charge in writing.

iii)	The contractor shall be responsible for rectifying defects noticed within a year from the date of completion of the work and the portion of security deposit relating to asphaltic work shall be refunded after the expiry of this period

CLAUSE 36

Contractors Superintendence, Supervision, Technical Staff & Employees

Employment of Technical Staff and employees

i)	The contractor shall provide all necessary superintendence during execution of the work and as long thereafter as may be necessary for proper fulfilling of the obligations under the contract.

The contractor shall immediately after receiving letter of acceptance of the tender and before commencement of the work, intimate in writing to the Engineer-in-Charge the name, qualifications, experience, age, address and other particulars along with certificates, of the principal technical representative to be in charge of the work. Such qualifications and experience shall not be lower than specified in Schedule ‘F’. The Engineer-in-Charge shall within 15 days of receipt of such communication intimate in writing his approval or otherwise of such representative to the contractor. Any such approval may at any time be withdrawn and in case of such withdrawal, the contractor shall appoint another such representative according to the provisions of this clause. Decision of the Engineer-in-Charge shall be final and binding on the contractor in this respect. Such a principal technical representative shall be appointed by the contractor soon after receipt of the approval from the Engineer-in-Charge and shall be available at site within fifteen days of start of the work.

If the contractor (or any partner in case of firm/company) who himself has such qualifications, it will not be necessary for the said contractor to appoint such a principal technical representative but the contractor shall designate and appoint a responsible agent to represent him and to be present at the work whenever the contractor is not in a position to be so present. All the provisions applicable to the principal technical representative under the Clause will also be applicable in such a case to contractor or his responsible agent. The principal technical representative and/or the contractor shall on receiving reasonable notice from the Engineer-in-Charge or his designated representative(s) in charge of the work in writing or in person or otherwise, present himself to the Engineer-in-Charge and/or at the site of work, as required, to take instructions. Instructions given to the Principal technical representative or the responsible agent shall be deemed to have the same force as if these have been given to the contractor. The principal technical representative and/or the contractor or his responsible authorised agent shall be actually available at site atleast two working days every week, these days shall be determined in consultation with the Engineer-in-Charge as well as fully during important stages of execution of work, during recording measurement of works and whenever so required by the Engineer-in-Charge by a notice as aforesaid and shall also note down instructions conveyed by the Engineer-in-Charge or his designated representative in the site order book and shall affix his signature in  token of noting down the instructions and in token of acceptance of measurements. There shall be no objection if the representative/agent looks after more than one work and not more than three works in the same station provided these details are disclosed to the Engineer-in-Charge and he shall be satisfied that the provisions and purpose of this clause are fulfilled satisfactorily.

If the Engineer-in-Charge, whose decision in this respect is final and binding on the contractor, is convinced that no such technical representative or agent is effectively appointed or is effectively attending or fulfilling the provisions of this clause, a recovery shall be effected from the contractor as specified in Schedule ‘F’ and the decision of the Engineer-in-Charge as recorded in the site order book and measurement recorded in Measurement Books shall be final and binding on the contractor. Further if the contractor fails to appoint a suitable technical representative or responsible agent and if such appointed persons are not effectively present or do not discharge their responsibilities satisfactorily, the Engineer-in-Charge shall have full powers to suspend the execution of the work until such date as a suitable agent is appointed and the contractor shall be held responsible for the delay so caused to the work. The contractor shall submit a certificate of employment of the technical representative/ responsible agent along-with every on account bill/ final bill and shall produce evidence if at any time so required by the Engineer-in-Charge.

ii)	The contractor shall also provide and employ on the site the required complement of technical assistants and foreman who are skilled and experienced in their respective fields for proper supervision of the work.

The contractor shall provide and employ skilled, semi skilled and unskilled labour as is necessary for proper and timely execution of the work.

The Engineer-in-Charge shall be at liberty to object to and require the contractor to remove from the works any person who in his opinion misconducts himself, or is incompetent or negligent in the performance of his duties or whose employment is otherwise considered by the Engineer-in-Charge to be undesirable. Such person shall not be employed again at works site without the written permission of the Engineer-in-Charge and the person so removed shall be replaced as soon as possible by competent substitutes.

CLAUSE 37

Levy/ Taxes Payable by Contractor

- Sales Tax or any other tax on materials in respect of this contract shall be payable by the contractor and HLL shall not entertain any claim whatsoever in this respect.

- The contractor shall deposit royalty and obtain necessary permit for supply of the red bajri, stone, kankar, etc. from local authorities.

- If pursuant to or under any law, notification or order any royalty, cess or the like becomes payable by the HLL of India and does not anytime become payable by the contractor to the State HLL, Local authorities in respect of any material used by the contractor in the works then in such a case, it shall be lawful to the HLL of India and it will have the right and be entitled to recover the amount paid in circumstances as aforesaid from dues of the contractor.

CLAUSE 38

All tendered rates shall be inclusive of all taxes and levies payable under respective statutes. However, pursuant to the constitution (46th Amendment) Act, 1982, if any further tax or levy is imposed by statute, the last stipulated date for the receipt of tender including extensions, if any, and the contractor thereupon necessarily and properly pays  such taxes/levies the contractor shall be reimbursed the amount so paid, provided such payments, if any, is not, in the opinion of the Engineer in Charge ( whose decision shall be final and binding on the contractor) attributable to delay in execution of  work within the control of the contractor.

Conditions for reimbursement of Levy/ Taxes, if levied after receipt of tenders

- The contractor shall keep necessary books of accounts and other documents for the purpose of this condition as may be necessary and shall allow inspection of the same by a duly authorised representative of the HLL and/or the Engineer-in-Charge and further shall furnish such other information/document as the Engineer-in-Charge may require from time to time.

- The contractor shall, within a period of 30 days of the imposition of any such further tax or levy, pursuant to the Constitution (Forty Sixth Amendment) Act 1982, give a written notice thereof to the Engineer-in-Charge that the same is given pursuant to this condition, together with all necessary information relating thereto.

CLAUSE 39

Termination of Contract on death of Contractor

Without prejudice to any of the rights or remedies under this contract if the contractor dies, the Engineer-in-Charge on behalf of the HLL LifecareLimited shall have the option of terminating the contract without compensation to the contractor.

CLAUSE 40

If relation working in HLL, then Contractor not allowed to tender

The company or firm or any other person shall not be permitted to tender for works in HLL Civil Zone in which his near relative (s) (directly recruited or on deputation in HLL) is/are posted in any capacity either non-executive or executive employee.

The contractor shall also intimate the names of persons who are working with him in any capacity or are subsequently employed by him and who are near relative to any executive employee/ gazetted officer in the HLL or Ministry of Health and Family Welfare.

Any breach of these conditions by the Company or Firm or any other person, the tender/work will be cancelled and Earnest Money/ Security Deposit will be forfeited at any stage, whenever it is so noticed. The department will not pay any damages to the company or Firm or the concerned person. The Company or Firm or the person will also be debarred for further participation in the tender in the concerned HLL Civil Zone. Further, any breach of this condition by the tenderer would also render him liable to be removed from the approved list of contractors or this Department. If however the contractor is registered in any other Department he shall also be debarred from tendering in HLL for any breach of this condition.

NOTE :- Near relative (s) for this purpose is/are defined as : –

- Member of Hindu Undivided family (UHF).

- They are Husband and Wife.

- The one is related to other in the manner as father, mother, son(s) & Son’s wife (daughter-in-law), Daughter(s), Daughter’s husband (son-in-law), brother(s), brother’s wife, sister(s), sister’s husband (brother-in-law).

CLAUSE 41

No Gazetted Officer/ Engineer to work as Contractor within two years of Retirement

No engineer of gazetted rank or other gazetted officer employed in engineering or administrative duties in an engineering department of the Government of India shall work as a contractor or employee of a contractor for a period of two years after his retirement from Government service without the previous permission of Government of India in writing. This contract is liable to be cancelled if either the contractor or any of his employees is found at any time to be such a person who had not obtained the permission of Government of India as aforesaid, before submission of the tender or engagement in the contractor’s service, as the case may be.

CLAUSE 42  DELETED

CLAUSE 43

The work (whether fully constructed or not) and all materials, machines, tools and plants, scaffolding, temporary buildings and other things connected there-with, shall be at the risk of the contractor until the work has been delivered to the Engineer-in-Charge and a certificate from him to that effect obtained. In the event of the work or any materials properly brought to the site for incorporation in the work being damaged or destroyed in consequence of hostilities or warlike operation, the contractor shall, when ordered (in writing) by the Engineer-in-Charge to remove any debris from the site, collect and properly stack or remove in store all serviceable materials salvaged from the damaged work and shall be paid at the contract rates in accordance with the provisions of the agreement for the work of clearing the site of debris, stacking or removal of serviceable material and for reconstruction of all works ordered by the Engineer-in-Charge, such payments being in addition to compensation upto the value of the work originally executed before being damaged or destroyed and not paid for. In case of works damaged or destroyed but not already measured and paid for, the compensation shall be assessed by the Engineer-in-Charge upto Rs.5000/- and by the DGM(ID) for a higher amount. The contractor shall be paid for the damages/destruction suffered and for the restoring the material at the rate based on analysis of rates tendered for in accordance with the provisions of the contract. The certificate of the Engineer-in-Charge regarding the quality and quantity of  materials and purpose for which they were collected shall be final and binding on all parties to this contract.

Compensation during warlike situations

Provided always that no compensation shall be payable for any loss in consequence of hostilities or warlike operation (a) unless the contractor had taken all such precautions against air raid as are deemed necessary by the A.R.P. Officers or the Engineer-in-Charge (b) for any materials etc. not on the site of the work or for any tools, plant, machinery, scaffolding, temporary building and other things not intended for the work.

In the event of the contractor having to carry out reconstruction as aforesaid, he shall be allowed such extension of time for its completion as is considered reasonable by the Engineer-in-Charge.

CLAUSE 44

Apprentices Act provisions to be complied with

The contractor shall comply with the provisions of the Apprentices Act, 1961 and the rules and orders issued thereunder from time to time. If he fails to do so, his failure will be a breach of the contract and the Engineer-in-charge may, in his discretion, cancel the contract. The contractor shall also be liable for any pecuniary liability arising on account of any violation by him of the provisions of the said Act.

CLAUSE 45

Security Deposit of the work shall not be refunded till the contractor produces a clearance certificate from the Labour Officer. As soon as the work is virtually complete the contractor shall apply for the clearance certificate to the Labour Officer under intimation to the Engineer-in-Charge. The Engineer-in-Charge, on receipt of the said communication, shall write to the Labour Officer to intimate if any complaint is pending against the contractor in respect of the work. If no complaint is pending, on record till after 3 months after the completion of the work and/or no communication is received from the Labour Officer to this effect till six months after the date of completion, it will be deemed to have received the clearance certificate and the Security Deposit will be released if otherwise due.

Release of Security Deposit after labour clearance

CLAUSE 46

Without limiting the Contractor’s obligations and responsibilities stated elsewhere in the Contract, the Contractor shall at his own cost arrange, secure and maintain insurance in the joint names of the HLL and the contractor with any of the subsidiary of the General Insurance Corporation of India in such a manner that the HLL and the contractor are covered for all time during the period of contract i.e. the time period allowed for completion of work, extended period and the defect liability period.  The insurance shall be effected in accordance with terms approved by the HLL and the contractor shall submit the insurance policies to the Engineer-In-Charge within one week of signing of the agreement along with the receipt of premium.  The contractor shall timely pay and submit the receipts of payment of premiums for extensions of policies, if any. The insurance shall cover the following:-

Insurance

- Contractor’s All Risks Insurance

The contractor shall insure the work for a sum equivalent to the Contract value or such additional sums as specified and the interests of the HLL against ALL RISKS claims, proceedings, loss or damages, costs, charges and expenses from whatsoever cause arising out of or in consequence of the execution and maintenance of the work for which the contractor is responsible under the contract

- Workman Compensation & Employers Liability Insurance.

This insurance shall be effected for all the contractor’s employees engaged in the performance of the contract.  The HLL shall not be liable in respect of any damages or compensation payable at law in respect of or in consequence of any accident or injury to any workman or any other person in the employment of the contractor and the contractor shall indemnify and keep indemnified the HLL against all such damages and compensation and against all claims, demands, proceedings, costs, charges and expenses, whatsoever in respect or in relation thereof.

- Third Party Insurance.

The contractor shall be responsible for making good to the satisfaction of the Engineer-in-Charge any loss or any damage to all structures and properties belonging to the HLL or being executed or procured or being procured by the HLL or of the other agencies within the premises of all work of the HLL.  If such loss or damage is due to fault and or the negligence or willful acts or omissions of the contractor, his employees, agents, representatives.

The contractor shall take sufficient care in moving his plants, equipments and materials from one place to another so that they do not cause any damage to any person or to the property of the HLL or any third party including overhead and underground cables and in the event of any damage resulting to the property of the HLL or to a third party during the movement of the aforesaid plant, equipment or materials, the cost of such damages including eventual loss of production, operation or services in any plant or establishment as estimated by the HLL or ascertained or demanded by the third party, shall be borne by the contractor.

Before commencing the execution of the work, the contractor, shall insure and indemnify and keep the HLL harmless of all claims, against the contractor’s liability for any materials or physical damage, loss or injury which may occur to any property, including that of the HLL or to any person including any employee of HLL, or arising out of the execution of the work or in the carrying out of the contract, otherwise than due to the matters referred to in the provision to (a) above.   Such insurance shall be effected for an amount sufficient to cover such risks.  The terms shall include a provision whereby, in the event of any claim in respect of which the contractor, would be entitled to receive indemnify under the policy being brought or made against the HLL, the insurer willfully indemnify HLL against such claims and any costs, charges and expenses in respect thereof.

- The contractor shall also at times indemnify the HLL against all claims, damages or compensation under the provisions of Payment or Wages Act, 1936, Minimum Wages Act, 1948, Employer’s Liability Act, 1938, the Workman’s Compensation Act, 1947, Industrial Disputes Act, 1947 and Maternity Benefit Act, 1961, or any modification thereof or any other law relating thereof and rules made there under from time to time.

- Contractor shall also at his own cost carry and maintain any and all other insurance(s) which he may be required to take out under any law or regulation from time to time.  He shall also carry and maintain any other insurance, which may be required by the Engineer-in-Charge.

  - The Contractor shall prove to the Engineer-in-charge from time to time he has taken out all the insurance policies referred to above and has paid  the necessary premiums for keeping the policies alive till expiry of the Defects Liability Period.

  - The aforesaid insurance policies shall provide that they shall not be cancelled till the Engineer-in-charge has agreed for cancellation.

  - Remedy on the contractor’s failure to insure

If the contractor shall fail to effect and keep in force the insurance referred to above or any other insurance which he/they may be required to effect under the terms of the contract then and in any such case Engineer-in-charge may without being bound to, effect and keep in force any such insurance and pay such premium or premiums, as may be necessary for that purpose and from time to time deduct the amount so paid by the Engineer-in-charge from any moneys due or which may become due to the contractor or recover the same as a debt due from the contractor.

SAFETY CODE

- Suitable scaffolds should be provided for workmen for all works that cannot safely be done from the ground, or from solid construction except such short period work as can be done safely from ladders.  When a ladder is used an extra Mazdoor shall be engaged for holding the ladder and if the ladder is used for carrying materials as well suitable footholds and hand-hold shall be provided on the ladder and the ladder shall be given an inclination not steeper than ¼ to 1 (1/4 horizontal and 1 vertical).

- Scaffolding of staging more than 3.6 m (12 ft.) above the ground or floor, swung or suspended from an overhead support or erected with stationary support shall have a guard rail properly attached or bolted, braced and otherwise secured atleast 90 cm (3 ft.) high above the floor or platform of such scaffolding or staging and extending along the entire length of the outside and ends thereof with only such opening as may be necessary for the delivery of materials. Such scaffolding or staging shall be so fastened as to prevent it from swaying from the building or structure.

- Working Platforms, gangways and stairways should be so constructed that they should not sag unduly or unequally, and if the height of the platform or the gangway or the stairway is more than 3.6 ms (12 ft.) above ground level or floor level, they should be closely boarded, should have adequate width and should be suitably fastened as described in (2) above.

- Every opening in the floor of a building or in a working platform shall be provided with suitable means to prevent the fall of person or materials by providing suitable fencing or railing whose minimum height shall be 90 cm (3 ft.).

- Safe means of access shall be provided to all working platforms and other working places.  Every ladder shall be securely fixed.  No portable single ladder shall be over 9 m (30 ft) in length while the width between side rails in rung ladder shall in no case be less than 29 cm. (11 ½”) for ladder upto and including 3 metre (10 ft.) in length.  For longer ladders this width should be increased atleast ¼” for each additional 30 cm.(1 foot) of length.  Uniform step spacing of not more than 30 cm shall be kept.  Adequate precautions shall be taken to prevent danger from electrical equipment.  No materials on any of the sites or work shall be so stacked or placed as to cause danger or inconvenience to any person or the public.  The contractor shall provide all  necessary fencing and lights to protect the public from accident and shall be bound to bear the expenses of defence of every suit, action or other proceedings at law that may be brought by any person for injury sustained owing to neglect of the above precautions and to pay any damages and cost which maybe awarded in any such suit, action or proceedings to any such person or which may, with the consent of the contractor, be paid to compensate any  claim by any such person.

- Excavation and trenching- All trenches 1.2 m (4 ft,) or more in depth, shall at all times be supplied with atleast one ladder for each 30 metre (100 ft) in length or fraction thereof.  Ladder shall extend from bottom of the trench to atleast 90 cm. (3 ft) above the surface of the ground.  The sides of the trenches, which are 1.5 m (5 ft) or more in depth shall be stepped back to give suitable slope or securely held by timber bracing, so as to avoid the danger of sides collapsing. The excavated material shall not be placed within 1.5 m (5 ft) of the edges of the trench or half of the depth of the trench whichever is more.  Cutting shall be done from top to bottom.  Under no circumstances undermining or undercutting shall be done.

- Demolition. - Before any demolition work is commenced and also during the progress of the work,

- All roads and open areas adjacent to the work site shall either be closed or suitably protected.

- No electric cable or apparatus which is liable to be a source of danger or a cable or apparatus used by the operator shall remain electrically charged.

- All practical steps shall be taken to prevent danger to persons employed from risk of fire or explosion or flooding.  No floor, roof or other part of the building shall be so overloaded with debris or materials as to render it unsafe.

- All necessary personal safety equipment as considered adequate by the Engineer-in-Charge should be kept available for the use of the person employed on the site and maintained in a condition suitable for immediate use, and the contractor should take adequate steps to ensure proper use of equipment by those concerned. The following safety equipment shall invariably be provided.

- Workers employed on mixing asphaltic materials, cement and lime mortars shall be provided with protective footwear and protective goggles.

- Those engaged in whitewashing and mixing or stacking of cement bags or any material, which is injurious to the eyes, shall be provided with protective goggles.

- Those engaged in welding works shall be provided with welder’s protective eye shields.

- Stonebreakers shall be provided with protective goggles and protective clothing and seated at sufficiently safe intervals.

- When workers are employed in sewers and manholes, which are in active use, the contractors shall ensure that the manhole covers are opened and ventilated atleast for an hour before the workers are allowed to get into manholes and the manholes so opened shall be cordoned off with suitable railing and provided with warning signals or boards to prevent accident to the public.  In addition , the contractor shall ensure that the following safety measures are adhered to:-

- Entry for workers into the line shall not be allowed except under supervision of the Engineer in Charge or any other higher officer.

- Atleast 5 to 6 manholes upstream and downstream should be kept open for atleast 2 to 3 hours before any man is allowed to enter into the manhole for working inside.

- Before entry presence of toxic gases should be tested by inserting wet lead acetate paper, which changes colour in the presence of such gases and gives indication of their presence.

- Presence of oxygen should be verified by lowering a detector lamp into the manhole.  In case, no oxygen is found inside the sewer line, worker should be send only with oxygen kit.

- Safety belt with rope should be provided to the workers.  While working inside the manhole such rope should be handled by two men standing outside to enable him to be pulled out during emergency.

- The area should be barricaded or cordoned off by suitable means to avoid mishaps of any kind. Proper warning signs should be displayed for the safety of the public whenever for the cleaning works are undertaken during night or day.

- No smoking or open flames shall be allowed near the blocked manhole being cleaned.

- The malba obtained on account of cleaning of blocked manholes and sewer lines should be immediately removed to avoid accidents on account of slippery nature of the malba.

- Workers should not be allowed to work inside the manhole continuously. He should be given rest intermittently. The Engineer-in-Charge may decide the time upto which worker may be allowed to work continuously inside the manhole.

- Gas masks with Oxygen cylinder should be kept at site for use in emergency.

- Air blowers should be used for flow of fresh air through the manholes. Whenever called for, portable air blowers are recommended for ventilating the manholes. The motors for these, shall be vapour proof and of totally enclosed type. Non-sparking gas engines also could be used but they should be placed at least 2 metres away from the opening and on the leeward side, protected from wind so that they will not be the source of friction on any inflammable gas that might be present.

- The workers engaged for cleaning the manholes/sewers should be properly trained before allowing working in the manhole.

- The worker shall be provided with Gumboots or non-sparking shoes bump helmets and gloves non-sparking tools and safety lights and gas masks and portable air-blowers (when necessary). They must be supplied with barrier cream for anointing the limits before working inside the sewer lines.

- Workmen descending a manhole shall try each ladder stop or rung carefully before putting his full weight on it to guard against insecure fastening due to corrosion of the rung fixed to manhole well.

- If a man has received a physical injury, he should be brought out of the sewer immediately and adequate medical aid should be provided to him.

- The extent to which these precautions are to be taken depend on individual situation but the decision of the Engineer-in-Charge regarding the steps to be taken in this regard in an individual case will be final.

- The contractor shall not employ men and women below the age of 18 years on the work of painting with products containing lead in any form. Whenever men above the age of 18 years are employed on the work of lead painting, the following precautions should be taken: -

- No paint containing lead or lead products shall be used except in the form of paste or readymade paint.

- Suitable face masks should be supplied for use by the workers when paint is applied in the form of spray or a surface having lead paint is dry rubbed and scrapped.

- Overalls shall be supplied by the contractors to the workmen and adequate facilities shall be provided to enable the working painters to wash during and on the cessation of work.

- The Contractor shall not employ women and men below the age of 18 years on the work of painting with product containing lead in any form. Whenever men above the age of 18 are employed on the work of lead painting, the following principles must be observed for such use:

- White lead, sulphate of lead or product containing these pigments, shall not be used in painting operation except in the form of pastes or paint ready for use.

- Measures shall be taken, wherever required in order to prevent danger arising from the application of paint in the form of spray.

- Measures shall be taken, wherever practicable to prevent danger arising out of from dust caused by dry rubbing down and scrapping.

- Adequate facilities shall be provided to enable working painters to wash during and on cessation of work.

- Overall shall be worn by working painters during the whole of working period.

- Suitable arrangement shall be made to prevent clothing put off during working hours being spoiled by painting materials.

- Cases of lead poisoning and suspected lead poisoning shall be notified and shall be subsequently verified by medical man appointed by the competent authority of HLL

- HLL may require, when necessary, medical examination of workers.

- Instructions with regard to special hygienic precautions, to be taken in the painting trade, shall be distributed to working painters.

- When the work is done near any place where there is risk of drowning, all necessary equipment should be provided & kept ready for use and all necessary steps taken for prompt rescue of any person in danger and adequate provision, should be made for prompt first aid treatment of all injuries likely to be obtained during the course of the work.

- Use of hoisting machines and tackle including their attachments, anchorage and supports shall conform to the following standards or conditions: -

i)	(a)	These shall be of good mechanical construction, sound materials and adequate strength and free from  patent defects and shall be kept repaired and in good working order.

(b)	Every rope used in hoisting or lowering materials or as means of suspension shall be of durable quality and adequate strength, and free from patent defects.

(ii)	Every crane driver or hoisting appliance operator shall be properly qualified and no person under the age of 21 years should be in charge of any hoisting machine including any scaffolding winch or give signals to operator.

(iii)	In case of every hoisting machine and of every chain ring hook, shackle swivel and pulley blocks used in hoisting or as means of suspension the safe working load shall be ascertained by adequate means. Every hoisting machine and all gear referred to above shall be plainly marked with the safe working load. In case of hoisting machine having a variable safe working load each safe working load and the condition under which it is applicable shall be clearly indicated. No part of any machine or any gear, referred to above in this paragraph shall be loaded beyond the safe working load except for the purpose of testing.

(iv)	In case of HLL machines, the safe working load shall be notified by the Electrical Engineer-in-Charge. As regard contractor’s machines the contractors shall notify the safe working load of the machines to the Engineer-in-Charge whenever he brings any machinery to the site of work and get it verified by the Electrical Engineer concerned.

- Motors, gearing, transmission, electric wiring and other dangerous parts of hoisting appliances should be provided with efficient safeguards. Hoisting appliances should be provided with such means as will reduce to the minimum the risk of accidental descent of the load. Adequate precautions should be taken to reduce to the minimum the risk of any part of a suspended load becoming accidentally displaced. When workers are employed on electrical installations, which are already energised, insulating mats, wearing apparel, such as gloves, sleeves and boots, as may be necessary, should be provided. The worker should not wear any rings, watches and carry keys or other materials, which are good conductors of electricity.

- All scaffolds ladders and other safety devices mentioned or described herein shall be maintained in safe condition and no scaffold, ladder or equipment shall be altered or removed while it is in use. Adequate washing facilities should be provided at or near places of work.

- These safety provisions should be brought to the notice of all concerned by display on a notice board at a prominent place at work spot. The person responsible for compliance of the safety code shall be named therein by the contractor.

- To ensure effective enforcement of the rules and regulations relating to safety precautions the arrangements made by the contractor shall be open to inspection by Labour Officer or the Engineer-in-Charge or their representatives.

- Notwithstanding the above clauses from (1) to (15) there is nothing in these to exempt the contractor from the operations of any other Act or Rule in force in the Republic of India.

MODEL RULES FOR THE PROTECTION OF HEALTH AND SANITARY ARRANGEMENTS FOR WORKERS EMPLOYED BY

HLL LIFECARELIMITED OR ITS CONTRACTORS

- APPLICATION

These rules shall apply to all buildings and construction works in charge of the HLL LifecareLtd in which twenty or more workers are ordinarily employed or are proposed to be employed in any day during the period during which the contract work is in progress.

- DEFINITION

Work place means a place where twenty or more workers are ordinarily employed in connection with construction work, on any day during the period, during which the contract work is in progress.

- FIRST-AID FACILITIES

- At every work place there shall be provided and maintained, so as to be easily accessible during working hours, first aid boxes at the rate of not less than one box for 150-contract labour or part thereof ordinarily employed.

- The first-aid box shall be distinctly marked with a red cross on white back ground and shall contain the following equipment: -

- For work places in which the number of contract labour employed does not exceed 50- Each first-aid box shall contain the following equipment: -

- 6 small sterilised dressings.

- 3 medium size sterilised dressings.

- 3 large size sterilised dressings.

- 3 large sterilised burn dressings.

- 1 (30 ml.) bottle containing a two percent alcoholic solution of iodine

- 1 (30ml) bottle containing salvolatile having the dose and mode of administration indicated on the label.

- 1 snakebite lancet.

- 1 (30gms.) bottle of potassium permanganate crystals.

- 1 pair scissors.

- 1 copy of the first-aid leaflet issued by the Director General, Factory Advice Service and Labour Institute, Government of India.

- 1 Bottle containing 100 tablets (each of 5 gms.) of aspirin.

- Ointment for burns.

- A bottle of suitable surgical antiseptic solution

- For workplaces in which the number of contract labour exceeds 50- Each first–aid- box shall contain the following equipment.

- 12 small sterilised dressing.

- 6 medium size sterilised dressings.

- 6 large size sterilised dressings.

- 6 large size sterilised burn dressings.

- 6 (15-gms.) packets sterilised cotton wool.

- 1 (60 ml.) bottle containing two percent alcoholic solution iodine.

- 1 (60-ml.) bottle containing salvolite latile having the dose and mode of administration indicated on the label.

- 1 roll of adhesive plaster.

- 1 snake bite lancet.

- 1 (30 gms.) bottle of potassium permanganate crystals.

- 1 pair of scissors.

- 1 copy of the first-aid leaflet issued by the Director General Factory Advice Service and Labour Institute/ Government of India.

- A bottle containing 100 tablets (each of 5 gms.) of aspirin.

- Ointment for burns.

- A bottle of suitable surgical antiseptic solution.

iii)	Adequate arrangements shall be made for immediate recoupment of the equipment when necessary.

iv)	Nothing except the prescribed contents shall be kept in the First-aid box.

v)	The first-aid box shall be kept in charge of a responsible person who shall always be readily available during the working hours at the work place.

vi)	A person in charge of the first-aid box shall be a person trained in First-Aid treatment, at the work places where the number of contract labour employed is 150 or more.

vii)	In work places where the number of contract labour employed is 500 or more and hospital facilities are not available within easy distance from the works, First-aid posts shall be established and run by a trained compounder. The compounder shall be on duty and shall be available at all hours when the workers are at work.

viii)       	Where work places are situated in places, which are not towns or cities, a suitable motor transport shall be kept readily available to carry injured person or person suddenly taken ill to the nearest hospital.

- DRINKING WATER

- In every work place, there shall be provided and maintained, at suitable places, easily accessible to labour, a sufficient supply of cold water fit for drinking.

- Where drinking water is obtained from an intermittent public water supply, each work place shall be provided with storage where such drinking water shall be stored.

- Every water supply or storage shall be at a distance of not less than 50 feet from any latrine drain or other source of pollution. Where water has to be drawn from an existing well, which is within such proximity of latrine, drain or any other source of pollution, the well shall be properly chlorinated before water is drawn from it or for drinking. All such wells shall be entirely closed in and be provided with a trap door, which shall be dust and waterproof.

- A reliable pump shall be fitted to each covered well, the trap door shall be kept locked and opened only for cleaning or inspection which shall be done at least once a month.

- WASHING FACILITIES

- In every work place adequate and suitable facilities for washing shall be provided and maintained for the use of contract labour employed therein.

- Separate and adequate cleaning facilities shall be provided for the use of male and female workers.

- Such facilities shall be conveniently accessible and shall be kept in clean and hygienic condition.

- LATRINES AND URINALS

- Latrines shall be provided in every work place on the following scale namely:-

- Where female are employed there shall be at least one latrine for every 25 females.

- Where males are employed, there shall be at least one latrine for every 25 males.

Provided that where the number of males or females exceeds 100, it shall be sufficient if there is one latrine for 25 males or females as the case may be upto the first 100, and one for every 50 thereafter.

- Every latrine shall be under cover and so partitioned off as to secure privacy, and shall have a proper door and fastenings.

- Construction of latrines: The inside walls shall be constructed of masonry or some suitable heat-resisting nonabsorbent materials and shall be cement washed inside and outside at least once a year.  Latrines shall not be of a standard lower than bore-hole system.

- a) Where workers of both sexes are employed, there shall be displayed outside each block of latrine and urinal, a notice in the language understood by the majority of the workers “For Men only” or “For Women only” as the case may be.

b) The notice shall also bear the figure of a man or a woman, as the case may be.

- There shall be at least one urinal for upto 50 number of male workers and one for upto 50 number of female workers employed at a time, provided that where the number of male or female workers, as the case may be, exceeds 500, it shall be sufficient if there is one urinal for every 50 males or females, upto the first 500 and one for every 100 or part thereafter.

- a) The latrines and urinals shall be adequately lighted and shall be maintained in a clean and sanitary condition at all times.

b) Latrines and urinals other than those connected with a flush sewage system shall comply with the requirements of the Public Health Authorities.

- Water shall be provided by means of tap or otherwise so as to be conveniently accessible in or near the latrines and urinals.

- Disposal of excreta: - Unless otherwise arranged for by the local sanitary authority, arrangements for proper disposal of excreta by incineration at the work place shall be made by means of a suitable incinerator. Alternately excreta may be disposed off by putting a layer of night soil at the bottom of a pucca tank prepared for the purpose and covering it with a 15 cm. layer of waste or refuse and then covering it with a layer of earth for a fortnight (When it will turn to manure).

- The contractor shall at his own expense, carry out all instructions issued to him by the Engineer-in-Charge to effect proper disposal of night soil and other conservancy work in respect of the contractor’s workmen or employees on the site. The contractor shall be responsible for payment of any charges, which may be levied by Municipal or Cantonment Authority for execution of such on his behalf.

- PROVISION OF SHELTER DURING REST

At every place there shall be provided, free of cost, four suitable sheds, two for meals and the other two for rest separately for the use of men and women labour. The height of each shelter shall not be less than 3 metres (10 ft.) from the floor level to the lowest part of the roof. These shall be kept clean and the space provided shall be on the basis of 0.6 sq. m. (6 sft.) per head.

Provided that the Engineer-in-Charge may permit subject to his satisfaction, a portion of the building under construction or other alternative accommodation to be used for the purpose.

- CRECHES

- At every work place, at which 20 or more women worker are ordinarily employed, there shall be provided two rooms of reasonable dimensions for the use of their children under the age of six years. One room shall be used as a playroom for the children and the other as their bedroom. The rooms shall be constructed with specifications as per clause 19 H (ii) a, b & c.

- The rooms shall be provided with suitable and sufficient openings for light and ventilation. There shall be adequate provision of sweepers to keep the places clean.

- The contractor shall supply adequate number of toys and games in the playroom and sufficient number of cots and beddings in the bedroom.

- The contractor shall provide one ayah to look after the children in the crèche when the number of women workers does not exceed 50 and two when the number of women workers exceeds 50.

- The use of the rooms earmarked as crèches shall be restricted to children, their attendants and mothers of the children.

- CANTEENS

- In every work place where the work regarding the employment of contract labour is likely to continue for six months and where in contract labour numbering one hundred or more are ordinarily employed, an adequate canteen shall be provided by the contractor for the use of such contract labour.

- The contractor shall maintain the canteen in an efficient manner.

- The canteen shall consist of atleast a dining hall, kitchen, storeroom, pantry and washing places, separately for workers and utensils.

- The canteen shall be sufficiently lighted at all times when any person has access to it.

- The floor shall be made of smooth and impervious materials and inside walls shall be lime-washed or colour washed atleast once in each year. Provided that the inside walls of the kitchen shall be lime-washed every 4 months.

- The premises of the canteen shall be maintained in a clean and sanitary condition.

- Wastewater shall be carried away in suitable covered drains and shall not be allowed to accumulate so as to cause a nuisance.

- Suitable arrangements shall be made for the collection and disposal of garbage.

- The dining hall shall accommodate at a time 30 percent of the contract labour working at a time.

- The floor area of the dining hall, excluding the area occupied by the service counter and any furniture, except tables and chairs, shall not be less than one square metre (10 sft.) per diner to be accommodated as prescribed in sub-Rule 9.

a) 	A portion of the dining hall and service counter shall be partitioned off and reserved for women workers in proportion to their number.

b)	Washing places for women shall be separate and screened to secure privacy.

- Sufficient tables’ stools, chair or benches shall be available for the number of diners to be accommodated as prescribed in sub-Rule 9.

- a)

1.	There shall be provided and maintained, sufficient utensils, crockery, furniture and any other equipment’s, necessary for the efficient running of the canteen.

- The furniture utensils and other equipment shall be maintained in a clean and hygienic condition.

b)

1.	Suitable clean cloths for the employees serving in the canteen shall be provided and maintained.

- A service counter, if provided, shall have top of smooth and impervious material.

- Suitable facilities including an adequate supply of hot water shall be provided for the cleaning of utensils and equipment’s.

- The foodstuffs and other items to be served in the canteen shall be in conformity with the normal habits of the contract labour.

- The charges for foodstuffs, beverages and any other items served in the canteen shall be based on ‘No profit, No loss’ and shall be conspicuously displayed in the canteen.

- In arriving at the price of food stuffs, and other articles served in the canteen, the following items shall not be taken into consideration as expenditure namely: -

- The rent of land and building.

- The depreciation and maintenance charge for the building and equipment’s provided for the canteen.

- The cost of purchase, repairs and replacement of equipment’s including furniture, crockery, cutlery and utensils.

- The water charges and other charges incurred for lighting and ventilation.

- The interest and amounts spent on the provision and maintenance of equipment’s provided for the canteen.

- Registered accountants and auditors shall audit the accounts pertaining to the canteen once every 12 months.

- ANTI-MALARIAL PRECAUTIONS

The contractor shall at his own expense, conform to all anti-malarial instructions given to him by the Engineer-in-Charge including the filling-up of any borrow pits which may have been dug by him.

- The above rules shall be incorporated in the contracts and in notices inviting tenders and shall form an integral part of the contracts.

- AMENDMENTS

HLL may, from time to time, add to or amend these rules and issue directions it may consider necessary for the purpose of removing any difficulty, which may arise in the administration thereof.

CONTRACTOR’S LABOUR REGULATIONS

- SHORT TITLE

These regulations may be called the Contractors Labour Regulations.

- DEFINITIONS

- Workman means, any person employed by HLL or its contractor directly or indirectly, through a subcontractor, with or without the knowledge of the HLL, to do any skilled, semiskilled or unskilled, manual, supervisory, technical or clerical work, for hire or reward, whether the terms of employment are expressed or implied, but does not include any person: -

- Who is employed mainly in a managerial or administrative capacity; or,

- Who, being employed in a supervisory capacity draws wages exceeding five hundred rupees per mensem or exercises either by the nature of the duties attached to the office or by reason of powers vested in him, functions mainly of managerial nature; or,

- Who is an out worker, that is to say, person to whom any article or materials are given out by or on behalf of the principal employers to be made up cleaned, washed, altered, ornamental finished, repaired adopted or otherwise processed for sale for the purpose of the trade or business of the principal employers and the process is to be carried out either in the home of the out worker or in same other premises, not being premises under the control and management of the principal employer.

ii)	Fair Wages means wages whether for time or piecework fixed and notified under the provision of the Minimum Wages Act from time to time.

iii)	Contractors shall include every person who undertakes to produce a given result other than a mere supply of goods or articles of manufacture through contract labour or who supplies contract labour for any work and includes a subcontractor.

- Wages shall have the same meaning as defined in the Payment of Wages Act.

i)	Normally working hours of an adult employee should not exceed 9 hours a  day  and in case of child 4 ½ hours a day. The working day shall be so arranged that inclusive of interval for rest, if any, it shall not spread over more than 12 hours on any day.

- When an adult worker is made to work for more than 9 hours on any day or for more than 48 hours in any week he shall be paid over time for the extra hours put in by him at double the ordinary rate of wages. Children shall not be made to work extra hours.

iii)	a)	Every worker shall be given a weekly holiday normally on a Sunday, in accordance with the provisions of Minimum Wages  (Central) Rules 1960, as amended  from time to time, irrespective of whether such worker is governed by the Minimum Wages Act or not.

b)	Where the minimum wages prescribed by the HLL, under the Minimum Wages Act, are not inclusive of the wages for the weekly day of rest, the worker shall be entitled to rest day wages, at the rate applicable to the next preceding day, provided he has worked under the same contractor for a continuous period of not less than 6 days.

- Where a contractor is permitted by the Engineer-in-Charge to allow a worker to work on a normal weekly holiday, he shall grant a substituted holiday to him for the whole day, on one of the five days, immediately before or after the normal weekly holiday, and pay wages to such worker for the work performed on the normal weekly holiday at the overtime rate.

- DISPLAY OF NOTICE REGARDING WAGES ETC.

The contractor shall, before he commences his work on contract, display and correctly maintain and continue to display and correctly maintain, in a clear and legible condition in conspicuous places on the work, notices in English and in local Indian languages spoken by the majority of the workers, giving the minimum rates of the wages fixed under Minimum Wages Act, the actual wages being paid, the hours of work for which such wage are earned, wages periods, dates of payments of wages and other relevant information as per Appendix ‘III’.

- PAYMENT OF WAGES.

- The contractor shall fix wage periods in respect of which wages shall be payable.

- No wage period shall exceed one month.

- The wages of every person employed as contract labour in an establishment or by a contractor, where less than one thousand such persons are employed, shall be paid before the expiry of seventh day and in other cases before the expiry of tenth day after the last day of the wage period in respect of which the wages are payable.

- Where the employment of any worker is terminated by or on behalf of the contractor the wages earned by him shall be paid before the expiry of the second working day from the date on which his employment is terminated.

- All payment of wages shall be made on a working day at the work premises and during the working time and on a date notified in advance and in case the work is completed before the expiry of the wage period, final payment shall be made within 48 hours of the last working day.

- Wages due to every worker shall be paid to him direct or to other person authorised by him in this behalf.

- All wages shall be paid in current coin or currency or in both.

- Wages shall be paid without any deductions of any kind except those specified by the Central HLL by general or special order in this behalf or permissible under the Payment of Wages Act 1956.

- A notice showing the wages period and the place and time of disbursement of wages shall be displayed at the place of work and a copy sent by the contractor to the Engineer-in-Charge under acknowledgement.

- It shall be the duty of the contractor to ensure the disbursement of wages in presence of authorised representative of the Engineer-in-Charge who will be required to be present at the place and time of the disbursement of wages by the contractor to workmen.

- The contractor shall obtain from the or any other authorised representative of the Engineer-in-Charge, as the case may be, a certificate under his signature at the end of the entries in the “Register of Wages” or the “Wage-cum-Muster Roll”, as the case may be, in the following form: -

“Certified that the amount shown in the column No…………has been paid to the workman concerned in my presence on……….…..at…………”

- FINES AND DEDUCTIONS WHICH MAY BE MADE FROM WAGES

- The wages of a worker shall be paid to him without any deduction of any kind except the following: -

- Fines

- Deductions for absence from duty i.e. from the place or the places where by the terms of his employment he is required to work. The amount of deduction shall be in proportion to the period for which he was absent.

- Deductions for damage to or loss of goods expressly entrusted to the employed person for custody, or for loss of money or any other deductions which he is required to account, where such damage or loss is directly attributable to his neglect or default.

- Deduction for recovery of advances or for adjustment of overpayment of wages, advances granted shall be entered in a register.

- Any other deduction, which the Central Government may from time to time, allows.

- No fines should be imposed on any worker save in respect of such acts and omissions on his part as have been approved of by the Chief Labour Commissioner.

Note:- An approved list of Acts and Omission for which fines can be imposed is enclosed at Appendix-X.

- No fine shall be imposed on a worker and no deduction for damage or loss shall be made from his wages until the worker has been given an opportunity of showing cause against such fines or deductions.

- The total amount of fine, which may be imposed, in any one-wage period, on a worker, shall not exceed an amount equal to three paise in a rupee of the total wages, payable to him in respect of that wage period.

- No fine imposed on any worker shall be recovered from him by instalment, or after the expiry of sixty days from the date on which it was imposed.

- Every fine shall be deemed to have been imposed on the day of the act or omission in respect of which it was imposed.

- LABOUR RECORDS

- The contractor shall maintain a Register of Persons employed on work on contract in Form XIII of the CL (R&A) Central Rules 1971 (Appendix IV)

- The contractor shall maintain a Muster Roll register in respect of all workmen employed by him on the work under Contract in Form XVI of the CL (R&A) Rules 1971 (Appendix V)

- The contractor shall maintain a Wage Register in respect of all workmen employed by him on the work under contract in Form XVII of the CL (R&A) Rules 1971 (Appendix VI)

- Register of accident – The contractor shall maintain a register of accidents in such form as may be convenient at the work place but the same shall include the following particulars:

- Full Particulars of the labourers who met with accident.

- Rate of wages.

- sex

- Age

- Nature of accident and cause of accident

- Time and date of accident

- Date and time when admitted in hospital

- Date of discharge from the hospital

- Period of treatment and result of treatment

j) 	Percentage of loss of earning capacity and disability as assessed by Medical Officer.

k)	Claim required to be paid under Workmen’s Compensation Act.

- Date of payment of compensation

- Amount paid with details of the person to whom the same was paid

- Authority by whom the compensation was assessed

- Remarks.

v)	The contractor shall maintain a Register of Fines in the Form XII of the CL (R&A) Rules 1971 (Appendix XI) The contractor shall display in a good condition and in a conspicuous place of work the approved list of acts and omission for which fines can be imposed (Appendix X)

- The contractor shall maintain a Register of deductions for damage or loss in Form XX of the CL (R&A) Rules 1971 (Appendix XII).

vii)	The contractor shall maintain a Register of Advances in Form XXIII of the CL (R&A) Rules 1971 (Appendix-XIII).

- The contractor shall maintain a Register of Overtime in Form XXIII of the CL (R&A) Rules 1971 (Appendix-XIV).

- ATTENDANCE CARD-CUM WAGE SLIP

i)	The contractor shall issue an Attendance card cum wage slip to each workman employed by him in the specimen form at (Appendix-VII).

ii)	The card shall be valid for each wage period.

iii)	The contractor shall mark the attendance of each workman on the card twice each day, once at the commencement of the day and again after the rest interval, before he actually starts work.

iv)	The card shall remain in possession of the worker during the wage period under reference.

v)	The contractor shall complete the wage slip portion on the reverse of the card at least a day prior to the disbursement of wages in respect of the wage period under reference.

vi)	 The contractor shall obtain the signature or thumb impression of the worker on the wage slip at the time of disbursement of wages and retain the card with him.

9.	EMPLOYMENT CARD

The contractor shall issue an Employment Card in the Form XIV of CL (R&A) Central Rules 1971 to each worker within three days of the employment of the worker (Appendix-VIII).

- SERVICE CERTIFICATE

On termination of employment for any reason whatsoever the contractor shall issue to the workman whose services have been terminated, a Service Certificate in the Form XV of the CL (R&A) Central Rules 1971 (Appendix-IX).

- PRESERVATION OF LABOUR RECORDS

All records required to be maintained under Regulations Nos. 6 &7 shall be preserved in original for a period of three years from the date of last entries made in them and shall be made available for inspection by the Engineer-in-Charge or Labour Officer or any other officers authorised by the Ministry of Communication in this behalf.

- POWER OF LABOUR OFFICER TO MAKE INVESTIGATIONS OR ENQUIRY

The labour officer or any person authorised by the Central HLL on their behalf shall have power to make enquiries with a view to ascertaining and enforcing due and proper observance of Fair Wage Clauses and provisions of these Regulations. He shall investigate into any complaint regarding the default made by the contractor or subcontractor in regard to such provision.

13.	REPORT OF LABOUR OFFICER

The Labour Officer or other persons authorised as aforesaid shall submit a report of result of his investigation or enquiry to the Engineer in charge concerned indicating the extent, if any, to which the default has been committed with a note that necessary deductions from the contractor’s bill be made and the wages and other dues be paid to the labourers concerned.  In case an appeal is made by the contractor under Clause 13 of these regulations, actual payment to labourers will be made by the Engineer in charge after a decision has been made on such appeal.

- Engineer in charge shall arrange payments to the labour concerned within 45 days from the receipt of the report from the Labour Officer

14.	APPEAL AGAINST THE DECISION OF LABOUR OFFICER

Any person aggrieved by the decision and recommendations of the Labour Officer or other person so authorised may appeal against such decision to the Superintending Engineer concerned within 30 days from the date of decision, forwarding simultaneously a copy of his appeal to the Executive Engineer concerned but subject to such appeal, the decision of the officer shall be final and binding upon the contractor.

15.	PROHIBITION REGARDING REPRESENTATION THROUGH LAWYER

- A workman shall be entitled to be represented in any investigation or inquiry under these regulations by: -

- An officer of a registered trade union of which he is a member.

- An officer of a federation of trade unions to which the trade union referred to in Clause (a) is affiliated.

- Where the employer is not a member of any registered trade union, by an officer of a registered trade union, connected with the industry in which the worker is employed or by any other workman employed in the industry in which the worker is employed.

- An employer shall be entitled to be represented in any investigation or inquiry under these regulations by:-

- An officer of an association of employers of which he is a member.

- An officer of a federation of associations of employers to which association referred to in Clause (a) is affiliated.

- Where the employer is not a member of any association of employers, by an officer of association of employer connected with the industry, in which the employer is engaged or by any other employer, engaged in the industry in which the employer is engaged.

- No party shall be entitled to be represented by a legal practitioner in any investigation inquiry under these regulations.

16.	INSPECTION OF BOOKS AND SLIPS

The contractor shall allow inspection of all the prescribed labour records to any of his workers or to his agent at a convenient time and place after due notice is received or to the Labour Officer or any other person, authorised by the Central Government on his behalf.

17.	SUBMISSION OF RETURNS

The contractor shall submit periodical returns as may be specified from time to time.

18.	AMENDMENTS

The HLL may from time to time add to or amend the regulations and on any question as to the application/interpretation or effect of those regulations the decision of the Superintending Engineer concerned shall be final.

Appendix ’I’

REGISTER OF MATERNITY BENEFITS (Clause 19F)

Name and address of the contractor____________________________________

Name and Location of the work________________________________________

| Name of the Employee | Father’s/ husband’s name | Nature of Employment | Period of actual confinement | Date on which notice of given |
| --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 |

| Date on which maternity leave commenced and ended |  |  |  |  |
| --- | --- | --- | --- | --- |
| Date of Delivery/ Miscarriage | In case of delivery |  | In case of miscarriage |  |
|  | Commenced | Ended | Commenced | Ended |
| 6 | 7 | 8 | 9 | 10 |

| Leave pay paid to the employee |  |  |  | Remarks |
| --- | --- | --- | --- | --- |
| In case of delivery |  | In case of miscarriage |  |  |
| Rate of leave pay | Amount paid | Rate of leave pay | Amount paid |  |
| 11 | 12 | 13 | 14 | 15 |

Appendix ’II’

SPECIMEN FORM OF THE REGISTER,REGARDING

MATERNITY BENEFIT ADMISSIBLE TO THE CONTRACTOR’S LABOUR IN HLL LIFECARELIMITED.

Name and address of the contractor_______________________________

Name and location of the work___________________________________

- Name of the woman and her husband’s name.

- Designation

- Date of appointment.

- Date with months and years in which she is employed.

- Date of discharge / dismissal, if any.

- Date of production of certificates in respect of pregnancy.

- Date on which the woman informs about the expected delivery.

- Date of delivery / miscarriage / death.

- Date of production of certificates in respect of delivery / miscarriage.

- Date with the amount of maternity/ death benefit paid in advance of expected delivery.

- Date with amount of subsequent payment of maternity benefit.

- Name of the person nominated by the woman to receive the payment of the maternity benefit after her death.

- If the woman dies, the date of death, the name of the person to whom maternity benefit amount was paid, the month thereof and the date of payment.

- Signature of the contractor for authenticating entries in the register.

- Remarks column for the use of inspecting officer.

Appendix ’III’

LABOUR BOARD

Name of work:__________________________________________________

Name of Contractor:_____________________________________________

Address of Contractor:___________________________________________

Name and address of HLL Cenet:_______________________________

Name of HLL Labour Officer :____________________________________

Address of HLL Labour Officer:___________________________________

Name of Labour Enforcement Officer:_______________________________

Address of Labour Enforcement Officer:_____________________________

| Sl.No | Category | Minimum wage Fixed | Actual wage paid | Number Present | Remarks |
| --- | --- | --- | --- | --- | --- |

Weekly holiday_____________________________________________________

Wage period ______________________________________________________

Date of payment of Wages__________________________________________

Working hours____________________________________________________

Rest interval______________________________________________________

Appendix ’IV’

Form-XIII (See Rule 75)

Register of Workmen Employed by Contractor

Name and address of contractor_______________________________________

Name and address of establishment under which contract is carried on_______________________________________________________________

Nature and location of Work___________________________________________

Name and address of Principal Employer_______________________________

| Sl. No. | Name and surname of Workman | Age and Sex | Father’s/ Husband’s Name | Nature of employment / designation. | Permanent home address of the workman (Village and Tehsil, Taluka and District) | Local Address | Date of commencement of employment | Signature or thumb impression of the workman | Date Termination of employment. | Reasons For termination. | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |

Appendix ’V’

Form-XVI (See Rule 78(2)(a)

Muster Roll

Name and address of the contractor__________________________________

Name and address of establishment under which contract is carried on_____________________________________________________________

Nature and location of work_________________________________________

Name and address of Principal Employer______________________________

For the month of fortnight__________________________________________

| Sl. No. | Name of workman | Sex | Father’s/ Husband’s name | Dates |  |  |  |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 |  |  |  |  | 6 |
|  |  |  |  | 1 | 2 | 3 | 4 | 5 |  |

Appendix ’VI’

Form –XVII (See Rule 78(2)(a))

Register of Wages

Name and address of the contractor______________________________

Name and address of establishment under which

contract is carried on__________________________________________

Nature and location of work____________________________________

Name and address of Principal Employer_________________________

Wages period_______ Monthly/fortnightly

| Sl.No. | Name of workman | Serial No.in the register of workman | Designation Nature of work done | No. of days worked | Units of work done | Daily rate of wages/piece rate | Basic Wages |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |

| Dearness allowances | Overtime | Other cash payments(Indicate nature) | Total | Deductions if any, (indicate nature) | Net amount paid | Signature or thumb impression of the workman | Initial of contractor or his representative |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |

Appendix’VII’

(Observe)

Wage Card No.___________

Wage Card

Name and address of the contractor____________________ Date of issue_______

Name and location of work___________________________  Designation_______

Name of Workman__________________________________         Month/fortnight

Rate of Wages_______________________________________________

|  | DATE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Morning |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Evening |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Initial |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Rate_______________                                  Amount________________________________

Received from_____________________ the sum of Rs. _____________on account of my wages.

Signature

Appendix ’VII’

(Reverse)

Form-XIX

(See rule 78(2)(b))

Wages Slip

Name  and address of the contractor______________________________

Name and Father’s/Husband’s name of workman_____________________

Nature and location of work______________________________________

For the Week/Fortnight/Month ending______________________________

- No. of days worked  _____________________________________

- No. of units worked in case of piece rate workers______________

- Rate of daily wages/piece rate______________________________

- Amount of overtime wages_________________________________

- Gross wages payable_____________________________________

- Deduction, if any_________________________________________

- Net amount of wages paid________________________________

Initials of the Contractors or his representative

Appendix ’VIII’

Form-XIV

(See rule 76)

Employment Card

Name and address of the contractor__________________________________

Name and address of establishment under which contract is carried on_______________________________________________________________

Nature of work and location of work_____________________________________

Name and address of Principal Employer________________________________

- Name of Workman__________________________________________

- Sl No. in the register of workman employed_______________________

- Nature of employment/designation_______________________________

- Wage rate (with particulars of unit in case of piece work)_____________

- Wages period_______________________________________________

- Tenure of employment________________________________________

- Remarks___________________________________________________

Signature of contractor

Appendix ’IX’

Form-XV (See Rule 77)

Service Certificate

Name and address of the contractor____________________________________

Nature and location of work___________________________________________

Name and Address of workman________________________________________

Age or date of birth__________________________________________________

Identification marks_________________________________________________

Father’s/Husband’s name____________________________________________

Name and address of establishment in/under which contract is carried on_______________________________________________________________

Name and address of Principal Employer________________________________

| Sl.No. | Total period for which employed |  | Nature of work done | Rate of Wages (with particulars of unit in case of piece work) | Remarks |
| --- | --- | --- | --- | --- | --- |
|  | From | To |  |  |  |
| 1 | 2 | 3 | 4 | 5 | 6 |

Signature

Appendix ’X’

LIST OF ACTS AND OMISSIONS FOR WHICH FINES CAN BE IMPOSED

In accordance with rule 7 (v) of the HLL Contractors Labour Regulations to be displayed prominently at the site of work both in English and local Language.

- Wilful insubordination or disobedience, whether along or in combination with other.

- Theft fraud or dishonestly in connection with the contractors beside a business or property of HLL.

- Taking or giving bribes or any illegal gratifications.

- Habitual late attendance.

- Drunkenness fighting ,riotous or disorderly or indifferent behavior.

- Habitual negligence.

- Smoking near or around the area where combustible or other materials are locked.

- Habitual indiscipline.

- Causing damage to work in the progress or to property of the HLL or of the contractor.

- Sleeping on duty.

- Malingering or showing down work.

- Giving of false information regarding name and father’s name etc.

- Habitual loss of wage cards supplied by the employers.

- Unauthorized use of employer’s property of manufacturing or making of unauthorized articles at the work place.

- Bad workmanship in construction and maintenance by skilled workers which is not approved by the HLL and for which the contractors are compelled to undertake rectification.

- Making false complaints and/or misleading statements.

- Engaging on trade within the premises of the establishment.

- Any unauthorized divulgence of business affairs of the employees.

- Collection or canvassing for the collection of any money within the premises of an establishment unless authorized by the employer.

- Holding meeting inside the premises without previous sanction of the employers.

- Threatening or intimidating any workman or employer during the working hours within the premises.

Appendix ’XI’

Form-XII (See Rule 78(2)(d))

Register of Fines

Name and address of the contractors________________________________

Name and address of establishment under which contract is carried on___________________________________________________________

Nature and location of work_______________________________________

Name and address of Principal Employer_____________________________

| Sl.No. | Name of workman | Father’s/Husband’s name | Designation/nature of employment | Act/Omission For which fine imposed | Date of Offence |
| --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 |

| Whether workman Showed cause against fine | Name of person in whose presence employees explanation was heard | Wage period and wages payable | Amount of fine imposed | Date on which fine realized | Remarks. |
| --- | --- | --- | --- | --- | --- |
| 7 | 8 | 9 | 10 | 11 | 12 |

Appendix ’XII’

Form-XX(See Rule 78(2)(d))

Register of Deduction for Damage or Loss

Name and address of the contractors______________________________

Name and address of establishment under which contract is carried on__________________________________________________________

Nature and location of work______________________________________

Name and address of Principal Employer___________________________

| Sl.No. | Name of workman | Father’s/Husband’s name | Designation/nature of employment | Particulars of damage or loss | Date of damage or loss |
| --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 |

| Whether workman showed cause against fine | Name of person in whose presence employees explanation was heard |  | Amount of deduction imposed | No. of installments |  | Date of recovery |  |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | First installment | Last installment |  |  |
| 7 |  | 8 | 9 |  | 10 | 11 | 12 | 13 |  |

Appendix ’XIII’

Form-XXII (See Rule 78(2)(d)

Register of Advances

Name and address of the contractors_______________________________

Name and address of establishment under which contract is carried

on___________________________________________________________

Nature and location of work_______________________________________

Name and address of Principal Employer____________________________

| Sl. No. | Name of workman | Father’s/Husband’s name | Designation nature of employment | Wage period and wages payable | Date and Amount of Advance given | Purpose(s) for which Advance made | Number of Installments by which advance to be repaid | Date and amount of each installments repaid | Date on which last Installments was repaid | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |

Appendix ’XIV’

Form-XXIII (See Rule 78(2)(e))

Register of Overtime

Name and address of the contractors________________________________

Name and address of establishment under which contract is carried on ______________________________________________________________

Nature and location of work_______________________________________

Name and address of Principal Employer _____________________________

| Sl.No. | Name of workman | Father’s/husband’s name | Sex | Designation /nature of employment | Date on which Overtime worked | Total overtime worked or production incase of piece rated | Normal rate of wages | Overtime rate of wages | Overtime earnings | Rate on which overtime wages paid | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |

Technical Specifications For Elevators

1.1	This section deals with technical requirement of Electric Traction Type Passenger Elevator & Passenger Elevator Machine Room Less type, its components, and safety devices. All features shall be of latest International standards such as EN81, European standards, American standards or IS 14665 (part -1 to 5) and amended up to date. The technical specifications given below are for general guidance only and standard specifications of manufactures are acceptable subject to the condition that these specifications meet the technical / functional requirement specified below.

The contractor shall be responsible to check and ensure dimensions of hoist way, before tendering that requirements of statutory laws and local codes of Electrical / elevator inspector are met with and the equipment offered are suitable for the space available.

1.2	POWER SUPPLY

HLL shall provide 415 V+10%, 3 phases, 50 Hz AC power supply for the elevator at suitable location in top landing. Elevator shall be suitable for operation on 415 V+10%, 3 phases, 50 Hz AC power supply. Wiring shaft lighting and required electrical panel shall be carried out by the elevator contractor which shall be included in his quoted rates and nothing extra shall be paid on this account. All power required for erection, testing and handing over the elevator shall be in the scope of the contractor.

1.3	CODES & STANDARDS

1.3.1	Work carried out shall in general be in conformity with following:

- CPWD specification for electrical work.

- IS 14665 (part -1 to 5) and amended up to date or international specifications which ever is superior shall be applicable and in accordance with regulations of local codes which govern the requirements of the elevator.

- In addition, Indian Electricity Rules 1956 and Indian Electricity Act 1910 and the rules issued there under with amendments issued from time to time shall also apply.

- All the codes and standards mean the latest publication. Unless specified otherwise, the installation shall generally follow the Indian Standard code of practice/the relevant British Standard code of Practice.

1.3.2	All designs, materials, manufacturing techniques and workmanship shall be in accordance with accepted National or international standards/ practices for this type of equipment.

1.3.3	The tenderer shall also state, where applicable, the National or other International Standard (s) to which the whole or any specific part, of the equipment or system complies. In addition, any other information/ description, the tenderers may wish to provide, the features/ performance figures specified/indicated shall be with supporting documents/calculations.

1.4	TECHNICAL REQUIREMENT

| Sl.No. | Items | Technical requirement |
| --- | --- | --- |
| 1 | Type of Elevator | Passenger Lift |
| 2 | Capacity | 1020 Kgs (minimum), 15 Persons (minimum) |
| 3 | Speed | 1.00 Mtr/sec |
| 4 | Serving Floors | BF1,BF2, GF & FF. |
| 5 | Travel in meters | 14 M |
| 6 | Stops & Opening | 4 stops & 4 Openings. |
| 7 | Hoist Way available | Refer drawings attached to this tender document |
| 8 | Machine | Machine Room Less Gearless traction machine with electro-magnetic brake placed in the hoist way on top. |
| 9 | Control system | Micro-processor based control with variable voltage variable frequency technology. |
| 10 | Operation | Simplex full collective. |
| 11 | Car Enclosure | MS painted finish on all sides and ceiling for passenger lift. |
| 12 | Flooring | Granite flooring |
| 13 | Number of Entrance | Entrance at front side on all the serving floors (All stops – opening on the same side). (Refer drawings attached to this document) |
| 14 | Car & Hoist way Entrance (landing) Doors. | Automatic side/center opening automatic MS painted steel door, min 0.9m wide. |
| 15 | Safety Feature | (i) All safety feature required as per IS / International Standards. |
|  |  | (ii) Additional features. |
|  |  | a) Reverse phase relay on controller. |
|  |  | b) Single Phasing power supply protection. |
|  |  | c) Overload warning indicator on car (visual and audio) |
|  |  | d) Fireman’s switch |
|  |  | e) Battery operated alarm bell & emergency light with battery and charger. |
|  |  | f) Infra red rays sensing device along the edge of the car door for full height. |
| 16 | Signals | a) LED Hall buttons/ landing call registered indicator at all landings. |
|  |  | b) Digital car position indicator in car and at all landings with automatic announcement system. |
|  |  | c) Up/ Down pre-announcing indicator at all landings |
|  |  | d) Integral car operating panel with aesthetic luminous switches, emergency stop switch, key switch for auto/ attendant mode. |
|  |  | e) Annunciator in car |
| 17 | Fixtures (In car) | a) MS painted ceiling. |
|  |  | b) Concealed decorative luminaries with CFL lamps complete with housing, reflector and accessories. |
|  |  | c) Axial pressure fan suitable design to suit the ceiling. |
| 18 | Inter com (In car) | Suitable to hook to EPABX system. |
| 19 | Automatic rescue device. | Solid state battery operated device to automatically rescue passengers trapped in the elevator car in between floors in the event of power failure. |
| 20 | Manual Rescue Device | Manual rescue device shall also be provided so as to bring the elevator car to the nearest floor in the event of failure of battery operated automatic rescue device. |

1.5	 CONTROLLER

1.5.1	The control system shall be of microprocessor controller type, incorporating variable voltage variable frequency drive for elevators of 1.0 m/s speed. It shall be suitable for site programmability and shall have field test mechanism for quick fault diagnosis. The elevator motor shall be fed through this controller for smooth & silent operation of elevator.

1.6	ELEVATOR HOISTING MACHINE

1.6.1	Manufacturer’s standard design/constructional features are acceptable. The elevator hoisting machine shall be compact, energy efficient and proven design. The hoisting machinery shall be gearless type with 3 Phase AC motor. The drive shall be of variable voltage variable frequency type.

1.7	MOTOR

1.7.1	The elevator hoisting motor shall be as per manufacturer’s selection. Motor shall be dynamically balanced and shall have high starting torque and low starting current, suitable for elevator duty and equipped with required protection. Motor shall be part of drive unit.

1.8	INSTALLATION OF ELEVATOR HOISTING MACHINE

1.8.1	The required arrangement for installation of elevator hoisting machine shall be 	provided by the contractor.

1.9	GUIDE

1.9.1	Machined steel guides shall be provided for the car and counterweight. The guide rails shall have tongued and grooved joints, sliding clips shall be used for fastening the guides to allow building settlement without distorting the guide. The flanges shall be mechanical for the fish plate mounting so that rail alignments at joints almost remain constant. To keep down the noises level and to reduce wear and tear of sections, only Nylon ribs shall be used in the guide shoes. However, initially cast iron ribs shall be provided for smoothening of guide rails which shall later be replaced free of cost by Nylon ribs.

1.10	DRIVING MACHINE BRAKE

1.10.1	Electric elevator machine shall be equipped with brakes which shall be applied automatically by means of springs in compression only or by gravity when the operating device is in the ‘off’ position or in the event of power failure. The brake shall be designed to have a capacity sufficient to hold the car at rest with 125% of its rated load.

1.11	ROPES / FLAT BELTS

1.11.1	The elevator shall be provided with round stranded steel wire ropes or flat belts having tensile strength not less than 12.5 tone/ cm2. Lubricants between the strands shall be achieved by providing impregnated hemp core. The rope shall conform to IS –2365 – 1963 amended up to date.

1.12	LEVELING

1.12.1	Leveling with floors should be exact virtually independent of passenger load. This is to be achieved by self adaptive load compensation.

1.13	SELECTOR

Selector shall be as per OEM, however selector shall be microprocessor based.

1.14	CAR DETAILS

1.14.1  	CAR FRAME

The car frame shall be made of structural steel of rigid construction to withstand without permanent deformation the operation of safety gear. The car shall be so mounted on the frame that vibration and noise transmitted to the passengers inside is minimized.

1.15	CAR PLATFORM

1.15.1	The car platform shall be of framed construction and designed on the basis of rated load evenly distributed. The dimensions shall conform to IS – 3534 – 1968 amended up to date unless otherwise specified. The flooring shall be finished with antiskid material (sample shall be got approved).

1.16	CAR BODY

1.16.1	 The side walls of the car shall be as per SOQ.

1.17	CAR ROOF

1.17.1	The roof of the car shall be solid type with extra supporting arrangement capable of taking load of maintenance team (at least 140 Kg weight) and also have a fan and light fittings.

1.18	CAR DOOR

1.18.1	The car entrance doors shall be as per SOQ. Doors shall be automatic side/centre opening horizontal sliding and power operated type.

1.19	HOIST WAY (LANDING) DOORS

1.19.1	Doors shall be as per SOQ. It shall be fitted with a locking device which shall comply with clause 21 of IS –3-4666-1980 amended up to date.

1.20	CAR DOOR & HOIST WAY DOOR OPERATORS

1.20.1	(i)	Each hoist way door shall be provided with an interlock which shall prevent movement of the car away from the landing unless the door is in the closed position as defined in the IS codes.

- Door system should have the following features:

- Reliable robust construction, linear drive door gear with electronically controlled closing and opening for trouble free operation under adverse duty conditions.

- Door system interface compatible with modern micro-contactor control system for optimum performance.

- Proven door safety devices for maximum safety of users.

1.21	SAFETY GEARS & GOVERNORS

- Elevator shall be provided with car safety devices attached to the elevator car-frame and placed beneath the car. The safety device shall be capable of stopping and sustaining the elevator car with full rated load.

- The elevator shall be provided with over speed monitoring & tripping safety device and its operation shall be independent of power.

- The car safety is provided to stop the car whenever excessive descending speed is attained. The safety shall be operated by a centrifugal speed governor located at the top of hoist way and connected to the governor through a continuous steel rope. The governor shall be provided with ropes in proper tension. Even after ropes stretch, suitable means shall be applied to cut off power from motor and apply the brakes on applications of the safety.

- Temper proof infrared rays sensing device shall be provided through out the height of door or upto 1.8m above sill as per OEM to ensure the door reopens till the obstruction exits in case obstruction comes while the door is closing.

1.22	COUNTER BALANCE

1.22.1	A suitable guided structural steel frame with appropriate filler weights shall be furnished to promote smooth and economical operation.

1.23	TERMINAL SWITCHES

1.23.1	Elevator shall be provided with proximity switches arranged to stop the car automatically within the limits of top car clearance and bottom run by over travel from any speed attained in normal operation. Such switches shall Act independently of the operating device, the ultimate or final limit switches and the buffers.

Proximity switches may be fitted in the elevator car or in the elevator well or in the machine room and such switches shall be brought in to operation by the movement of elevator car.

An automatic safety switch shall be provided to stop the machine should the chain, rope or other similar device mechanically connecting the stopping device to the car, fail.

1.24	ULTIMATE OR FINAL SWITCHES

1.24.1	Elevator shall be provided with ultimate or final switches arranged to stop the car automatically within the top and bottom clearance independently of the normal operating device and the terminal switches.

Final switches shall act to prevent movement of the elevator car under power in both directions of travel and shall after operating remains open until the elevator car has been moved by a hand winding to a position within the limits of normal travel.

All ultimate or final switches shall be of enclosed type and shall be securely mounted. The contacts of all switches shall be opened positively and mechanically by the movement of elevator car.

1.25	TERMINAL BUFFERS

1.25.1	Heavy-duty spring Buffers/polyerethene rubber pads as per OEM to adhere the latest safety parameters shall be installed as a means of stopping the car and counter weight at the extreme limits of travel. Buffers in the pit shall be mounted on steel channels, which shall extend between both the car and counter weight guide rails. Oil buffer as per OEM standard is acceptable.

1.26	ELECTRICAL INSTALLATION REQUIREMENTS

1.26.1	IS: 4666 – 1980 amended up to date state the requirement for main switches and wiring with reference to relevant regulations and read in conjunction with clause-3.1 (i).

1.27	ELECTRICAL WIRING AND WIRING FOR SIGNALS

1.27.1	Complete electric wiring shall be done in copper cable/ wires by the elevator supplier as per clause 7.1.2 of IS: 1860-1980 amended up to date and read in conjunction with clause-3.1 (i).

The wiring for signals, landing call buttons & indicators shall use serial communication technique to reduce the number of wires and read in conjunction with clause-3.1 (i)

1.28	TRAVELLING CABLE

1.28.1	Flat traveling cable shall be 16/20 core to give better running performance.

1.29	OVER LOAD WARNING

1.29.1	Over load warning feature with audiovisual indication shall be provided (Visual indication shall show “Over Loaded” and a buzzer shall also operate). Car shall not move until the overload condition is removed.

1.29.2	A load plate giving the rated load and permissible maximum number of passengers should be fitted in each lift car in a conspicuous position.

1.30	INTERCOM SYSTEM

1.30.1	Intercom suitable to hook to EPABX shall be provided inside the car for making emergency calls.

1.31	EMERGENCY RESCUE DEVICE:

1.31.1	AUTOMATIC EMERGENCY RESCUE DEVICE:

Elevator system shall have automatic battery operated emergency rescue device to automatically rescue passengers trapped in the elevator car in between floors in the event of power failure having following features:

Automatic operation and immediate actions in the event of mains failure capable to move the elevator to the nearest landing, opens the doors automatically. Shall have sealed maintenance free battery back up of suitable size with automatic charging unit and auto change over unit on mains failure. Message indicator in the elevator car.

1.32		MANUAL EMERGENCY RESCUE DEVICE

1.32.1	Manual emergency rescue device shall be provided to rescue the passengers trapped in the elevator car in the event of failure of battery operated automatic emergency rescue device. The elevator car stopped in between floors due to power failure shall be brought to the nearest landing by releasing the break by means of pulling the mechanical lever provided in the last landing. The standard constructional feature of OEM for this manual emergency rescue device is acceptable.

1.33	 	OPERATION

1.33.1	The elevator shall be operated in simplex mode (with/ without attendant) and generally the elevator shall be in automatic mode. However a two position key-operated switch marked to indicate “ATT” (Attended Operation) and “AUTO” (Automatic Mode) shall be provided. When the switch is in the position of “ATT” mode, the elevator shall be in attendant mode. It will connect the hall button pushes to the annunciate, provided in the car, to register the calls. In automatic mode, momentary pressure of the car button/ landing button will send/ bring the car to this landing and car will automatically stop.

1.34	LIST OF APPROVED MAKES

| ELEVATORS | OTIS / KONE / /SCHINDLER /MITSUBISHI/JOHNSON/THYSSENKRUPP |
| --- | --- |

LIST OF APPROVED MAKES FOR ELECTRICAL ITEMS IN LIFT

| S.No. | #### MATERIALS | #### PREFERED MAKE |
| --- | --- | --- |
| 1 | #### LT cables | Gloster / Havells / Polycab |
| 2 | #### Light fitting | Philips / Wipro / GE / Bajaj / Crompton |
| 3 | #### MCCB | L&T,HPL,Siemens |

**********