## Summary
TENDER FOR CLASS 10000 CLEAN ROOM AT AKKULAM FACTORY
SUMMARY
PART - 1 | HVAC SYSTEM
PART - 2 | MODULAR
PART - 3 | ELECTRICAL SYSTEM
PART - 4 | CIVIL WORKS
PART - 5 | MISCELLANEOUS WORK
TOTAL
BUY BACK OF DEHUMIDIFIEER ( - VALUE)

## AC
HLL LIFECARE LIMITED, AKKULAM PLANT,THIRUVANANTHAPURAM
SUPPLY, ERECTION, VALIDATION & COMMISSIONING OF NEW CLASS 10000 CLEAN ROOM
TENDER NO: HLL/AFT/CLEAN ROOM / 2016-17 dated 18/02/2017
BILL OF QUANTITY - ANNEXURE I
No | ITEM DESCRIPTION | Unit | QTY | Unit Rate (Rs.) |  | TOTAL (Rs.)
|  |  |  | SUPPLY | INSTL. | SUPPLY | INSTL.
PART -1 - HVAC SYSTEM
1 | DOUBLE SKIN AIR-HANDLING UNITS WITH VFD, HEAT PIPE & PLUG FANS
Supply, Installation, testing & commsssioning the AHU's as per specification including all accessories as specified and as required VFD driven AHU with plug fans and VFD starter panel with all necessary connections with pressure sensors (minimum 2 nos.) and cabling to be included. VFD’s with RFI Filter suitable for First Environment noise control upto 50 Mtr, Inbuilt DC link choke for Harmonic mitigation, and Alphanumeric Display, Input Voltage: 380-480V, 3 Ph, IP-20 and c1 harmonics filters for VFD , VFD shall be for HVAC Application type All AHU’s will be given only one power input cable. Any looping should be done by OEM in case of multiple motors in one AHU General Specification Pre-Plasticized Sheet/ powder coated, Extruded Aluminium panta post frame work Fan section, coil section, filter section, with necessary Insulations, drain pan, cooling coil of copper tubes and aluminium fins (min. 10fins per inch) and required number of rows deep. TEFC sq.cage induction motor of required rating including mounting and fixing arrangements Plug fan with VFD Drives, HEAT PIPES, anti vibration springs/isolator bearings etc, 10 mm thick synthetic media filter with frame. 90% efficiency down to 20 micron, Insulation of all section with fire retardant insulation material as per manufactures standard. Air vent on cooling coil with globe valve/screwed plugs. Insulation of Drain pan as per specifications. Double canvas connections of fire retardant quality for connecting AHU's to ducting/ plenum, Insulated drain piping with trap till the out let of the AHU, Thermostat, Thermowell at the inlet and outlet of cooling coils, gauge cocks at the inlet and outlet of coiling coils for pressure gauges (only provision), duct damper, including Control wiring to make M/V in close position while AHU is OFF with relays etc. Including R.C.C foundation along with PCC/RCC sub base with bolts and nuts and finishing the slabs or any opening etc good as same, Limit switch in door and inspection lamps to be fixed, Lockable off push button to be provided near AHU if machine is 3mtrs and above far from respective panel board to be included in the Ahu cost.
1. a | 14 TR, 6700 cfm, 13.4 sqft./ 8 Row/Static - 100mm | No | 2 |  |  |  | 0
(Double Skin Floor mounted Horizontal AHU with mixing box, 10 micron pre filters , Thermal break)
1.b | Water based wrap around type heat pipe around main cooling coil to maintain the required RH | No | 2 |  |  |  | 0
2 | CHILLED WATER PIPING (Pre insulated piping)
Supply, receive, store, handle, install, test and commissioning of the following chilled water with GI class (C) IS 3589 pipes, with high tech supports with insulation complete with all fittings such as bends, tees, elbows, reducers flanges, special fittings, suspension hangers, supports etc. as reqd. for installation as per site conditions and as per specifications. Under ground piping shall have bitumen coating. Piping insulation shall be expanded polyurethane foam with 36 kg/cu m minimum density, .90% minimum closed cell content, minimum compressive strength of 40 psi and thermal conductivity of 0.14 Btu-in/hr/ft2/OF. The insulation shall completely fill the annular space between the service pipe and jacket and shall be bonded to both, the service pipe & jacket. All the fittings & bends shall be finished with the same finish as specified for pre-insulated pipe, supplied by the same company. RCC opening as good as same all supports Pipes to be welded with V-cut grooves as per specifications. Wall opening as good as same.
| 65mm dia. | RM. | 30 |  |  |  | 0
| 40mm dia. | RM. | 20 |  |  |  | 0
3 | Drain water piping with Ball valves
Supply and fixing in positionn of condensate drain water & AHU room drain to the floor trap piping with 9mm thick nitrile rubber insulation and with necessary fittings like elbows, tees and reducers etc. Openings as good as same.
| 20 mm dia PVC | RM. | 20 |  |  |  | 0
4 | BUTTERFLY VALVES:
| Supply, installation, testing & commissioning of the following butter fly valves as per the specifications and as required. Butterfly valve shall cast iron body with black nitrile seat. All butterfly valves shall be provided with locking devices & PN 16 Rating. Valve above 300 mm dia shall be gear driven. | [5 empty] | 0
| 65mm dia. - shaft tapping | No. | 2 |  |  |  | 0
| 40 mm dia. | No. | 4 |  |  |  | 0
5 | Y STRAINER FOR AHU'S
Supply, installation, testing & commissioning of the following Y strainers as per the specifications and as required.
| 40 mm dia | No. | 2 |  |  |  | 0
6 | PRESSURE GAUGE
Supply, installation, testing and commissioning of Indicating-dial type pressure gauges of Dry type made of Stainless steel or cast aluminum case, 114-mm dia, Pressure-Element Assembly: Bourdon tube, Pressure Connection : Brass, NPS 12mm dia bottom-outlet type, Dial: Satin-faced, non-reflective aluminum with permanently etched scale markings, Pointer: Red or other dark-color metal, Window: Glass, Accuracy: Grade A, plus or minus 1 percent of middle half, Stainless Steel U-Siphon and 15mm Brass body ball valve as per specification
| AHU Dial typepressure gauges. | No. | 4
7 | THERMOMETERS Supply, installation, testing and commissioning of Dial type thermometers with Stem with Copper-plated steel, aluminum, or brass for thermowell installation and of length to suit installation, Stainless Steel U-Siphon and 15mm Brass body ball valve as per specification for AHU
| Dial type thermo meter. | No. | 5 |  |  |  | 0
8 | AUTO AIR VENTS including Ball Valves | [5 empty] | 0
| Supply & install of airvents / purge valves at the highest points in chilled water piping complete each floor with pipes nipple welded to pipe, hex nipple, socket, U-pipe connection at outlet of air vent etc. as required. | No. | 2
9 | THREE WAY MIXING VALVES
Supply and installing of the following three way mixing valves with modulating proportional thermostat with necessary control pipe line for control of chilled water flow through the AHU with necessary isolator valves as given in the drawings
| 40 mm dia. | No. | 2 |  |  |  | 0
10 | SHEET METAL WORK
Supply, fabricate, handle and erect factory fabricated GSS/AL ducting as per drawing, complete with all fittings such as tee bends, special off-chutes, turning vanes, splitter dampers, ins.doors, transformation pieces slip on flanges etc. as reqd. as per IS 655 including suspension and supporting arrangement for plenums, ducts, complete as reqd. and as per specs.(only hitech supports shall be used) wall opening as good as same
ALUMINIUM DUCTING FOR CLEAN ROOM
| 1. 1.00 mm AL. Ducting in sq.m. | Sq.m | 490 |  |  |  | 0
| 2. 1.25 mm AL. Ducting in sq.m. | Sq.m | 50 |  |  |  | 0
11 | PLENUM BOX WITH HEATER BANK & FINE FILTER
| Supply installing, testing and commissioning of Plenum Box of size 2Mt. (L) x 1.5Mt (W) X 0.55Mt.(H) with 2 x 4.5 KW Heater ( to be switched on parallelly) comprising thermostat, humidistat, safety thermostat, contactors , 13500 cfm Fine filter filters of efficiency 99.9% down to 5 microns | Lot | 1 |  |  |  | 0
12 | Supply installing, testing and commissioning of (Factory Fabricated) HEPA filters of efficiency 99.9% down to 0.3 microns in filter plenum of 18 Gauge with rubber Gaskets In SS suitable frame work with 70% perforated ss grille, with gear operated Volume Control damper, DOP port, pressure sensing port etc. The HEPA filters will be fixed to the plenum using M6 SS rode ,304 Q type SS bolts and nuts). SS perforated sheets Mat finish . Hole size 23mm x 7mm oblong shape with 70% perforation.
| 650 cfm Hepafilter (610 x 610 x 300) | Nos | 22
13 | Supply installing, testing and commissioning of perforated aluminium grille for return with VCD and 10 Micron Filter in Clean room | Sq.m | 10.3779
14 | Insulated Plenum Box (600x600x450) made of 22G G.I & Spigot & Butterfly Dampers with necessary threaded rods for supporting. | Nos | 24
15 | Factory made fresh air dampers with louvers and control lever. | Nos. | 1
16 | GRILLES & DIFFUSERS FOR FRESH AIR FAN
Supply and fix the following grilles and diffusers as per specifications. Machine made, powder coated, supply and return air grilles and diffusers (material : Al)
| Supply air grille with vcd | Sq.m | 0.5
| Return air grille w/o vcd | Sq.m | 0.5
17 | FIRE DAMPERS.
| Supply,fixing,testing and commissioning of Motorised Fire dampers complete with actuator and control panel with required lengths of control wiring as per site requirements. Damper shall be with 16G GI Sheet construction ,16G GI casing and 16G GI blades 150 mm wide complete with chrome plated spindles ,self lubricating bushes, With 18G 400 mm Extended sleeve, 1 1/2 Hrs fire rating as per UL-555 certified by CBRI. The damper shall be motorised so as to close the damper and trip the AHU in the event of fire automatically and open the same in case of power being restored.The damper shall also be closed in the event of fire signal and should be compatible for BMS as per specification. Also DC/AC power should provided for dampers and all necessary equipments for the same considered. | sq.m | 1
18 | Motorized Damper Actuators with control panel & temperature sensors -7 Nm torque | Nos | 2
19 | DUCT INSULATION & LINING
Thermal Insulation
| supply & fixing of 19 mm thick class O nitrile rubber insulation with antimicrobial property adhesive as per the recommendation of the manufacture with density 45-55kg/m3 | Sq.m | 520
20 | MAGNAHELIC Differential pressure gauge. Supply, Installation, testing & commissioning of Magnehelic gauge with suitable 24 gauge smoothened to 240 grit SS304 face plates & 16 gauge GI Box & PU Tube/ silicon tubing (Range: 30 - 0 - 30 Pa ) suitable to install in modular panel with nozzle & complete accessories for CHANGE rooms. | No | 1
21 | Validation applicable for Class 10000 clean room including Air balancing and velocity profile test, Pressure balancing test, Particle Count Test | Lot | 1
TOTAL AMOUNT _ PART 2
PART -2 MODULAR
1 | Wall Panels
| 50 MM thick modular ceiling with PCGI 0.5 mm thick inside/outside with sand witched puf as infil, 38±2 kg density with peripheral al profile | Sqm | 30
2 | Ceiling Panels
| Supply and Installation of sandwiched walkable false ceiling of minimum 100 mm Thickness. Both side Epoxy Powder coated (60-80 microns) 0.8mm thick G.I sheets(hot dipped with zinc coating of 120 gsm)with PUF as infill of density not less than 40+/-2 Kg/m3 .The load bearing capacity to be not less than 150kg/m2. The clean room panel should meet the Euro classes minimum reaction to fire B-s3,d0. Necessary stiffeners to be provided as per manufacturer's standard and complete in all respects including, supports, hangers( T bar suspension type frame work), sealants, etc.. Ceilings shall include cutouts for HEPA filter box housings, Diffusers, Light fittings, Pendants & Utilities as indicated in the drawings (In case the vendors specification are different - vendor to provide details). Note: 1.All ceiling joints and gaps between panel to panel, celing elements (such as HEPA module, diffusers, pipe & electrical drops etc.) etc. to be sealed using FDA approved food grade silicon sealant. 2.Colour of the ceiling panel: Bright White (RAL 9010) - Semi-mat or as decided by client 3.Joint width between panels shall not exceed 3mm.Note: 1.All ceiling joints and gaps between panel to panel, celing elements (such as HEPA module, diffusers, pipe & electrical drops etc.) etc. to be sealed using FDA approved food grade silicon sealant. 2.Colour of the ceiling panel: Bright White (RAL 9010) - Semi-mat or as decided by client 3.Joint width between panels shall not exceed 3mm. | sq.mt | 160
3 | LUMINARIES
| Supply, installation of Clean room light fittings comprising of 36 Watts led light/ panel of size 300x300 mm, including all materials required for erection, mounting, & all wiring, terminations and interconnections, earthing from the terminal block /ceiling to the light fitting/luminaire. All minor civil works such as chasing etc. shall be under the scope of the Contractor | Nos | 22
| 3 Nos. 36 W light points group controlled by 1 No 6A, SP Switch. | Nos | 3
| 4 Nos. 36 W light points group controlled by 1 No 6A, SP Switch. | Nos | 3
4 | Clean Room Doors
Clean room doors comprising of door frame 1.2 mm thick in GI powder coated finish, double wall 0.8 mm thick leaf/shutter with honeycomb infill, double glazed view glass of 300 mm x 600 mm SS hinges, SS handle, SS push plate, autimatic door closure with speed adjuster and door lock
| Double door-1.35 M x 2.1 M Ht | Nos. | 2
| Single doors-1.0 M x 2.1 M Ht | Nos. | 1
| Door Bottom Seals | Nos. | 3
5 | Single Glass Emergency Exit for JGM Production
| Emergency Exit panel with 1.2 mm stainless steel frame having 4 partitions and 5mm thick single float toughened safety glass. | Sq.mt | 9
6 | Double glass - window
| Free standing double skin window panel with 800mm wide 925mm high 5mm thick double float toughned safety glass Flush at both sides fixed on brick wall | Sq.mt | 3
7 | Coving for ceiling
| Standard gypsum covings of R50 between roof ceiling & wall panels | Mts. | 15
8 | Coving for sharp corners
| Supply and installation of aluminium powder coated or anodized polished - corner coving | Mts. | 60
TOTAL AMOUNT _ PART 3
PART -3 - ELECTRICAL, COMMUNICATION& SECURITY SYSTEM
1 | ELECTRICAL PANEL
| Supply, installation testing and commissioning of extensible type, cubical panel comprising of switch fuse units, busbar, cable alley, fabricated from 2 mm thick CRCA sheets duly rust inhibited and stove enamel painted complete with heavy duty rubber gaskets, hinged compartment doors, removable gland plate for cable entry, sheet steel or 5mm thick compartment segregation, name plate, interconnection busbar, mounting channels etc. including fully automatic star/delta/DOL/VFD starters, Control wiring, interlocks, push buttons, indication, lamps etc. for the outgoing shall be included in this panel. All mandatory and statute sanction orders and approvals from the electrical inspectorate and KSEB shall be obtained by the contractor before energizing the system . the first inspection fee shall be paid by the owner. a) INCOMING - 1 No. MCCB b) BUSBARS - 3 phase and neutral Aluminium bus bars with bus supports in suitable bus chamber. c) METERING ammeter with CT's and selector switch. 0-500 volts voltmeter with selector switch and fuses. 0-250 Amp ammeter with CT's and selector switch. d) 1 set R.Y.B lmps with fuses. e) OUTGOING - TPN MCCB/ MPCB for 1 No. earth bus(CU) throughout the panel with earthing bolts AHU Panel -1 with above specifications,Total HP- 22 HP working | Nos | 1
2 | 6 WAY Lighting DB
| 6 Way single phase db for lighting with all specifications & as per drawings | Nos | 1
3 | 6 WAY UPS DB
| 6 Way single phase db for emergency lighting , Computer with all specifications & as per drawings | Nos | 1
4 | 12 way Main Power DB
| 12 Way Three phase db for clean room area, booster chiller with all specifications & as per drawings | Nos | 1
5 | 8 way Main Power DB
| 8 Way Three phase db for chiller, fume hood, hvac panel with all specifications & as per drawings | Nos | 1
6 | PLUG & SOCKET OUTLETS
Factory assembled IP 55 Interlocked switched sockets complete with compatible plug top & concealed mounting type metel box.
a | 240V, 16A,1Ph 2P & earth Industrial plug & socket | Nos | 13
(8 Nos Inside cleanroon, 2 Nos for Booster Chiller, 1 Nos for Main chiller, 2 Nos for Computer)
b | 240V, 32A, 1Ph, 2P & earth Industrial plug & socket. | Nos | 5
(1 No for fume hood, 2 Nos for chillers, 1 No godown motor, 1 No Crane)
7 | ISOLATORS for AHU
| 3 Phase | Nos. | 4
8 | Control box & DIGITAL DISPLAY PANEL inside the room with indication lamp , ON/OFF of AHU, thermostat control of clean room, cooling & heating mode, humidity control etc. Digital display of RH/TEMPERATURE, pressure , control wiring from AHU to unit etc. as per dwg / picture attached | Nos. | 1
9 | CABLES
Supply of 1.1 Kv PVC insulated PVC sheathed steel armoured cables of approved make and laying and fixing of PVC insulated PVC sheathed cable of 1.1Kv grade on surface/cable tray as required and making end termination with brass compression gland for PVC sheathed cable of 1.1Kv grade and fabricating and installing MS cable trays including horizontal and vertical bends, reducers, tees, cross members and other accessories as required and duly suspended from ceiling with MS suspenders including painting etc. ( IN R.M.)
a | 3.5 core 25 sq.mm Al. cables | Rm. | 10
b | 4 core 6 sq.mm Al. cables | Rm. | 50
c | 4 core 4 sq.mm Al. cables | Rm. | 150
d | 3 core x 2.5 sq mmcopper cable | Rm. | 100
10 | supply, installation & Terminations of new cable From UPS panel to Tube Extruder of Capacity: 125 Amps.
| 4 C x 50 Sq.mm Cu Cable | Rm. | 60
11 | supply, installation & Terminations of new cable From UPS panel to Sheet Extruder of Capacity: 63 Amps. | Rm. | 60
4 C x 25 Sq.mm Cu Cable
12 | EARTHING
Supply and laying earthing for various equipments and motors.
| 10 SWG copper wire | Rm. | 200
13 | Removing & relocation of MCB Panel for Crane & dye Temperature Monitoring panel for sheet extruder with incoming & outgoing cable and terminations | Lot | 1
14 | Telephones
a | Telephones - store 1 No, Clean room 2 Nos | Nos | 3
Telephone wiring to be laid from the existing telephone point with three port splitter either concealed/surface conduit system as per site requirement .Rate shall only include laying of telephone wire.
b | 0.5 Sq.mm PVC insulated 2pair telephone wire | Mts | 60
c | RJ 11 Telephone outlet with Metal Box, Plate etc. | Nos | 3
15 | CCTV System
| Supply, Installation testing and commissioning of Analog CCTV and cabling upto the DVR in ground floor comprising of 2 Nos. CCD Colour Dome Camera With switches and cabling (appr. 60 mts, actual qty to be measured at site) and power supply. All accessories for installation to be included. The Cameras shall be connected and synchronized to the existing DVR already installed in the ground floor of the building. | Lot | 1
16 | Fire Detection System
| Analogue Addressable Fire multi-criteria Detectors (5 Nos.) complete with cabling upto fire panel kept in ground floor near substation. Also 1 manual call point, 1 sounders/ hooter and necessary cabling shall be included. The detectors & MCPs shall be connected and synchronized to the existing control panel already installed at the building. | Lot | 1
17 | Fire Extinguisher
| Supply, Installation of clean agent type fire extinguisher, should be BIS specification, handy type, user friendly, EPDM rubber hose type, controllable discharge mechanism. Capacity 4 KG. | Nos | 2
18 | PA system
| Supply, Installation testing and commissioning of 110 v two speakers & Amplifier with cabling | Lot | 1
TOTAL AMOUNT _ PART 4
PART - 4 CIVIL & UTILITIES
1 | EPOXY FLOORING
| 3mm thick epoxy self leveling flooring systems with BASF Construction Chemicals make Mastertop 1230 Plus or equivalent as approved, over after rubbing & cleaning the surface free from all loose particles, laitance, patching of small patches, nicks etc., with Epoxy putty, applying primer, Mastertop 1200 PLUS and spreading 4 component self leveling epoxy compound, tooling and finishing to gloss/matt finish.Note : Before epoxy flooring, floor has to be made clean and smooth. If PCC chipped off in some places it has to be plastered and level to be maintained. | Sqm | 160
2 | EPOXY WALL PAINITNG
| 0.5mm thick epoxy self leveling with BASF Construction Chemicals make Mastertop 1230 Plus or equivalent as approved, over after removing the existing emulsion paint & cleaning the surface free from all loose particles, laitance, patching of small patches, nicks etc., with Epoxy putty, applying primer, Mastertop 1200 PLUS and spreading 4 component self leveling epoxy compound, tooling and finishing to gloss finish. | Sqm | 180
3 | Providing and constructing 10cm thick Brick work in Cement Mortar 1:6 using best quality wire cut bricks including soaking the bricks in water,racking joints, watering ,curing, etc all complete with. | Sqm | 5
4 | 12mm thick Plastering of brick walls with Cement Mortar 1:4. One coat floated hard and toweled smooth including chicken mesh plastering on all joints of masonry to rcc and all chasing made in the walls for electrical and plumbing lines etc all complete with and 2 coats of painting | Sqm | 10
5 | PIPING & VALVES
Supply, installation, testing & commissioning of the following Piping & Valves as per the specifications and as required. TO have SS 304 pipes as all extension pipes upto nearest point of requirment. Couplings and other necessary items and MS supports for running pipes though the ceiling to be considered.
a | Cooling Water Line (Supply & Return)
| 1" SS T-tapping from existing header from terrace to clean room | Rm | 120
| connection to tube & sheet extruders by client.1 " Valve | No | 6
b | DM Water Line
1" SS T-tapping from existing header from terrace to clean room
| connection to tube & sheet extruders by client. | Rm | 60
| 1 " Valve | No | 1
c | Air Compressor Line
| 1" SS T-tapping from existing header pipe from shaft | Rm | 25
connection to tube & sheet extruders by client.
| 1 " Valve | No | 1
| 1 1/2" SS T-tapping from existing header pipe from shaft | Rm | 10
connection to tube & sheet extruders by client.
| 1 1/2 " Valve | No | 1
TOTAL AMOUNT _ PART 5
PART - 5 MISCELLANEOUS WORKS
1 | Dismantling and re-locating of the Existing AHU to mezzanine area as shown in the dwg as per the instructions of client & Consultant to be done with upmost precautions, and making good of surfaces . Necessary dismantling of the ahu ducting and relocating to proposed area has to be carried out simultaneously along with shut down. And hooking up of the supply/return air ducting | Lot | 1
2 | Dismantling of existing dehumidifier unit from the first floor and lifting shifting and storing of the same unit at the specified location approved by the client. All labour and other extra charges to be considerd | Lot | 1
3 | Installation of the client supplied pass box of dimension 1Mt. (W) x 1.4 (H) x 1 (D) on to the floor below and to the partition above with sufficient supports to make it air tight and stedy | Nos. | 2
4 | Installation of the client supplied SS Single Door of dimension (2.04 H x 0.66 W x 0.04 T in mm) to the store room | Nos. | 1
5 | Buyback of Dehumidifier ( - Value) MAKE : BRY AIR (ASIA) PVT LTD MODEL : FVB CFM: 6200 | Lot | 1
TOTAL AMOUNT _ PART 5
Total Amount (Basic) (Part1 +Part 2+Part 3+ Part 4+Part 5)
Excise Duty(% to be furnished)
Taxes (CST/VAT) (% to be furnished)
Freight
ServiceTax
WCT
OTHERS,IF ANY (please specify)
Grand Total (In Figures)
Grand Total (In Words)