## Abstract
CONSTRUCTION OF MACHINE MANUFACTURING UNIT OF CED AT AKKULAM, THIRUVANANTHAPURAM
ABSTRACT
Sl. No | Description | Total (Rs.)
1 | Civil works
2 | Plumbing works
3 | Electrical works
Total
Service tax component to be paid by the bidder
Service tax component to be directly paid by the HLL in case the bidder is a Proprietary/ partnership firm
GRAND TOTAL
[INCLUDING 100% SERVICE TAX (a +b)]

## CIVIL Abstract-2
CIVIL WORKS
Item No | DSR code | Details of items | Quantity | Unit | Rate in figures (Rs.) | Rate in words (Rs.) | Amount (Rs.)
1 | 20.2A.1 &2 | Boring, providing and installation bored cast-in-situ reinforced cement concrete piles of garde M-25 of specified diameter and length below pile cap, to carry a safe working load not less than specified, excluding the cost of steel reinforcement but including the cost of boring with bentonite solution and temporary casing of appropriate length for setting out and removal of same and the length of the pile to be embedded in the pile cap etc. by Crawler mounted, telescopic boom hydraulic pilling Rig all complete, including removal of excavated earth with all its lifts and leads (length of pile for payment shall be measured up to bottom of pile cap). Note: Truck Mounted rotary/TMR/Tube well boring machine shall not be used.700mm dia. Piles | 240 | m |  |  | 0
2 | 20.6.2 | Vertical load testing of piles in accordance with IS 2911 (Part IV) including installation of loading platform by Kentledge method and preparation of pile head or construction of test cap and dismantling of test cap after test etc. complete as per specification & the direction of Engineer in-charge. Note: 1. Initial and Routine Load Test shall not be carried out by Dynamic method of testing. Note: 2. Testing agency shall submitt the design of loading platform for the approval of Engineer-in-charge.: Single pile above 50 tonne and upto 100 tonne Safe capacity |  |  |  |  | 0
a | 20.6.2.1 | Initial test (Test Load 2.5 times the Safe capacity) | 1 | Each |  |  | 0
b | 20.6.2.2 | Routine test (Test Load 1.5 times the Safe capacity) | 1 | Each |  |  | 0
3(a) | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30cm in depth. 1.5m in width as well as 10 sqm on plan) including disposal of excavated earth, lead upto 50m and lift upto 1.5m, disposed earth to be levelled and neatly dressed. All kinds of soil | 950 | m3 |  |  | 0
3(b) | 2.6.1 + 2.26.1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30cm in depth. 1.5m in width as well as 10 sqm on plan) including disposal of excavated earth, lead upto 50m and lift 1.50m to 3.0m, disposed earth to be levelled and neatly dressed. All kinds of soil All classes of soil | 12 | m3 |  |  | 0
4 | 2.8.1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan) including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All kinds of soil. | 89 | m3 |  |  | 0
5 | 2.25 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m | 591 | m3 |  |  | 0
6 | 1.1.2.8 | Conveying and disposing off excavated excess earth from the site | 454 | m3 |  |  | 0
7 | 2.34.1 | Supplying chemical emulsion in sealed containers including delivery as specified Chlorpyriphos/ Lindane emulsifiable concentrate of 20% | 521 | Litres |  |  | 0
8 | 2.35.3.1 | Treatment of soil under existing floors using chemical emulsion @ one litre per hole, 300 mm apart including drilling 12 mm diameter holes and plugging with cement mortar 1 :2 (1 cement : 2 Coarse sand) to match the existing floor : With Chlorpyriphos/Lindane E.C. 20% with 1% concentration | 938 | m2 |  |  | 0
9 | 4.1.5 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:3:6 (1 Cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size). | 140 | m3 |  |  | 0
10 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:4:8 (1 Cement : 4 coarse sand : 8 graded stone aggregate 40 mm nominal size). | 19 | m3 |  |  | 0
11 | 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) | 7 | m3 |  |  | 0
12 | 5.37 | Providing and laying in position ready mixed M-25 grade concrete for reinforced cement concrete work, using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , excluding the cost of centering, shuttering finishing and reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, improve workability without impairing strength and durability as per direction of the Engineer - in - charge. (Note :- Cement content considered in this item is @ 330 kg/cum. Excess/less cement used as per design mix is payable/ recoverable separately). |  |  |  |  | 0
a | 5.37.1 | All works upto plinth level. | 303 | m3 |  |  | 0
b | 5.37.2 | All works above plinth level upto floor V level. | 290 | m3 |  |  | 0
13 | 5.35 | Add for using extra cement in the items of design mix over and above the specified cement content therein | 296.5 | ql |  |  | 0
14 | 5.9 | Centering and shuttering including strutting, propping etc. and removal of form for : |  |  |  |  | 0
a | 5.9.1 | Foundations, footings, bases of columns, etc. for mass concrete. | 340 | m2 |  |  | 0
b | 5.9.2 | Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc. | 370 | m2 |  |  | 0
c | 5.9.3 | Suspended floors, roofs, landings, balconies and access platform. | 1235 | m2 |  |  | 0
d | 5.9.5 | Lintels, beams, plinth beams, girders, bressumers and cantilevers. | 795 | m2 |  |  | 0
e | 5.9.6 | Columns, Pillars, Piers, Abutments, Posts and Struts. | 285 | m2 |  |  | 0
f | 5.9.7 | Stairs, (excluding landings) except spiral-staircases. | 62 | m2 |  |  | 0
g | 5.9.16.1 | Edges of slabs and breaks in floors and walls.Under 20 cm wide | 518 | m |  |  | 0
h | 5.9.19 | Weather shade, Chajjas, corbels etc., including edges. | 75 | m2 |  |  | 0
15 | 5.11.1 | Extra for additional height in centering, shuttering where ever required with adequate bracing, propping etc. including cost of de-shuttering and decentering at all levels, over a height of 3.5 m, for every additional height of 1 metre or part thereof (Plan area to be measured) Suspended floors, roofs, landing, beams and balconies (Plan area to be measured). | 730 | m2 |  |  | 0
16 | 5.22.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete Thermo-Mechanically Treated bars. | 85390 | kg |  |  | 0
17 | 7.1.1 | Random rubble masonry with hard stone in foundation and plinth including levelling up with cement concrete 1:6:12 (1 cement : 6 coarse sand : 12 graded stone aggregate 20mm nominal size) upto plinth level with :Cement mortar 1:6 (1 cement : 6 coarse sand). | 135 | m3 |  |  | 0
18 | 6.4.2 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in : Cement mortar 1:6 (1 cement : 6 coarse sand) | 240 | m3 |  |  | 0
19 | 6.12.2 | Half brick masonry with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundations and plinth in.cement mortar 1:4 (1 cement : 4 coarse sand) | 142 | m2 |  |  | 0
20 | 6.15 | Extra for providing and placing in position 2 Nos. 6mm dia. M.S. bars at every third course of half brick masonry. | 142 | m2 |  |  | 0
21 | 4.7.2 | Providing and fixing up to floor five level precast cement concrete solid block including hoisting and setting in position with cement mortar 1:3 (1 cement : 3 coarse sand), cost of required centering, shuttering complete :1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20mm nominal size). | 83 | m3 |  |  | 0
22 | 8.2.2.2 | Providing and fixing 18mm thick gang saw cut mirror polished premoulded and prepolished) machine cut for kitchen platforms, flooring, vanity counters, window sills , facias and similar locations of required size of approved shade, colour and texture laid over 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels. Granite of any colour and shade: Area of slab over 0.50 sqm.(Lowest retails price not less than Rs. 2000/m2) | 100 | m2 |  |  | 0
23 | 8.5 | Extra for providing opening of required size & shape for wash basins/ kitchen sink in kitchen platform, vanity counters and similar location in marble/Granite/stone work including necessary holes for pillar taps etc. including moulding, rubbing and polishing of cut edges etc. complete. | 4 | Each |  |  | 0
24 | 9.48.2 | Providing and fixing M.S. grills of required pattern in frames of windows etc. with M.S. flats, square or round bars etc. including priming coat with approved steel primer all complete.Fixed to openings /wooden frames with rawl plugs screws etc. | 762 | kg |  |  | 0
25 | 9.84 | Providing and fixing aluminium extruded section body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 36 kg to 80 kg and door width from 701 mm to 1000 mm) with double speed adjustment with necessary accessories and screws etc. complete. | 22 | Each |  |  | 0
26 | 9.117.1 | Providing and fixing factory made UPVC door frame made of UPVC extruded sections having an overall dimension as below (tolerance ±1mm), with wall thickness 2.0 mm (± 0.2mm), corners of the door frame to be Jointed with galvanized brackets and stainless steel screws, joints mitred and Plastic welded. The hinge side vertical of the frames reinforced by galvanized M.S. tube of size 19 X 19mm and 1mm (± 0.1 mm) wall thickness and 3 nos. stainless steel hinges fixed to the frame complete as per manufacturers specification and direction of Engineer-in-charge: Extruded section profile size 48x40 mm. | 40 | m |  |  | 0
27 | 9.118.2 | 30 mm thick factory made Polyvinyl Chloride (PVC) door shutter made of styles and rails of a UPVC hollow section of size 60x30 mm and wall thickness 2 mm (± 0.2 mm), with inbuilt decorative moulding edging on one side. The styles and rails mitred and joint at the corners by means of M.S. galvanised/plastic brackets of size 75x220 mm having wall thickness 1.0 mm and stainless steel screws. The styles of the shutter reinforced by inserting galvanised M.S. tube of size 25x20 mm and 1 mm (± 0.1 mm) wall thickness. |  |  |  |  | 0
|  | The lock rail made up of 'H' section, a UPVC hollow section of size 100x30 mm and 2 mm (± 0.2 mm) wall thickness fixed to the shutter styles by means of plastic/ galvanised M.S. 'U' cleats. The shutter frame filled with a UPVC multi-chambered single panel of size not less than 620 mm, having over all thickness of 20 mm and 1 mm (± 0.1 mm) wall thickness . The panels filled vertically and tie bar at two places by inserting horizontally 6 mm galvanised M.S. rod and fastened with nuts and washers, complete as per manufacturer's specification and direction of Engineer-in-charge. | 10.5 | m2 |  |  | 0
28 | 10.17 | Providing and fixing M.S. fan clamp type I or II of 16 mm dia M.S. bar bent to shape with hooked ends in R.C.C. slabs, beams during laying including painting the exposed portion of loop, all as per standard design complete. | 45 | Each |  |  | 0
29 | 10.28 | Providing and fixing stainless steel ( Grade 304) railing made of Hollow tubes, channels, plates etc. including welding, grinding, buffing, polishing and making curvature (wherever required) and fitting the same with necessary stainless steel nuts and bolts complete i/c fixing the railing with necessary accessories & stainless steel dash fasteners , stainless steel bolts etc., of required size, on the top of the floor or the side of waist slab with suitable arrangement as per approval of Engineer-in-charge. ( for payment purpose only weight of stainless steel members shall be considered excluding fixing accessories such as nuts, bolts, fasteners etc.) | 350 | kg |  |  | 0
30 | 11.36 | Providing and fixing Ist quality ceramic glazed wall tiles 300x450mm size conforming to IS : 15622 (thickness to be specified by the manufacturer ) of approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados over 12 mm thick bed of cement Mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm including pointing in white cement mixed with pigment of matching shade complete.(Lowest retail price not less than Rs. 400/m2) Make: NITKO, KAJARIA, ORIENT. | 215 | m2 |  |  | 0
31 | 11.4 | Providing and laying rectified antiskid Ceramic floor tiles 300x300 mm or more (thickness to be specified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make in all colours, shades, except White, Ivory, Grey, Fume Red Brown, laid on 20 mm thick Cement Mortar 1:4 (1 Cement : 4 Coarse sand) including pointing the joints with white cement and matching pigments etc., complete (Lowest retail price not less than Rs. 500/m2) Make: NITKO, KAJARIA, ORIENT. | 54 | m2 |  |  | 0
32 | 11.41.2 | Providing and laying vitrified floor tiles in different sizes (thickness to be specified by the manufacturer) with water absorption's less than 0.08% and conforming to IS : 15622 of approved make in all colours and shades, laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand) including grouting the joints with white cement and matching pigments etc., complete.Size of Tile 600x600 mm: (Lowest retail price not less than Rs. 900/m2) Make: NITKO, KAJARIA, ORIENT. | 580 | m2 |  |  | 0
33 | 11.46.2 | Providing and laying Vitrified tiles in different sizes (thickness to be specified by manufacturer) with water absorption less than 0.08 % and conforming to I.S. 15622, of approved make in all colours & shade in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.Size of Tile 600x600 mm: (Lowest retail price not less than Rs. 900/m2) Make: NITKO, KAJARIA, ORIENT. | 58 | m2 |  |  | 0
34 | 16.75 | Providing and laying C.C. pavement of mix M-25 with ready mixed concrete from batching plant. The ready mixed concrete shall be laid and finished with screed board vibrator , vacuum dewatering process and finally finished by floating, brooming with wire brush etc. complete as per specifications and directions of Engineer-incharge. (The panel shuttering work shall be paid for separately). | 50 | M3 |  |  | 0
35 | LMR | Groove cutting over VDF Flooring 5x25mm deep, clean the groove with air blower | 440 | RM |  |  | 0
36 | 10.6.1 | Supplying and fixing rolling shutters of approved make, made of required size M.S. laths, interlocked together through their entire length and jointed together at the end by end locks, mounted on specially designed pipe shaft with brackets, side guides and arrangements for inside and outside locking with push and pull operation complete, including the cost of providing and fixing necessary 27.5 cm long wire springs manufactured from high tensile steel wire of adequate strength conforming to IS: 4454 – part 1 and M.S. top cover of required thickness for rolling shutters.80x1.25mm M.S. laths with 1.25 mm thick top cover. | 24 | m2 |  |  | 0
37 | 10.7 | Providing and fixing ball bearing for rolling shutters. | 4 | Each |  |  | 0
38 | 10.8.1 | Extra for providing mechanical device chain and crank operation for operating rolling shutters. Exceeding 10.00 sqm and upto 16.80 sqm in the area | 15 | m2 |  |  | 0
39 | 13.2.1 | 15 mm cement plaster of mix 1:4 (1 cement: 4 fine sand) for outside walls upto 10.0m height | 1270 | m2 |  |  | 0
40 | 13.22 | Extra for plastering exterior walls of height 10m to 13m | 209.49 | m2 |  |  | 0
41 | 13.22 +13.22 | Extra for plastering exterior walls of height 13m to 16m | 115 | m2 |  |  | 0
42 | 13.5.1 | 15 mm cement plaster on rough side of single or half brick wall of mix : 1:4 (1 cement: 4 coarse sand) | 2400 | m2 |  |  | 0
43 | 13.16.1 | 6 mm cement plaster of mix : 1:3 (1 cement: 3 fine sand) for under side of roof slab | 808 | m2 |  |  | 0
44 | 13.9.1 + 13.21 | Cement plaster 1:3 (1 cement: 3 coarse sand) finished with a floating coat of neat cement.12 mm cement plaster including providing and mixing water proofing material in cement plaster work in proportion recommended by the manufacturers. to the top surface of slab & sunshade | 385 | m2 |  |  | 0
45 | 13.8 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. | 2695 | m2 |  |  | 0
46 | 13.43.1 | Applying one coat of water thinnable cement primer of approved brand and manufacture on wall surface : | 2695 | m2 |  |  | 0
47 | 13.47.1 | Finishing walls with Premium Acrylic Smooth exterior paint with Silicone additives of required shade New work (Two or more coats applied @ 1.43 ltr/ 10 sqm. over and including priming coat of exterior primer applied @ 2.20 kg/ 10 sqm). | 1270 | m2 |  |  | 0
48 | 13.60.1 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade: Two or more coats on new work. Inside of walls | 3208 | m2 |  |  | 0
49 | 13.61.1 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade :Two or more coats on new work. | 115 | m2 |  |  | 0
50 | 16.68 | Providing and laying 60mm thick factory made cement concrete interlocking paver block of M -30 grade made by block making machine with strong vibratory compaction, of approved size, design & shape, laid in required colour and pattern over and including 50mm thick compacted bed of fine sand, filling the joints with fine sand etc. all complete as per the direction of Engineer-in-charge. | 140 | m2 |  |  | 0
51 | 16.69 | Providing and laying at or near ground level factory made kerb stone of M-25 grade cement concrete in position to the required line, level and curvature, jointed with cement mortar 1:3 (1 cement: 3 coarse sand) including making joints with or without grooves (thickness of joints except at sharp curve shall not to more than 5mm), including making drainage opening wherever required complete etc. as per direction of Engineer-in-charge (length of finished kerb edging shall be measured for payment). (Precast C.C. kerb stone shall be approved by Engineer-in-charge). | 2 | m3 |  |  | 0
52 | 11.20.3 | Chequerred precast cement concrete tiles 22 mm thick in footpath & courtyard, jointed with neat cement slurry mixed with pigment to match the shade of tiles including rubbing and cleaning etc. complete, on 20 mm thick bed of cement mortar 1:4 (1 cement: 4 coarse sand). Dark shade using ordinary cement. | 30 | m2 |  |  | 0
53 | 21.1.1.2 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) : For fixed portion Powder coated aluminium (minimum thickness of powder coating 50 micron) | 1415 | kg |  |  | 0
54 | 21.1.2.2 | For shutters of doors, windows & ventilators including providing and fixing hinges/ pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately). Powder coated aluminium (minimum thickness of powder coating 50 micron) | 1045 | kg |  |  | 0
55 | 21.2.2 | Providing and fixing 12mm thick prelaminated particle board flat pressed three layer or graded wood particle board conforming to IS: 12823 Grade l Type ll, in panelling fixed in aluminum doors, windows shutters and partition frames with C.P. brass / stainless steel screws etc. complete as per architectural drawings and directions of engineer-in-charge. Pre-laminated particle board with decorative lamination on both sides. | 35 | m2 |  |  | 0
56 | 21.3 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . (Cost of aluminium snap beading shall be paid in basic item): |  |  |  |  | 0
(a) | 21.3.2 | With float glass panes of 5.50 mm thickness | 85 | m2 |  |  | 0
(b) | 21.3.3 | With float glass panes of 8 mm thickness | 13 | m2 |  |  | 0
57 | 21.4.2 | Providing and fixing double action hydraulic floor spring of approved brand and manufacture conforming to IS : 6315, having brand logo embossed on the body / plate with double spring mechanism and door weight upto 125 kg., for doors, including cost of cutting floors , embedding in floors as required and making good the same matching to the existing floor finishing and cover plates with brass pivot and single piece M.S. sheet outer box with slide plate etc. complete as per the direction of Engineer-in-charge. With brass cover plate minimum 1.25 mm thickness. | 2 | Each |  |  | 0
58 | 21.11 | Providing and fixing stainless steel (SS 304 grade) adjustable friction windows stays of approved quality with necessary stainless steel screws etc. to the side hung windows as per direction of Engineer-in-charge complete. |  |  |  |  | 0
a | 21.11.1 | 205 X 19 mm | 18 | Each |  |  | 0
b | 21.11.2 | 255 X 19 mm | 51 | Each |  |  | 0
59 | 21.12.2 | Providing and fixing aluminium tubular handle bar 32 mm outer dia, 3.0 mm thick & 2100 mm long with SS screws etc .complete as per direction of Engineer-in-Charge.Powder coated minimum thickness 50 micron aluminium tubular handle bar | 44 | Each |  |  | 0
60 | 21.13 | Providing and fixing 100mm brass locks (best make of approved quality) for aluminium doors including necessary cutting and making good etc. complete | 16 | Each |  |  | 0
61 | 21.15.2 | Providing and fixing aluminium casement windows fastener of required length for aluminium windows with necessary screws etc. complete. Powder coated minimum thickness 50 micron aluminium | 69 | Each |  |  | 0
62 | 21.18 | Providing and fixing 12 mm thick frameless toughened glass door shutter of approved brand and manufacture, including providing and fixing top & bottom pivot & spring type fixing arrangement and making necessary holes etc. for fixing required door fittings, all complete as per direction of Engineer-in-charge (Door handle, lock and stopper etc.to be paid separately). | 9 | m2 |  |  | 0
63 | LMR | Propviding and fixing 12mm thick toughened glass automatic sliding door (DORMA make) of size 200x240cm size (two side sliding ) including Aluminum Channel DC Brush less Motor Micro Computer 130 ~ 300 Volt wide AC Input SMPS Power Supply 2 nos Microwave Sensors All Accessories 2 nos GLASS holding clamps Electronic Lock Switch and all other accessories etc complete. The sensor consists of backup battery support for ensuring normal running of automatic sliding electro-mechanical lock for ensuring safe usage of automatic sliding door system, radar and sensors are highly sensitive which provides safety from accidental squeezing and striking, 32-bit control chip for ensuring higher processing speeds. . | 1 | Each |  |  | 0 | 0
64 | 21.18 | Providing and fixing 12 mm thick frameless toughened glass partition of approved brand and manufacture, including providing and fixing top & bottom etc.all complete as per direction of Engineer-in-charge | 48 | m2 |  |  | 0
65 | 22.5 | Providing and laying water proofing treatment in sunken portion of WCs, bathroom etc., by applying cement slurry mixed with water proofing cement compound consisting of applying : a) First layer of slurry of cement @ 0.488 kg/sqm mixed with water proofing cement compound @ 0.253 kg/sqm. This layer will be allowed to air cure for 4 hours. b) Second layer of slurry of cement @ 0.242 kg/sqm mixed with water proofing cement compound @ 0.126 kg/sqm. This layer will be allowed to air cure for 4 hours followed with water curing for 48 hours. The rate includes preparation of surface, treatment and sealing of all joints, corners, junctions of pipes and masonry with polymer mixed slurry | 29 | m2 |  |  | 0
66 | 12.52.2 | Providing and fixing tiled false ceiling of approved materials of size 595x595 mm in true horizontal level suspended on inter locking metal grid of hot dipped galvanized steel sections ( galvanized @ 120 gsm/sqm, both side inclusive) consisting of main "T" runner with suitably spaced joints to get required length and of size 24x38mm made from 0.30mm thick (minimum) sheet, spaced at 1200mm center to center and cross "T" of size 24x25mm made of 0.30mm thick (minimum) sheet, 1200mm long spaced between main "T" at 600mm center to center to form a grid of 1200x600 mm and secondary cross "T" of length 600mm and size 24x25mm made of 0.30 mm thick (minimum) sheet to be interlocked at middle of the 1200x600mm panel to form grids of 600x600mm |  |  |  |  | 0
|  | and wall angle of size 24x24x0.3 mm and laying false ceiling tiles of approved texture in the grid including, wherever, required, cutting/making, opening for services like diffusers, grills, light fittings, fixtures, smoke detectors etc. Main "T" runners to be suspended from ceiling using GI slotted cleats of size 27 x 37 x 25 x1.6 x mm fixed to ceiling with 12.5 mm dia and 50 mm long dash fasteners, 4mm GI adjustable rods with galvanised butterfly level clips of size 85 x 30 x 0.8 mm spaced at 1200mm center to center along main T, bottom exposed width of 24 mm of all T-sections shall be pre-painted with polyester paint, all complete at all heights as per specifications drawings and as directed by Engineer-in-charge. |  |  |  |  | 0
|  | GI Metal Ceiling Lay in perforated Tegular edge global white color tiles of size 595x595 mm and 0.5mm thick with 8mm drop; made of GI sheet having galvanizing of 100 gms/sqm (both sides inclusive) and 20% perforation area with 1.8mm dia holes and having NRC (Noise Reduction Coefficient ) of 0.5, electro statically polyester powder coated of thickness 60 microns (minimum), including factory painted after bending and perforation, and backed with a black Glass fiber acoustical fleece. | 300 | m2 |  |  | 0
67 | 12.45.1 | Providing and fixing false ceiling at all height including providing and fixing of frame work made of special sections, power pressed from M.S. sheets and galvanized with zinc coating of 120 gms/sqm (both side inclusive) as6mm dia bolts, other flange of cleat fixed to the angle hangers of 25x10x0.50 mm of required length with nuts & bolts of required size and other end of angle hanger fixed with intermediate G.I. channels 45x15x0.9 mm running at the spacing of 1200 mm centre to centre, to which the ceiling section 0.5 mm thick bottom wedge of 80 mm with tapered flanges of 26 mm each having lips of 10.5 mm, at 450 mm centre to centre, shall be fixed in a direction perpendicular to G.I. intermediate channel with connecting clips made out of 2.64 mm dia x 230 mm long G.I. wire at every junction, including fixing perimeter channels 0.5 mm thick 27 mm high having flanges of 20 mm and 30 mm long, the perimeter of ceiling fixed to wall/partition with the help of rawl plugs at 450 mm centre, with 25mm long dry wall screws @230 mm interval, including fixing of gypsum board to ceiling section |  |  |  |  | 0
|  | and perimeter channel with the help of dry wall screws of size 3.5 x 25 mm at 230 mm c/c, including jointing and finishing to a flush finish of tapered and square edges of the board with recomme-nded jointing compound , jointing tapes , finishing with jointing compound in 3 layers covering upto 150 mm on both sides of joint and two coats of primer suitable for board, all as per manufacturer’s specification and also including the cost of making openings for light fittings, grills, diffusers, cutouts made with frame of perimeter channels suitably fixed, all complete as per drawings, specification and direction of the Engineer in Charge but excluding the cost of painting with per IS : 277 and consisting of angle cleats of size 25 mm wide x 1.6 mm thick with flanges of 27 mm and 37mm, at 1200 mm centre to centre, one flange fixed to the ceiling with dash fastener 12.5 mm dia x 50mm long with |  |  |  |  | 0
|  | 12.5 mm thick tapered edge gypsum plain board conforming to IS: 2095- Part I | 250 | m2 |  |  | 0
68 | 26.1 | Providing and supplying aluminium extruded tubular and other aluminium sections as per the architectural drawings and approved shop drawings , the aluminium quality as per grade 6063 T5 or T6 as per BS 1474,including super durable powder coating of 60-80 microns conforming to AAMA 2604 of required colour and shade as approved by the Engineer-in-Charge. ( The item includes cost of material such as cleats, sleeves, screws etc. necessary for fabrication of extruded aluminium frame work. Nothing extra shall be paid on this account). | 650 | kg |  |  | 0
69 | 26.2 | Designing, fabricating, testing, protection, installing and fixing in position semi (grid) unitized system of structural glazing (with open joints) for linear as well as curvilinear portions of the building for all heights and all levels, including: |  |  |  |  | 0
|  | a) Structural analysis & design and preparation of shop drawings for the specified design loads conforming to IS 875 part III (the system must passed the proof test at 1.5 times design wind pressure without any failure), including functional design of the aluminum sections for fixing glazing panels of various thicknesses, aluminium cleats, sleeves and splice plates etc. gaskets, screws, toggles, nuts, bolts, clamps etc., structural and weather silicone sealants, flashings, fire stop (barrier)-cum-smoke seals, microwave cured EPDM gaskets for water tightness, pressure equalisation & drainage and protection against fire hazard including |  |  |  |  | 0
|  | b) Fabricating and supplying serrated M.S. hot dip galvanised/Aluminium alloy of 6005 T5 brackets of required sizes, sections and profiles etc. to accommodate 3 Dimentional movement for achieving perfect verticality and fixing structural glazing system rigidly to the RCC/ masonry/structural steel framework of building structure using stainless steel anchor fasteners/ bolts, nylon seperator to prevent bimetallic contacts with nuts and washers etc. of stainless steel grade 316, of the required capacity and in required numbers. |  |  |  |  | 0
|  | c) Providing and filling, two part pump filled, structural silicone sealant and one part weather silicone sealant compatible with the structural silicone sealant of required bite size in a clean and controlled factory / work shop environment , including double sided spacer tape, setting blocks and backer rod, all of approved grade, brand and manufacture, as per the approved sealant design, within and all around the perimeter for holding glass. |  |  |  |  | 0
|  | d) Providing and fixing in position flashings of solid aluminium sheet 1 mm thick and of sizes, shapes and profiles, as required as per the site conditions, to seal the gap between the building structure and all its interfaces with curtain glazing to make it watertight. |  |  |  |  | 0
|  | e) Making provision for drainage of moisture/ water that enters the curtain glazing system to make it watertight, by incorporating principles of pressure equalization, providing suitable gutter profiles at bottom (if required), making necessary holes of required sizes and of required numbers etc. complete. This item includes cost of all inputs of designing, labour for fabricating and installation of aluminium grid, installation of glazed units, T&P, scaffolding and other incidental charges including wastages etc., enabling temporary structures and services, cranes or cradles etc. as described above and as specified. |  |  |  |  | 0
|  | The item includes the cost of getting all the structural and functional design including shop drawings checked by a structural designer, dully approved by Engineer-in-charge. The item also includes the cost of all mock ups at site, cost of all samples of the individual components for testing in an approved laboratory, field tests on the assembled working structural glazing as specified, cleaning and protection till the handing over of the building for occupation. In the end, the Contractor shall provide a water tight structural glazing having all the performance characteristics etc. all complete as required, as per the Architectural drawings, as per item description, as specified as per the approved shop drawings and as directed by the Engineerin-, Charge. |  |  |  |  | 0
|  | Note:- 1. The cost of providing extruded aluminium frames, shadow boxes, extruded aluminium section capping for fixing in the grooves of the curtain glazing and vermin proof stainless steel wire mesh shall be paid for separately under relevant items under this subhead However, for the purpose of payment, only the actual area of structural glazing (including width of grooves ) on the external face shall be measured in sqm. up to two decimal places. |  |  |  |  | 0
|  | Note:-2. The following performance test are to be conducted on structural glazing system if area of structural glazing exceeds 2500 Sqm from the certified laboratories accreditated by NABL(National Accreditation Board for Testing and Calibration Laboratories), Department of Science & Technologies, India. Cost of testing is payable separately. The NIT approving authority will decide the necessity of testing on the basis of cost of the work, cost of the test and importance of the work. Performance Testing of Structural glazing system Tests to be conducted in the NBL Certified laboratories |  |  |  |  | 0
|  | 1. Performance Laboratory Test for Air Leakage Test (-50pa to – 300pa) & (+50pa to +300pa) as per ASTM E-283-04 testing method for a range of testing limit 1 to 200 mVhr” |  |  |  |  | 0
|  | 2. Static Water Penetration Test. (50pa to 1500pa) as per ASTME- 331-09 testing method for a range up to 2000 ml.” |  |  |  |  | 0
|  | 3. Dynamic Water Penetration (50pa to 1500pa) as per AAMA 501.01- 05 testing method for a range upto 2000 ml” |  |  |  |  | 0
|  | 4. Structural Performance Deflection and deformation by static air pressure test (1.5 times desing wind pressure without any failure) as per ASTME-330-10 testing method for a range upto 50 mm” |  |  |  |  | 0
|  | 5. Seismic Movement Test (upto 30 mm) as per AAMA 501.4-09 testing method for Qualitative test” Tests to be conducted on site |  |  |  |  | 0
|  | 6. Onsite Test for Water Leakage for a pressure range 50 kpa to 240 kpa (35psi) upto 2000ml” | 100 | m2 |  |  | 0
70 | 26.3 | Providing, assembling and supplying vision glass panels (IGUs) comprising of hermetically-sealed 6-12- 6 mm insulated glass (double glazed) vision panel units of size and shape as required and specified, comprising of an outer heat strengthened float glass 6mm thick, of approved colour and shade with reflective soft coating on surface # 2 of approved colour and shade, an inner Heat strengthned clear float glass 6mm thick, spacer tube 12mm wide, dessicants, including primary seal and secondary seal (structural silicone sealant) etc. all complete for the required performances, as per the Architecturaldrawings, as per the approved shop drawings, as specified and asdirected by the Engineer-in-Charge. |  |  |  |  | 0
|  | The IGUs shall be assembled inthe factory/ workshop of the glass processor. (Payment for fixing ofIGU Panels in the curtain glazing is included in cost of item No.26.2)For payment, only the actual area of glass on face # 1 of the glasspanels (excluding the areas of the grooves and weather siliconesealant) provided and fixed in position, shall be measured in sqm. |  |  |  |  | 0
|  | (i) Coloured tinted float glass 6mm thick substrate with reflective soft coating on face # 2, + 12mm Airgap + 6mm Heat Strengthened clear Glass of approved make having properties as visible Light transmittance (VLT) of 25 to 35 %, Light reflection internal 10 to 15%, light reflection external 10 to 20 %, shading coefficient (0.25- 0.28) and U value of 3.0 to 3.3 W/m2 degree K etc. The properties of performance glass shall be decided by technical sanctioning authority as per the site requirement. | 100 | m2 |  |  | 0
71 | 26.4 | Extra for openable side / top hung vision glass panels (IGUs) including providing and supplying at site all accessories and hardwares for the openable panels as specified and of the approved make such as heavy duty stainless steel friction hinges, min 4 -point cremone locking sets with stainless steel plates, handles, buffers etc. including necessary stainless steel screws/ fasteners, nuts, bolts, washers etc. all complete as per the Architectural drawings, as per the approved shop drawings, as specified and as directed by the Engineerin- Charge. | 10 | m2 |  |  | 0
|  | Total amount |  |  |  |  | 0

## PLUMBING WORKS-3
PLUMBING WORKS
Sl. No. | DSR Code No. | Description | Quantity | Unit | Rate in figures (Rs.) | Rate in words (Rs.) | Amount
1 | M.R | Providing and fixing white vitreous china Floor Mounted type water closet (European type W.C.pan) with seat and lid, 3/6 litre low level white vitrous Dual Flushing cistern and C.P flush bend with fitting and C.I brackets, 40mm flush bend, overflow arrangement with specials of standard make and mosquito proof coupling of approved municipal design complete including painting of fittings and brackets, cutting and making good the walls and floors wherever required. , WC pan with ISI marked white solid plastic seat and lid (Lowest retail price not less than 10,000/each. Materials to be selected by the Engineer in charge) | 9 | Each |  |  | 0
2 | LMR | Providing and fixing wash basin ( half pedestal single unit)) with CI / MS brackets, 15mm CP brass Pillar taps, 32mm CP brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever required.: White Vitreous China Wash basin size 630 x 450mm with a single 15mm C.P brass piller tap. Make:Hindware,Cera,Jaquar etc.., (Lowest retail price of basin not less than Rs. 4500/each and Pillar tap not less than Rs. 2000/each. Materials to be selected by the Engineer in charge) | 1 | Each |  |  | 0
3 | LMR | Providing and fixing white vitreous china flat back or wall corner type lipped front urinal basin of 430x260x350mm and 340x410x265mm sizes respectively with automatic flushing cistern with standard flush pipe and C.P. brass spreaders with brass unions and G.I clamps complete, including painting of fittings and brackets, cutting and making good the walls and floors wherever required : One urinal basin with 5 litre white P.V.C. automatic flushing cistern. (Lowest retail price of urinals not less than Rs. 4200/each and automatic flushing cistern not less than Rs. 1200/each. Materials to be selected by the Engineer in charge) | 4 | Each |  |  | 0
4 |  | Providing and fixing stone slab with table rubbed, edges rounded and polished, of size 75x50 cm deep and 1.8 cm thick, fixed in urinal partitions by cutting a chase of appropriate width with chase cutter and embedding the stone in the chase with epoxy grout or with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 6 mm nominal size) as per direction of Engineer-in-charge and finished smooth. | 4 | Each |  |  | 0
5 | LMR | Providing and fixing wash basin (counter type) with CI / MS brackets, 15mm CP brass Pillar taps, 32mm CP brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever required.: White Vitreous China Wash basin size 630 x 450mm with a single 15mm C.P brass piller tap. (Lowest retail price of basin not less than Rs. 3000/each and Pillar tap not less than Rs. 2000/each. Materials to be selected by the Engineer in charge) | 8 | Each |  |  | 0
6 | LMR | Providing and fixing C.P. brass bib cock of approved quality conforming to IS:8931. , 15 mm nominal bore. (Lowest retail price not less than 1200/each. Materials to be selected by the Engineer in charge) | 1 | Each |  |  | 0
7 | LMR | Providing and fixing C.P. brass long body bib cock (Sink cock)of approved quality conforming to IS standards and weighing not less than 690 gms. 15 mm nominal bore (Lowest retail price not less than 1800/each. Materials to be selected by the Engineer in charge) | 11 | Each |  |  | 0
8 | 18.52.1 | Providing and fixing C.P. brass stop cock (concealed) of standard design and of approved make conforming to IS:8931: 15 mm nominal bore. | 1 | Each |  |  | 0
9 | 18.53.1 | Providing and fixing C.P. brass angle valve for basin mixer and geyser points of approved quality conforming to IS:8931 a) 15 mm nominal bore: 15mm nominal bore | 35 | Each |  |  | 0
10 | 17.28.1.1 | Providing and fixing PVC Waste pipe for sink or wash basin including PVC waste fittings complete.:Semi rigid pipe 32mm dia | 11 | Each |  |  | 0
11 | 18.21.2.1 | Providing and fixing uplasticised PVC connection pipe with brass unions : 45 cm length 15 mm nominal bore | 35 | Each |  |  | 0
12 | 18.65 | Providing and fixing SS soap Dish Holder having length of 138mm, breadth 102mm, height of 75mm with concealed fitting arrangements. Weighing not less than 106 gms. | 20 | Each |  |  | 0
13 | 17.34.1 | Providing and fixing Toilet paper holder . etc..,:C.P Brass | 15 | Each |  |  | 0
14 | 17.31 | Providing and fixing 600 x 450mm bevelled edge mirror of superior glass (of approved quality) complete with 6mm thick hard board ground fixed to wooden cleats with C.P. brass screws and washers complete. | 7 | Each |  |  | 0
15 | 17.73.2 | Providing and fixing SS towel rail complete with brackets fixed to wooden cleats with CP brass screws with concealed fitting arrangement of approved quality and colour. 600mm long towel rail with total length of 645mm, width 78mm and effective height of 88mm, weighing not less than 190gms. | 15 | Nos. |  |  | 0
16 | MR | Providing & fixing of CP Health faucet. Hand operated spray unit (instand type). (Lowest retail price not less than 1200/each. Materials to be selected by the Engineer in charge) | 9 | Set |  |  | 0
17 | M.R. | Providing and fixing of over head shower set with shower flange 170 mm long, including shower head and shower arm conforming to I.S Specification of approved make as per directions including all lead and lift etc., complete. (Lowest retail price not less than 1500/each. Materials to be selected by the Engineer in charge) | 1 | Nos. |  |  | 0
18 | 18.7 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for Hot and Cold water supply including all CPVC plain and brass threded fittings including fixing the pipe with clamps at 1.00m spacing. This includes jointing of pipes and fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer in caharge. |  |  |  |  | 0
|  | Internal Work - Exposed on wall |  |  |  |  | 0
a) | 18.7.1 | 15mm nominal outer dia.Pipes | 10 | Mtr. |  |  | 0
b) | 18.7.2 | 20mm nominal outer dia.Pipes | 30 | Mtr. |  |  | 0
c) | 18.7.3 | 25mm nominal outer dia.Pipes | 30 | Mtr. |  |  | 0
19 | 18.8 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for Hot and Cold water supply including all CPVC plain and brass threded fittings including fixing the pipe with clamps at 1.00m spacing. This includes jointing of pipes and fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer in caharge. |  |  |  |  | 0
|  | Concealed work including cutting chases and making good the wall etc. |  |  |  |  | 0
a) | 18.8.1 | 15 mm nominal outer dia.Pipes | 30 | Mtr. |  |  | 0
b) | 18.8.2 | 20 mm nominal outer dia.Pipes | 30 | Mtr. |  |  | 0
20 | LMR | Providing and fixing PVC pipes for water supply arrangements including cost pipes, fittings, Clamp/clip, solvent cement,testing of pipes, labour charges etc complete : Exposed on wall |  |  |  |  | 0
a) | LMR | 20mm dia. PVC pipe (12kg/cm2) | 15 | Mtr. |  |  | 0
b) | LMR | 25mm dia. PVC pipe (12kg/cm2) | 30 | Mtr. |  |  | 0
c) | LMR | 32mm dia. PVC pipe (10kg/cm2) | 60 | Mtr. |  |  | 0
d) | LMR | 50mm dia. PVC pipe (8kg/cm2) | 30 | Mtr. |  |  | 0
21 | LMR | Providing and fixing PVC pipes for water supply arrangements including cost pipes, fittings, solvent cement,testing of pipes, labour charges etc complete : Concealed work including cutting chases and making good the wall etc |  |  |  |  | 0
a) | LMR | 20mm dia. PVC pipe (12kg/cm2) | 50 | Mtr. |  |  | 0
b) | LMR | 25mm dia. PVC pipe (12kg/cm2) | 65 | Mtr. |  |  | 0
c) | LMR | 32mm dia. PVC pipe (10kf/cm2) | 20 | Mtr. |  |  | 0
22 | 18.18 | Providing and fixing Ball Valve (brass) of approved quality, High or low pressure, with plastic floats complete. .., |  |  |  |  | 0
a) | 18.18.2 | 20mm dia nominal bore | 2 | Nos. |  |  | 0
b) | 18.18.3 | 25mm dia nominal bore | 2 | Nos. |  |  | 0
23 | LMR | Providing, Fixing, Testing & Commissioning of full way brass valve of brass body with threaded / flanged joints complete with nuts, bolts, gaskets, washers etc. |  |  |  |  | 0
(a) | LMR | 15mm dia | 2 | Each |  |  | 0
(b) | LMR | 20mm dia | 4 | Each |  |  | 0
24 | 18.17 | Providing and fixing Gun metal gate valve with C.I. wheel of approved quality (screwed end). |  |  |  |  | 0
a) | 18.17.1 | 25 mm dia nominal bore | 2 | Nos. |  |  | 0
b) | 18.17.2 | 32 mm dia nominal bore | 2 | Nos. |  |  | 0
25 | 18.77 | Cutting holes upto 15 x 15 cm in R.C.C. floors and roofs for passing drain pipe etc. and repairing the hole after insertion of drain pipe etc. with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) including finishing complete. | 20 | each |  |  | 0
26 | 12.41.2 | Providing and fixing on wall face unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A including jointing with seal ring conforming to IS : 5382 leaving 10 mm gap for thermal expansion.(i) Single socketed pipes. 110 mm diameter | 60 | mtr. |  |  | 0
27 | 12.42 | Providing and fixing on wall face unplasticised - PVC moulded fittings/ accessories for unplasticised Rigid PVC rain water pipes conforming to IS : 13592 Type A including jointing with seal ring conforming to IS : 5382 leaving 10 mm gap for thermal expansion. |  |  |  |  | 0
a) | 12.42.1.2 | 110 mm Coupler | 15 | each |  |  | 0
b) | 12.42.3.2 | 110x110x110 mm Single tee with door | 4 | each |  |  | 0
c) | 12.42.5.2 | 110 mm bend | 12 | each |  |  | 0
d) | 12.42.6.2 | 110 mm Shoe | 4 | each |  |  | 0
28 | 12.43.2 | Providing and fixing unplasticised -PVC pipe clips of approved design to unplasticised - PVC rain water pipes by means of 50x50x50mm hard wood plugs, screwed with M.S. screws of required length including cutting brick work and fixing in cement mortar 1:4 (1 cement : 4 coarse sand) and making good the wall etc. complete. 110 mm | 60 | Each |  |  | 0
29 | MR | Providing and fixing to the Inlet mouth of rain water pipe S.S grating 110mm diameter and weighing not less than 440 grams. | 4 | Nos |  |  | 0
30 | M.R. | Providing and fixing PVC soil, waste and vent pipe to IS : 13592 of SWR quality, including all fittings, like EG : Bends, Tees, Elbows, Collars, junction, inspection doors, cowls, offsets, access pipes, jointing with rubber ring / solvent cement by application of leak proof adhesive like FRP paste including cutting holes in walls and floors and making good. clipping to walls and slabs, trenching, refilling etc. complete Make: Supreme, Finolex, Astral |  |  |  |  | 0
a) | MR | 50mm dia (6kg / sq.cm) | 35 | Mtr. |  |  | 0
b) | M.R. | 63mm dia (6kg / sq.cm) | 90 | Mtr. |  |  | 0
c) | M.R. | 75mm dia (6kg / sq.cm) | 80 | Mtr. |  |  | 0
d) | MR | 90mm dia (6kg / sq.cm) | 30 | Mtr. |  |  | 0
e) | M.R. | 110mm dia (6 kg / sq.cm) | 120 | Mtr. |  |  | 0
f) | M.R. | 160mm dia (6 kg / sq.cm) | 80 | Mtr. |  |  | 0
g | MR | 50mm dia. (10kg/sq.cm) | 30 | Mtr. |  |  | 0
31 | MR | Providing and fixing PVC pipes for external works including all specials and fittings, solvent cementearth work excavation for trenches, refilling and after laying pipes ect complete |  |  |  |  | 0
a) | MR | 20mm dia PVC pipes, 12kg/cm2 for water supply connection from the existing line | 50 | Mtr. |  |  | 0
b) | MR | 25mm dia PVC pipes, 12kg/cm2 for water supply connection from the existing line | 50 | Mtr. |  |  | 0
32 | M.R. | Providing and fixing PVC floor trap self cleansing design with or without vent arm complete including cutting and making good the walls and floors. |  |  |  |  | 0
a) | MR | 110mm dia inlet 110mm dia outlet | 20 | Nos |  |  | 0
33 | M.R | Providing and fixing CP grating of 6mm thick with rim including setting in floor with white cement mortar and making good the floor (Chilli make) |  |  |  |  | 0
a) |  | 125mm dia | 20 | Nos. |  |  | 0
34 | 19.7 | Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement : 4 coarse sand ) with R.C.C. top slab with 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand : 8 graded stone aggregate 40mm nominal size), inside plastering 12mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) finished with a floating coat of neat cement complete as per standard design : |  |  |  |  | 0
a) | 19.7.1.1 | Inside size 90x80 cm and 45 cm deep including C.I. cover with frame (light duty) 455x610 mm internal dimensions, total weight of cover and frame to be not less than 38 kg (weight of cover 23 kg and weight of frame 15 kg) : With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 8 | Nos. |  |  | 0
b) | 19.7.2 | Inside size 120x90 cm and 90 cm deep including C.I. cover with frame (medium duty) 500 mm internal diameter, total weight of cover and frame to be not less than 116 kg (weight of cover 58 kg and weight of frame 58 kg) : |  |  |  |  | 0
| 19.7.2.1 | With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 2 | Nos. |  |  | 0
c) | 19.7.3 | Inside size 120x90 cm and 90 cm deep including C.I. cover with frame (heavy duty) 560 mm internal diameter, total weight of cover and frame to be not less than 208 kg (weight of cover 108 kg and weight of frame 100 kg) : |  |  |  |  | 0
| 19.7.3.1 | With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 2 | Nos. |  |  | 0
35 | 19.8 | Extra for depth for manholes |  |  |  |  | 0
a) | 19.8.1.1 | Size 90x80 cm: With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 5 | m |  |  | 0
b) | 19.8.2.1 | Size 120x90 cm: with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 5 | m |  |  | 0
36 | 19.4 | Providing and fixing square – mouth PVC. Gully trap grade “A” complete with CI grating brick masonry chamber with water tight tight CI cover with frame of 300 x 300mm size (inside) the weight of cover to be not less than 4.50 kg and frame to be not less than 2.70 kg as per standard design |  |  |  |  | 0
a) | 19.4.2.1 | 150 x 100mm size P type with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 3 | each |  |  | 0
37 | LMR | Supplying and fixing Wash Basin with one pair mounting brackets, EWC & Cistern complete with fittings & seat cover, hinged rail, grab rails and one no of faucet for WB with Rack Bolt, Flexible Tube for pillar Tap & Waste Coupling Designed for people with special needs (Handicapped/ Physically disabled People) P trap, Angle valve, including fittings and brackets, cutting and making good the walls wherever required, including cost & conveyance of all materials, labour charges, sundries etc complete as directed by the Engineer in charge.(Materials should be selected by Engineer in charge).(Make Hindware No. 70002- | 2 | Each |  |  | 0
38 | 18.48 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank ISI : 12701 marked with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank | 2000 | Ltrs |  |  | 0
39 | 19.32.1 | Making soak pit 2.5 m diameter 3.0 metre deep with 45 x 45 cm dry brick honey comb shaft with bricks and S.W. drain pipe 100 mm diameter, 1.8 m long complete as per standard design.With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | 1 | Each |  |  | 0
40 | LMR | Providing and fixing 560 mmC.I. M.H.cover with frame (heavy duty) total weight of cover and frame to be not less than 208 kg (weight of cover 108 kg and weight of frame 100 kg) : | 2 | Each |  |  | 0
|  | TOTAL COST |  |  | Rs. |  | 0

## electrical
Electrical works
Sl: No: | Code No | Description of item | Unit | Qty | Rate in figures (Rs.) | Rate in words (Rs.) | Amount (Rs.)
1 | 1.10 | Point wiring in PVC conduit, with Modular type switch: Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required.
a | 1.10.2 | Group B | Point | 50 |  |  | 0
b | 1.10.3 | Group C | Point | 130 |  |  | 0
2 | 1.11 | Twin control point wiring in PVC conduit, with modular type switch: Wiring for twin control light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, 2 way modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required. | Point | 6 |  |  | 0
3 | 1.12 | Power plug wiring in PVC conduit ( 2x4 sq mm ): Wiring for light/ power plug with 2X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 1 No 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | Metre | 250 |  |  | 0
4 | 1.13 | Power plug wiring in PVC conduit ( 4x4 sq mm ): Wiring for light/ power plug with 4X4 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 2 Nos 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | Metre | 50 |  |  | 0
5 | 1.14 | Circuit Sub main wiring in PVC Conduit: Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required |  |  |  |  | 0
a | 1.14.1 | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | Metre | 970 |  |  | 0
b | 1.14.2 | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | Metre | 150 |  |  | 0
c | 1.14.9 | 4 X 6 sq. mm + 2 X 6 sq. mm earth wire | Metre | 30 |  |  | 0
6 | 1.18 | Telephone wiring in existing conduit: Supplying and drawing following pair 0.5 sq mm FRLS PVC insulated annealed copper conductor, unarmored telephone cable in the existing surface/ recessed steel/ PVC conduit as required. |  |  |  |  | 0
a | 1.18.2 | 2 Pair | Metre | 550 |  |  | 0
b | 1.18.3 | 4 Pair | Metre | 100 |  |  | 0
7 | 1.19 | T. V cable in existing conduit: Supplying and drawing co-axial TV cable RG-6 grade, 0.7 mm solid copper conductor PE insulated, shielded with fine tinned copper braid and protected with PVC sheath in the existing surface/ recessed steel/ PVC conduit as required. | Metre | 30 |  |  | 0
|  | PVC CONDUIT, METAL BOXES |  |  |  |  | 0
8 | 1.21 | S/F PVC conduit: Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. |  |  |  |  | 0
a | 1.21.1 | 20 mm | Metre | 250 |  |  | 0
b | 1.21.2 | 25 mm | Metre | 500 |  |  | 0
9 | 1.22 | S/F Metal boxes: Supplying and fixing metal box of following sizes (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including painting etc as required. |  |  |  |  | 0
| 1.22.7 | 200 mm X 150 mm X 60 mm deep | Each | 2 |  |  | 0
10 | 1.24 | S/F Modular type switch/ socket: Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required. |  |  |  |  | 0
d | 1.24.6 | Telephone socket outlet | Each | 22 |  |  | 0
e | 1.24.7 | TV antenna socket outlet | Each | 1 |  |  | 0
11 | 1.25 | Supplying and fixing electronic fan regulator: Supplying and fixing stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | Each | 36 |  |  | 0
12 | 1.26 | S/F Modular type blanking plates: Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | Each | 30 |  |  | 0
13 | 1.27 | S/F Modular boxes, base & cover plate: Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc as required. |  |  |  |  | 0
| 1.27.1 | 1 or 2 Module (75mmX75mm) | Each | 58 |  |  | 0
14 | 1.31 | S/F light plug point modular type accessaries: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. (For light plugs to be used in non residential buildings). | Each | 70 |  |  | 0
15 | 1.32 | S/F Power plug point with modular type switch: Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | Each | 24 |  |  | 0
16 | 1.33 | S/F Ceiling rose: Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required. | Each | 60 |  |  | 0
17 | 1.41 | ITC Fluroscent / LED fitting directly on surface/ceiling: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc. directly on ceiling/ wall, including connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | Each | 118 |  |  | 0
18 | 1.42 | ITC Fluroscent/LED fitting with down rod: Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting of all types, complete with all accessories and tube etc., including supplying and fixing ball and socket arrangement, 2 no. down rods of 20 mm dia X 1.6 mm thick steel conduit upto 30 cm length, painting and wiring the down rods and connection with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable and earthing etc. as required. | Each | 20 |  |  | 0
19 | 1.43 | S/F extra down rod: Providing and fixing extra conduit down rod of 20 mm dia, 2 X 10 cm length wiring with 2 X 1.5 sq. mm FR PVC insulated, copper conductor, single core cable including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | Each | 40 |  |  | 0
20 | 1.44 | ITC Ceiling fan: Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard length (upto 30 cm) with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable etc. as required. | Each | 36 |  |  | 0
21 | 1.48 | Extra down rod 15 mm dia 20 CM Length: Supplying and fixing extra conduit down rod of 20 cm length G.I. pipe 15 mm dia, heavy gauge including painting etc. as required. (Note : More than 5 cm length shall be rounded to the nearest 10 cm and 5 cm or less shall be ignored) | Each | 72 |  |  | 0
22 | 1.50 | ITC Exhaust fan: Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. |  |  |  |  | 0
| 1.50.1 | Upto 450 mm sweep | Each | 8 |  |  | 0
23 | 2.2 | S&F MCCB in cubicle Pannel: Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections, etc. as required. |  |  |  |  | 0
a | 2.2.1 | 100 Amp, 16 KA TP MCCB | Each | 1 |  |  | 0
b | 2.2.2 | 125 Amp, 16 KA TP MCCB | Each | 2 |  |  | 0
24 | 2.4 | S/F TP MCB DB: Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) |  |  |  |  | 0
a | 2.4.4 | 4 way (4 + 12), Double door | Each | 3 |  |  | 0
b | 2.4.5 | 6 way (4 + 18), Double door | Each | 2 |  |  | 0
25 | 2.9 | S/F Vertical Type Pre Wired TP MCB DB: Supplying and fixing following way prewired vertical type TP&N MCB distribution board of steel sheet for 415 volts on surface/ recess complete with loose wire box of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's, terminal connectors for all incoming and outgoing circuits, duly prewired with adequate size of FR PVC insulated copper conductor upto the terminal connector/ neutral link, earthing etc as required ,suitable for MCCB incomer.(But without MCB/ RCCB/ Isolator). (Note : Prewired vertical type MCB TPDB is normally used where 3 phase outlets are required.) |  |  |  |  | 0
a | 2.9.6 | 6 way Double door | Each | 1 |  |  | 0
b | 2.9.7 | 8 way Double door | Each | 2 |  |  | 0
26 | 2.10 | S/F 'C' series, MCB: Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  |  | 0
a | 2.10.1 | Single pole | Each | 40 |  |  | 0
b | 2.10.4 | Triple pole | Each | 6 |  |  | 0
27 | 2.11 | S/F S P MCB blanking plate: Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | Each | 30 |  |  | 0
28 | 2.13 | S/F FP MCB Isolator: Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  |  | 0
a | 2.13.1 | 40 amps | Each | 3 |  |  | 0
b | 2.13.2 | 63 amps | Each | 2 |  |  | 0
29 | 2.15 | S/F TPN RCCB: Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current upto 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  |  | 0
a | 2.15.1 | 25 amps | Each | 3 |  |  | 0
b | 2.15.3 | 63 amps | Each | 2 |  |  | 0
30 | 2.18 | S/F 20A SPN MCB industrial socket outlet: Supplying and fixing 20 amps, 240 volts, SPN industrial type, socket outlet, with 2 pole and earth, metal enclosed plug top alongwith 20 amps "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | Each | 3 |  |  | 0
31 | 2.20 | S/F 30A TPN MCB industrial socket: Supplying and fixing 30 amps, 415 volts, TPN industrial type, socket outlet, with 4 pole and earth, metal enclosed plug top alongwith 30 amps "C" curve, TPMCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | Each | 3 |  |  | 0
32 | 2.21 | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | Each | 3 |  |  | 0
33 | 5.16 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess: Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | Metre | 100 |  |  | 0
34 | 7.7 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. |  |  |  |  | 0
| 7.7.1 | Upto 35 sq. mm (clamped with 1mm thick saddle) | Metre | 100 |  |  | 0
35 | 9.1 | Supplying and making end termination with brass compression gland and aluminium lugs: Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. |  |  |  |  | 0
a | 9.1.20 | 3½ X 25 sq. mm (38mm) | Each | 6 |  |  | 0
b | 9.1.21 | 3½ X 35 sq. mm (32mm) | Each | 4 |  |  | 0
c | 9.1.32 | 4 X 10 sq. mm (25mm) | Each | 8 |  |  | 0
d | 9.1.33 | 4 X 16 sq. mm (28mm) | Each | 6 |  |  | 0
0
|  | LMR Items |  |  |  |  | 0
36 |  | Point wiring in PVC conduit, with Modular type switch, Group control Wiring for light point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc as required for controling two or three lights by single switch. | Each | 10 |  |  | 0
37 |  | Supplying and drawing of UTP 4 pair CAT -6A LAN cable in existing surface/ recessed PVC conduit as required, AMP/Molex make | Metre | 1000 |  |  | 0
38 |  | Supply & installation of modular type Cat 6A information outlet with modular plate & GI box including connection etc as required, AMP/ Molex make | Each | 40 |  |  | 0
39 |  | Supply & installation of following pair krone module in suitable size MDF box with all accessories. |  |  |  |  | 0
|  | 50 pair | Each | 1 |  |  | 0
40 |  | S/F PVC holder: Supplying and fixing PVC batten/ angle holder including connection etc. as required. | Each | 13 |  |  | 0
41 |  | S/F DP MCB Isolator with Enclosure: Supplying and fixing DP sheet steel enclosure on surface/ recess along with 25/32amps 240 volts "C" curve DP MCB complete with connections, testing and commissioning etc. as required. | each | 11 |  |  | 0
42 |  | S/F 4P MCB Isolator with Enclosure: Supplying and fixing 4P sheet steel enclosure on surface/ recess along with 16/25/32amps 415 volts "C" curve 4P MCB isolator complete with connections, testing and commissioning etc. as required. | each | 2 |  |  | 0
43 |  | Supply of Surface mounted Indoor Industrial Tube, TMC 501 P 2xT-LED with mounting rail for TLED lamps + LED tube 1200mm with Mounting Accessories of Philips or Wipro & Crompton | Each | 29 |  |  | 0
44 |  | Supply of Surface mounted Endura LED Bulkhead WT 202W LED of Philips/Equi + LED Non Dimmable 5W B22 | Each | 2 |  |  | 0
45 |  | Supply & installation of LED Lamp Non Dimmable 7/9W B22 on existing angle batten | Each | 13 |  |  | 0
46 |  | Supply of Linnet - LCL-10-CDL,Sleek LED mirror light,with high out put diffuser, 2 feet size of Crompton or Equi | Each | 15 |  |  | 0
47 |  | Supply of Indoor down lighter,recessed mounted LED down lights with the option for fixed/ adjustable and spot options. BBS312 1xDLED of Philips or Equi | Each | 50 |  |  | 0
48 |  | Supply of Indoor recess mounted direct/indirect architectural luminaire giving soft glare free light,provided with high transmittance, micro linear frosted (MLF) PMMA curved diffuser of size 600mmx600mm LED LCTAR1 - 40-CDL of crompton or equi Philips/Wipro | Each | 29 |  |  | 0
49 |  | Supply of ceiling fan 1050/1200 mm sweep,230V,1Ph, complete with double ball bearing, motor blades, down rods, canopy, capacitor etc complete as required 5 star rating (Crompton Riviera / Usha Maxx Air / Khaitan Newtec) | Each | 36 |  |  | 0
50 |  | Supply and installation of Decorative Wall fan 400 mm sweep, 230V.1Ph, complete with Openable mesh Cover ,string Operated etc as required. (Crompton WM Wind Flo / Usha Helix high speed / Khaitan Merlin Hi speed) | Each | 6 |  |  | 0
51 |  | Supply and fitting 250 mm sweep automatic shutter Sleek and stylish design type exhaust fan complete with louvers and cable from ceiling rose / connector to fan. (Usha Crisp Air / Crompton Crossair / Khaitan Vento). | Each | 5 |  |  | 0
52 |  | Supply and fitting 450 mm sweep heavy duty Industrial type exhaust fan complete with louvers and cable from ceiling rose / connector to fan. (Usha Turbo Hi speed / Crompton Driffair / Khaitan Euro Metal). | Each | 3 |  |  | 0
53 |  | Supply of the following size 1.1kV grade XLPE insulated PVC sheathed, armoured Aluminium conductor power cable confirming to IS 7098 (part 1) ammended upto date. |  |  |  |  | 0
a |  | 3½ X 35 sq. mm | Metre | 40 |  |  | 0
b |  | 3½ X 25 sq. mm | Metre | 30 |  |  | 0
c |  | 4 X 16 sq. mm | Metre | 60 |  |  | 0
d |  | 4 X 10 sq. mm | Metre | 90 |  |  | 0
54 |  | S/F 'C' series, MCB: Supplying and fixing following rating, 415 volts, "C" curve, miniature circuit breaker suitable for inductive load of three pole (TP) in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  |  | 0
a |  | 63 Amps | Each | 2 |  |  | 0
b |  | 40Amps | Each | 3 |  |  | 0
55 |  | Supplying and fixing U-PVC Trunking Type Cable Management System for Power, Data, Communication Cables/wires complete with Cover Plates, End Caps, Internal & External angles, Cable Retainers, cable Dividers,Tees, accessories etc as required. The same shall be suitable for fixing 6A, 16A Sockets, switchs, RJ45, RJ-11 with its modular box & front plate etc. The CMS shall conform to BS:4678/ BS:4662 & corresponding BIS. |  |  |  |  | 0
|  | Size 105 x 50 mm with separation partition & Plastic clip | Mtr | 60 |  |  | 0
56 |  | Supply & installation of following modular type switches & sockets in the exisitng DLP trunking with all required accessories like modular box, front plate etc as required. |  |  |  |  | 0
a |  | 6A socket with switch | Each | 10 |  |  | 0
b |  | 6/16A socket with switch | Each | 6 |  |  | 0
c |  | RJ45 data outlet | Each | 10 |  |  | 0
d |  | RJ11 telephone outlet | Each | 4 |  |  | 0
|  | Grand Total Electrical |  |  |  |  | 0

## Civil Det. Est-5. (hidden)
CONSTRUCTION OF C.E.D MACHINE MANUFACTURING UNIT AT AKKULAM, THIRUVANANTHAPURAM
DETAILED ESTIMATE - CIVIL
Item No | DSR code | Details of items |  | No | Length | Breadth | Height | Quantity
1 | 20.2A.1 &2 | Boring, providing and installation bored cast-in-situ reinforced cement concrete piles of garde M-25 of specified diameter and length below pile cap, to carry a safe working load not less than specified, excluding the cost of steel reinforcement but including the cost of boring with bentonite solution and temporary casing of appropriate length for setting out and removal of same and the length of the pile to be embedded in the pile cap etc. by Crawler mounted, telescopic boom hydraulic pilling Rig all complete, including removal of excavated earth with all its lifts and leads (length of pile for payment shall be measured up to bottom of pile cap). Note: Truck Mounted rotary/TMR/Tube well boring machine shall not be used.700mm dia. Piles
|  | Piles under column (Southern side ) | 1 | 17 | 12 |  |  | 204
|  | Car porch | 1 | 2 | 16 |  |  | 32
|  | Total | [5 empty] | 236
|  | Say | [5 empty] | 240 | m
2 | 20.6.2 | Vertical load testing of piles in accordance with IS 2911 (Part IV) including installation of loading platform by Kentledge method and preparation of pile head or construction of test cap and dismantling of test cap after test etc. complete as per specification & the direction of Engineer in-charge. Note: 1. Initial and Routine Load Test shall not be carried out by Dynamic method of testing. Note: 2. Testing agency shall submitt the design of loading platform for the approval of Engineer-in-charge.: Single pile above 50 tonne and upto 100 tonne Safe capacity
a | 20.6.2.1 | Initial test (Test Load 2.5 times the Safe capacity) |  | 1 |  |  |  | 1 | No
b | 20.6.2.2 | Routine test (Test Load 1.5 times the Safe capacity) |  | 1 |  |  |  | 1 | No
3(a) | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30cm in depth. 1.5m in width as well as 10 sqm on plan) including disposal of excavated earth, lead upto 50m and lift upto 1.5m, disposed earth to be levelled and neatly dressed. All kinds of soil
|  | Levelling site |  | 1 | 20 | 15 | 2 | 600
|  | For Pile cap |  | 19 | 1.7 | 1.7 | 1.3 | 71.383
|  | Foundation of retaining wall -Eastern side |  | 1 | 20 | 3.2 | 1.1 | 70.4
|  | Do Southern side |  | 1 | 10 | 3.2 | 1.1 | 35.2
|  | For foundation of Columns at Northern side of work shop |  | 12 | 2.4 | 2.4 | 0.9 | 62.208
|  | Columns at Eastern side building |  | 10 | 2.7 | 2.4 | 1.2 | 77.76
|  | Ramp |  | 1 | 2 | 6.2 | 0.4 | 4.96
|  | Entrance portion |  | 1 | 1.7 | 6.5 | 0.3 | 3.315
|  | Septic tank |  | 1 | 3.8 | 2.6 | 1.5 | 14.82
|  | Total | [5 empty] | 940.046
|  | Say | [5 empty] | 950 | m3
3(b) | 2.6.1 + 2.26.1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30cm in depth. 1.5m in width as well as 10 sqm on plan) including disposal of excavated earth, lead upto 50m and lift 1.50m to 3.0m, disposed earth to be levelled and neatly dressed. All kinds of soil All classes of soil
|  | Septic tank |  | 1 | 3.8 | 2.6 | 0.95 | 9.386
|  | Total | [5 empty] | 9.386
[7 empty] | Say | 12 | m3
4 | 2.8.1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan) including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All kinds of soil.
|  | For rubble masonry foundation to the sides of work shop- Northern side |  | 1 | 15.5 | 0.8 | 0.75 | 9.3
|  | Do Southern side |  | 1 | 23.9 | 0.8 | 0.75 | 14.34
|  | Do Western side |  | 1 | 18.75 | 0.8 | 0.75 | 11.25
|  | Machine centre and store sides |  | 1 | 27 | 0.8 | 0.75 | 16.2
|  | Cross wall |  | 2 | 4.38 | 0.8 | 0.75 | 5.256
|  | Retaining wall at Southern side |  | 1 | 60 | 0.6 | 0.6 | 21.6
|  | Plinth beams | [5 empty] | 0
|  | Y-direction |  | 2 | 18 | 0.4 | 0.2 | 2.88
|  | left of stair |  | 1 | 5.7 | 0.4 | 0.2 | 0.456
|  | Middle of toilets |  | 1 | 5.7 | 0.4 | 0.2 | 0.456
|  | X-direction left portion |  | 4 | 6.42 | 0.4 | 0.2 | 2.0544
|  | do right portion |  | 4 | 6.2 | 0.4 | 0.2 | 1.984
|  | Extra beams | [5 empty] | 0
|  | Front of utility |  | 1 | 6.42 | 0.23 | 0.05 | 0.07383
|  | Front of cafeteria |  | 1 | 6.2 | 0.23 | 0.05 | 0.0713
|  | Toilets |  | 2 | 6.12 | 0.23 | 0.05 | 0.14076
|  | do |  | 2 | 4.25 | 0.23 | 0.05 | 0.09775
|  | do |  | 2 | 1.5 | 0.23 | 0.05 | 0.0345
|  | Total | [5 empty] | 86.1945
|  | Say | [5 empty] | 90 | m3
5 | 2.25 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m
|  | Qty of earth work as per item above except site levelling | [5 empty] | 426.2405
|  | Deduct PCC of foundation | [5 empty] | 29.145
|  | PCC under rubble wall | [5 empty] | 11.2692
|  | Qty of RCC upt to plinth | [5 empty] | 199.464
Plinth beams
|  | Y-direction |  | 2 | 18 | 0.3 | 0.2 | 2.16
|  | left of stair |  | 1 | 5.7 | 0.3 | 0.2 | 0.342
|  | Middle of toilets |  | 1 | 5.7 | 0.3 | 0.2 | 0.342
|  | X-direction left portion |  | 4 | 6.42 | 0.3 | 0.2 | 1.5408
|  | do right portion |  | 4 | 6.2 | 0.3 | 0.2 | 1.488
|  | Qty of rubble foundation | [5 empty] | 21.6
|  | Volume of Septic tank |  | 1 | 2.6 | 1.4 | 2.35 | 8.554
|  | Total deduction | [5 empty] | 275.905
|  | Less deduction | [5 empty] | 150.3355
Add quantity for plinth filling
|  | Work shop |  | 1 | 41.55 | 17.55 | 0.45 | 328.1411
|  | Electrical room |  | 1 | 6.49 | 5.59 | 0.5 | 18.1395
|  | Utility room |  | 1 | 6.49 | 3.42 | 0.5 | 11.0979
|  | Cafeteria |  | 1 | 6.2 | 9.24 | 0.5 | 28.644
|  | Passage |  | 1 | 12.92 | 2 | 0.5 | 12.92
|  | Stair room |  | 1 | 3 | 5.96 | 0.5 | 8.94
|  | Store |  | 1 | 2.97 | 5.96 | 0.5 | 8.8506
|  | WC |  | 4 | 1.5 | 1.2 | 0.5 | 3.6
|  | Toilets- left |  | 1 | 2.5 | 1.5 | 0.5 | 1.875
|  | do |  | 1 | 1.5 | 2.75 | 0.5 | 2.0625
|  | PH toilet |  | 1 | 1.5 | 4.25 | 0.5 | 3.1875
|  | Front portion of toilet |  | 1 | 6.49 | 1.48 | 0.5 | 4.8026
|  | Total | [5 empty] | 582.5963
|  | Say | [5 empty] | 591 | m3
6 | 1.1.2.8 | Conveying and disposing off excavated excess earth from the side as directed by the Engineer in charge
|  | Qty of earth work excavation | [5 empty] | 1026.2405 | m3
|  | Refilling quantity | [5 empty] | 582.5963
|  | Balance | [5 empty] | 443.6442
|  | Say | [5 empty] | 454 | m3
7 | 2.34.1 | Supplying chemical emulsion in sealed containers including delivery as specified Chlorpyriphos/ Lindane emulsifiable concentrate of 20%
|  | Work shop |  | 1 | 41.55 | 17.55 |  | 729.2025
|  | Electrical room |  | 1 | 6.49 | 5.59 |  | 36.2791
|  | Utility room |  | 1 | 6.49 | 3.42 |  | 22.1958
|  | Cafeteria |  | 1 | 6.2 | 9.24 |  | 57.288
|  | Passage |  | 1 | 12.92 | 2 |  | 25.84
|  | Stair room |  | 1 | 3 | 5.96 |  | 17.88
|  | Store |  | 1 | 2.97 | 5.96 |  | 17.7012
|  | WC |  | 4 | 1.5 | 1.2 |  | 7.2
|  | Toilets- left |  | 1 | 2.5 | 1.5 |  | 3.75
|  | do |  | 1 | 1.5 | 2.75 |  | 4.125
|  | PH toilet |  | 1 | 1.5 | 4.25 |  | 6.375
|  | Front portion of toilet |  | 1 | 6.49 | 1.48 |  | 9.6052
|  | Total | [5 empty] | 937.4418
|  | Qty of chemical |  | 1 | 937.4418 | 0.55556 |  | 520.801
|  | Say | [5 empty] | 521 | litre
8 | 2.35.3.1 | Treatment of soil under existing floors using chemical emulsion @ one litre per hole, 300 mm apart including drilling 12 mm diameter holes and plugging with cement mortar 1 :2 (1 cement : 2 Coarse sand) to match the existing floor : With Chlorpyriphos/Lindane E.C. 20% with 1% concentration
|  | Area as per above item | [5 empty] | 937.4418
|  | Say | [5 empty] | 938 | m2
9 | 4.1.5 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:3:6 (1 Cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size).
|  | For Pile cap |  | 17 | 1.7 | 1.7 | 0.1 | 4.913
|  | Foundation of retaining wall -Eastern side |  | 1 | 20 | 3.2 | 0.1 | 6.4
|  | Do Southern side |  | 1 | 10 | 3.2 | 0.1 | 3.2
|  | For foundation of Columns at Northern side of work shop |  | 12 | 2.4 | 2.4 | 0.1 | 6.912 |  |  | 29.145
|  | Columns at Eastern side building |  | 10 | 2.7 | 2.4 | 0.1 | 6.48
|  | Ramp |  | 1 | 2 | 6.2 | 0.1 | 1.24
Car porch
Flooring concrete
|  | Work shop |  | 1 | 41.55 | 12.55 | 0.15 | 78.2179
|  | Work shop |  | 1 | 41.55 | 5 | 0.05 | 10.3875
|  | Electrical room |  | 1 | 6.49 | 5.59 | 0.05 | 1.814
|  | Utility room |  | 1 | 6.49 | 3.42 | 0.05 | 1.1098
|  | Cafeteria |  | 1 | 6.2 | 9.24 | 0.05 | 2.8644
|  | Passage |  | 1 | 12.92 | 2 | 0.05 | 1.292
|  | Stair room |  | 1 | 3 | 5.96 | 0.05 | 0.894
|  | Store |  | 1 | 2.97 | 5.96 | 0.05 | 0.88506
|  | WC |  | 4 | 1.5 | 1.2 | 0.05 | 0.36
|  | Toilets- left |  | 1 | 2.5 | 1.5 | 0.05 | 0.1875
|  | do |  | 1 | 1.5 | 2.75 | 0.05 | 0.20625
|  | PH toilet |  | 1 | 1.5 | 4.25 | 0.05 | 0.31875
|  | Front portion of toilet |  | 1 | 6.49 | 1.48 | 0.05 | 0.48026
|  | Entrance portion |  | 1 | 1.7 | 6.5 | 0.1 | 1.105
|  | Porch |  | 1 | 3 | 7 | 0.1 | 2.1
|  | Under plinth beam | [5 empty] | 0
|  | Y-direction |  | 2 | 18 | 0.4 | 0.05 | 0.72
|  | left of stair |  | 1 | 5.7 | 0.4 | 0.05 | 0.114
|  | Middle of toilets |  | 1 | 5.7 | 0.4 | 0.05 | 0.114
|  | X-direction left portion |  | 4 | 6.42 | 0.4 | 0.05 | 0.5136
|  | do right portion |  | 4 | 6.2 | 0.4 | 0.05 | 0.496
|  | Extra beams | [5 empty] | 0
|  | Front of utility |  | 1 | 6.42 | 0.23 | 0.05 | 0.07383
|  | Front of cafeteria |  | 1 | 6.2 | 0.23 | 0.05 | 0.0713
|  | Toilets |  | 2 | 6.12 | 0.23 | 0.05 | 0.14076
|  | do |  | 2 | 4.25 | 0.23 | 0.05 | 0.09775
|  | do |  | 2 | 1.5 | 0.23 | 0.05 | 0.0345
|  | Septic tank |  | 1 | 2.8 | 1.6 | 0.1 | 0.448
|  | Total | [5 empty] | 134.1911
|  | Say | [5 empty] | 140 | m3
10 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:4:8 (1 Cement : 4 coarse sand : 8 graded stone aggregate 40 mm nominal size).
|  | For rubble masonry foundation to the sides of work shop- Northern side |  | 1 | 15.5 | 0.8 | 0.15 | 1.86
|  | Do Southern side |  | 1 | 23.9 | 0.8 | 0.15 | 2.868
|  | Do Western side |  | 1 | 18.75 | 0.8 | 0.15 | 2.25
|  | Machine centre and store sides |  | 1 | 27 | 0.8 | 0.15 | 3.24
|  | Cross wall |  | 2 | 4.38 | 0.8 | 0.15 | 1.0512
|  | Total | [5 empty] | 11.2692
|  | Say | [5 empty] | 19 | m3
11 | 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size)
|  | Inside of Septic tank |  | 1 | 2.3 | 1.1 | 0.05 | 0.1265
|  | Fixing CI MH cover | 3.14 | 4 | 0.9 | 0.3 | 0.05 | 0.16956
|  | Ramp |  | 1 | 1.85 | 6 | 0.45 | 4.995
|  | Total | [5 empty] | 5.2911
|  | Say | [5 empty] | 7 | m3
12 | 5.37 | Providing and laying in position ready mixed M-25 grade concrete for reinforced cement concrete work, using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , excluding the cost of centering, shuttering finishing and reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, improve workability without impairing strength and durability as per direction of the Engineer - in - charge.
(Note :- Cement content considered in this item is @ 330 kg/cum. Excess/less cement used as per design mix is payable/recoverable separately).
a | 5.37.1 | All works upto plinth level.
|  | For Pile cap |  | 19 | 1.5 | 1.5 | 1.2 | 51.3
|  | Foundation of retaining wall -Eastern side |  | 1 | 20 | 3 | 0.4 | 24
|  | Do Southern side |  | 1 | 10 | 3 | 0.4 | 12
|  | For foundation of Columns at Northerns side of work shop |  | 12 | 2.2 | 2.2 | 0.8 | 46.464
|  | Columns at Eastern side building |  | 10 | 2.5 | 2.2 | 0.9 | 49.5
|  | Retaining wall up to plinth level |  | 1 | 30 | 0.45 | 1.2 | 16.2 |  | 199.464
Plinth beams
|  | Y-direction |  | 2 | 18 | 0.3 | 0.6 | 6.48
|  | left of stair |  | 1 | 5.7 | 0.3 | 0.6 | 1.026
|  | Middle of toilets |  | 1 | 5.7 | 0.3 | 0.6 | 1.026
|  | X-direction left portion |  | 4 | 6.42 | 0.3 | 0.6 | 4.6224
|  | do right portion |  | 4 | 6.2 | 0.3 | 0.6 | 4.464
|  | Extra beams | [5 empty] | 0
|  | Front of utility |  | 1 | 6.42 | 0.23 | 0.45 | 0.66447
|  | Front of cafeteria |  | 1 | 6.2 | 0.23 | 0.45 | 0.6417
|  | Toilets |  | 2 | 6.12 | 0.23 | 0.45 | 1.2668
|  | do |  | 2 | 4.25 | 0.23 | 0.45 | 0.87975
|  | do |  | 2 | 1.5 | 0.23 | 0.45 | 0.3105
|  | Grade slab Eastern side building |  | 1 | 13.52 | 18 | 0.15 | 36.504
|  | do Work shop |  | 1 | 41.55 | 5 | 0.15 | 31.1625
Septic tank
|  | Bottom slab |  | 1 | 2.6 | 1.4 | 0.15 | 0.546
|  | Side walls allround |  | 1 | 7.4 | 0.15 | 2.1 | 2.331
|  | Top slab |  | 1 | 2.6 | 1.4 | 0.1 | 0.364
|  | Baffle wall |  | 1 | 1.4 | 0.05 | 0.45 | 0.0315
|  | Total | [5 empty] | 291.7847
|  | Say | [5 empty] | 303 | m3
b | 5.37.2 | All works above plinth level upto floor V level.
Basement floor
|  | column |  | 12 | 0.3 | 0.55 | 3.45 | 6.831
|  | Retaining wall |  | 1 | 30 | 0.34 | 3.45 | 35.19
Lintels
X-direction
|  | Left portion |  | 5 | 6.49 | 0.23 | 0.15 | 1.1195
|  | do |  | 1 | 3.47 | 0.23 | 0.15 | 0.11972
|  | Right portion |  | 1 | 6.2 | 0.23 | 0.15 | 0.2139
|  | do |  | 1 | 5.9 | 0.23 | 0.15 | 0.20355
|  | do |  | 1 | 2.97 | 0.23 | 0.15 | 0.10247
|  | do |  | 1 | 1.1 | 0.23 | 0.15 | 0.03795
|  | Y-direction |  | 2 | 5.22 | 0.23 | 0.15 | 0.36018
|  | do |  | 2 | 3 | 0.23 | 0.15 | 0.207
|  | do |  | 1 | 2 | 0.23 | 0.15 | 0.069
|  | do |  | 2 | 5.22 | 0.23 | 0.15 | 0.36018
|  | do |  | 1 | 5.89 | 0.23 | 0.15 | 0.2032
|  | do |  | 2 | 2.01 | 0.23 | 0.15 | 0.13869
|  | do |  | 1 | 2.15 | 0.23 | 0.15 | 0.074175
|  | duct |  | 4 | 2.55 | 0.23 | 0.15 | 0.3519
Half brick wall and lintel
|  | X-direction |  | 1 | 6.49 | 0.12 | 0.15 | 0.11682
|  | do |  | 1 | 6.2 | 0.12 | 0.15 | 0.1116
|  | do |  | 2 | 1.5 | 0.12 | 0.15 | 0.054
|  | Y-direction |  | 2 | 2.52 | 0.12 | 0.15 | 0.09072
|  | do |  | 1 | 1.05 | 0.12 | 0.15 | 0.0189
basement floor Roof beams
|  | All round |  | 1 | 61.84 | 0.3 | 0.43 | 7.9774
Inner beams
|  | Horizontal |  | 2 | 13.22 | 0.3 | 0.43 | 3.4108
|  | Extra beams |  | 1 | 6.2 | 0.3 | 0.43 | 0.7998
|  | Toilets |  | 2 | 6.12 | 0.23 | 0.28 | 0.78826
|  | Y-direction |  | 1 | 17.7 | 0.3 | 0.43 | 2.2833
|  | do |  | 2 | 5.7 | 0.3 | 0.43 | 1.4706
|  | do cabin |  | 1 | 3.35 | 0.23 | 0.28 | 0.21574
|  | duct beam |  | 4 | 2.55 | 0.23 | 0.28 | 0.65688
|  | Stair landing beams |  | 1 | 3.53 | 0.23 | 0.3 | 0.24357
|  | do |  | 1 | 3.07 | 0.23 | 0.28 | 0.19771
Sunshades
|  | Front side |  | 1 | 11.52 | 0.77 | 0.1 | 0.88704
|  | Rear side |  | 1 | 11.52 | 0.77 | 0.1 | 0.88704
basement floor roof slabs
|  | Right portion |  | 1 | 13.52 | 18 | 0.17 | 41.3712
|  | deduct stair rom |  | -1 | 3.07 | 4.23 | 0.17 | -2.2076
|  | Stair slab |  | 1 | 8.9 | 1.5 | 0.15 | 2.0025
|  | Steps | 0.5 | 25 | 1.5 | 0.3 | 0.15 | 0.84375
|  | Landing slab |  | 1 | 3.53 | 1.83 | 0.12 | 0.77519
|  | Counter slab to toilet |  | 1 | 0.9 | 4.7 | 0.07 | 0.2961
Ground floor
|  | column |  | 16 | 0.3 | 0.55 | 3.15 | 8.316
|  | Do carshed |  | 2 | 0.3 | 0.55 | 3.15 | 1.0395
Lintels
X-direction
|  | Left portion |  | 4 | 6.49 | 0.23 | 0.15 | 0.89562
|  | do |  | 1 | 3.47 | 0.23 | 0.15 | 0.11972
|  | Right portion |  | 2 | 6.2 | 0.23 | 0.15 | 0.4278
|  | do |  | 1 | 5.9 | 0.23 | 0.15 | 0.20355
|  | do |  | 1 | 2.97 | 0.23 | 0.15 | 0.10247
|  | do |  | 1 | 1.1 | 0.23 | 0.15 | 0.03795
|  | Y-direction |  | 3 | 5.22 | 0.23 | 0.15 | 0.54027
|  | do |  | 3 | 5.17 | 0.23 | 0.15 | 0.5351
|  | do |  | 4 | 5.22 | 0.23 | 0.15 | 0.72036
|  | do |  | 2 | 1.5 | 0.23 | 0.15 | 0.1035
|  | do |  | 1 | 2.15 | 0.23 | 0.15 | 0.074175
|  | duct |  | 4 | 2.55 | 0.23 | 0.15 | 0.3519
Half brick wall and lintel
|  | Toilets |  | 2 | 2.52 | 0.12 | 0.15 | 0.09072
|  | do |  | 2 | 1.5 | 0.12 | 0.15 | 0.054
|  | Cabin |  | 1 | 3.37 | 0.12 | 0.15 | 0.06066
|  | do |  | 1 | 1.2 | 0.12 | 0.15 | 0.0216
|  | duct |  | 1 | 1.05 | 0.12 | 0.15 | 0.0189
Ground floor Roof beams
|  | All round |  | 1 | 61.84 | 0.3 | 0.43 | 7.9774
Inner beams
|  | Horizontal |  | 2 | 13.22 | 0.3 | 0.43 | 3.4108
|  | Extra beams |  | 1 | 6.2 | 0.3 | 0.43 | 0.7998
|  | Toilets |  | 2 | 6.12 | 0.23 | 0.28 | 0.78826
|  | Y-direction |  | 1 | 17.7 | 0.3 | 0.43 | 2.2833
|  | do |  | 2 | 5.7 | 0.3 | 0.43 | 1.4706
|  | do cabin |  | 1 | 3.35 | 0.23 | 0.28 | 0.21574
|  | duct beam |  | 4 | 2.55 | 0.23 | 0.28 | 0.65688
|  | Stair landing beams |  | 1 | 3.53 | 0.23 | 0.3 | 0.24357
|  | do |  | 1 | 3.07 | 0.23 | 0.28 | 0.19771
|  | Car porch |  | 2 | 4.5 | 0.3 | 0.45 | 1.215
|  | do |  | 1 | 5.77 | 0.3 | 0.45 | 0.77895
Sunshades
|  | Front side |  | 1 | 11.52 | 0.77 | 0.1 | 0.88704
|  | Rear side |  | 1 | 11.52 | 0.77 | 0.1 | 0.88704
|  | Right side |  | 1 | 2.4 | 0.6 | 0.1 | 0.144
|  | do |  | 1 | 3 | 0.6 | 0.1 | 0.18
Ground floor roof slabs
|  | Right portion |  | 1 | 13.52 | 18 | 0.17 | 41.3712
|  | deduct stair rom |  | -1 | 3.07 | 4.23 | 0.17 | -2.2076
|  | Stair slab |  | 1 | 8.25 | 1.5 | 0.15 | 1.8562
|  | Steps | 0.5 | 23 | 1.5 | 0.3 | 0.15 | 0.77625
|  | Landing slab |  | 1 | 3.53 | 1.83 | 0.12 | 0.77519
|  | Car porch slab |  | 1 | 4.5 | 6.37 | 0.17 | 4.8731
|  | Counter slab to toilet |  | 1 | 0.9 | 4.7 | 0.07 | 0.2961
First floor
|  | column |  | 16 | 0.3 | 0.55 | 3.15 | 8.316
Lintels
X-direction
|  | Left portion |  | 2 | 6.49 | 0.23 | 0.15 | 0.44781
|  | Right portion |  | 2 | 6.2 | 0.23 | 0.15 | 0.4278
|  | do |  | 1 | 2.97 | 0.23 | 0.15 | 0.10247
|  | do |  | 1 | 1.1 | 0.23 | 0.15 | 0.03795
|  | Y-direction |  | 3 | 5.22 | 0.23 | 0.15 | 0.54027
|  | do |  | 3 | 5.17 | 0.23 | 0.15 | 0.5351
|  | do |  | 4 | 5.22 | 0.23 | 0.15 | 0.72036
|  | duct |  | 4 | 2.55 | 0.23 | 0.15 | 0.3519
Half brick wall and lintel
|  | Front of library |  | 1 | 6.27 | 0.12 | 0.15 | 0.11286
|  | duct |  | 1 | 1.05 | 0.12 | 0.15 | 0.0189
First floor Roof beams
|  | All round |  | 1 | 61.84 | 0.3 | 0.43 | 7.9774
Inner beams
|  | Horizontal |  | 2 | 13.22 | 0.3 | 0.43 | 3.4108
|  | Extra beams |  | 1 | 6.2 | 0.3 | 0.43 | 0.7998
|  | Y-direction |  | 1 | 17.7 | 0.3 | 0.43 | 2.2833
|  | do |  | 1 | 5.7 | 0.3 | 0.43 | 0.7353
|  | duct beam |  | 4 | 2.55 | 0.23 | 0.28 | 0.65688
|  | Stair landing beams |  | 1 | 3.53 | 0.23 | 0.3 | 0.24357
|  | do |  | 1 | 3.07 | 0.23 | 0.28 | 0.19771
Sunshades
|  | Front side |  | 1 | 11.52 | 0.77 | 0.1 | 0.88704
|  | Rear side |  | 1 | 11.52 | 0.77 | 0.1 | 0.88704
|  | Right side |  | 1 | 2.4 | 0.6 | 0.1 | 0.144
|  | do |  | 1 | 3 | 0.6 | 0.1 | 0.18
First floor roof slabs
|  | Right portion |  | 1 | 13.52 | 18 | 0.17 | 41.3712
|  | deduct stair rom |  | -1 | 3.07 | 4.23 | 0.17 | -2.2076
|  | Stair slab |  | 1 | 8.25 | 1.5 | 0.15 | 1.8562
|  | Steps | 0.5 | 23 | 1.5 | 0.3 | 0.15 | 0.77625
|  | Landing slab |  | 1 | 3.53 | 1.83 | 0.12 | 0.77519
Terrace floor
|  | Column |  | 4 | 0.3 | 0.55 | 2.7 | 1.782
|  | Stair room Lintels all round |  | 2 | 5.22 | 0.23 | 0.15 | 0.36018
|  | do |  | 1 | 2.92 | 0.23 | 0.15 | 0.10074
|  | Beam all round |  | 1 | 16.28 | 0.23 | 0.3 | 1.1233
|  | sunshade |  | 2 | 2.92 | 0.6 | 0.1 | 0.3504
|  | slab |  | 1 | 3.6 | 6.42 | 0.15 | 3.4668
Over Head Tank
|  | Columns |  | 4 | 0.3 | 0.55 | 3.15 | 2.079
|  | Beams |  | 3 | 3.3 | 0.3 | 0.43 | 1.2771
|  |  |  | 2 | 3 | 0.3 | 0.43 | 0.774
|  | Bottom slab |  | 1 | 3.3 | 3 | 0.18 | 1.782
|  | Side walls allround |  | 1 | 11.8 | 0.15 | 1.65 | 2.9205
|  | Inside Wall |  | 1 | 3.3 | 0.15 | 1.65 | 0.81675
|  | Top slab |  | 1 | 3.5 | 3.2 | 0.15 | 1.68
|  | Total | [5 empty] | 283.562
|  | Say | [5 empty] | 290 | m3
13 | 5.35 | Add for using extra cement in the items of design mix over and above the specified cement content therein |  |  | 593 | 0.5 | ql/m3 | 296.5 | ql
14 | 5.9 | Centering and shuttering including strutting, propping etc. and removal of form for :
a | 5.9.1 | Foundations, footings, bases of columns, etc. for mass concrete.
|  | For Pile cap |  | 19 | 6 |  | 1.2 | 136.8
|  | Foundation of retaining wall -Eastern side |  | 2 | 20 |  | 0.4 | 16
|  | ends |  | 2 | 3 |  | 0.4 | 2.4
|  | Do Southern side |  | 2 | 10 |  | 0.4 | 8
|  | For foundation of Columns at Southern side of work shop |  | 12 | 8.8 |  | 0.8 | 84.48
|  | Columns at Eastern side building |  | 10 | 9.4 |  | 0.9 | 84.6
|  | PCC |  | 1 | 8.8 |  | 0.1 | 0.88
|  | Total | [5 empty] | 333.16
|  | Say | [5 empty] | 340 | m2
b | 5.9.2 | Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc.
|  | Retaining wall up to plinth level |  | 2 | 30 |  | 1.2 | 72
|  | Retaining wall basement floor |  | 2 | 30 |  | 3.45 | 207
|  | Ends |  | 2 | 0.4 |  | 4.65 | 3.72
Septic tank side wall
|  | Out side |  | 1 | 8 |  | 2.25 | 18
|  | Inside |  | 1 | 6.8 |  | 2.1 | 14.28
|  | Baffle wall |  | 1 | 1.1 |  | 0.95 | 1.045
Over Head Tank
|  | Side walls allround |  | 2 | 11.8 |  | 1.65 | 38.94
|  | Inside Wall |  | 2 | 3.3 |  | 1.65 | 10.89
|  | Total | [5 empty] | 365.875
|  | Say | [5 empty] | 370 | m2
c | 5.9.3 | Suspended floors, roofs, landings, balconies and access platform.
Basement floor
|  | Right portion |  | 1 | 13.52 | 18 |  | 243.36
|  | deduct stair rom |  | -1 | 3.07 | 4.23 |  | -12.9861
|  | Landing slab |  | 1 | 3.53 | 1.83 |  | 6.4599
|  | Counter slab to toilet |  | 1 | 0.9 | 4.7 |  | 4.23
|  | Grade slab |  | 1 | 13.52 | 18 |  | 243.36
|  | do Work shop |  | 1 | 41.55 | 5 |  | 207.75
Ground floor
|  | Right portion |  | 1 | 13.52 | 18 |  | 243.36
|  | deduct stair rom |  | -1 | 3.07 | 4.23 |  | -12.9861
|  | Landing slab |  | 1 | 3.53 | 1.83 |  | 6.4599
|  | Car porch slab |  | 1 | 4.5 | 6.37 |  | 28.665
|  | Counter slab to toilet |  | 1 | 0.9 | 4.7 |  | 4.23
First floor
|  | Right portion |  | 1 | 13.52 | 18 |  | 243.36
|  | deduct stair rom |  | -1 | 3.07 | 4.23 |  | -12.9861
|  | Landing slab |  | 1 | 3.53 | 1.83 |  | 6.4599
Terrace floor
|  | slab |  | 1 | 3.6 | 6.42 |  | 23.112
|  | Septic tank slab |  | 1 | 2.3 | 1.1 |  | 2.53
|  | Edge |  | 1 | 8 |  | 0.1 | 0.8
Over Head Tank
|  | Bottom slab |  | 1 | 3.3 | 3 | 0.18 | 1.782
|  | Top slab |  | 1 | 3.5 | 3.2 | 0.15 | 1.68
|  | Total | [5 empty] | 1228.6404
|  | Say | [5 empty] | 1235 | m2
d | 5.9.5 | Lintels, beams, plinth beams, girders, bressumers and cantilevers.
Basement floor
Plinth beams
|  | Y-direction |  | 2 | 18 |  | 1.2 | 43.2
|  | left of stair |  | 1 | 5.7 |  | 1.2 | 6.84
|  | Middle of toilets |  | 1 | 5.7 |  | 1.2 | 6.84
|  | X-direction left portion |  | 4 | 6.42 |  | 1.2 | 30.816
|  | do right portion |  | 4 | 6.2 |  | 1.2 | 29.76
|  | Extra beams | [5 empty] | 0
|  | Front of utility |  | 1 | 6.42 |  | 0.9 | 5.778
|  | Front of cafeteria |  | 1 | 6.2 |  | 0.9 | 5.58
|  | Toilets |  | 2 | 6.12 |  | 0.9 | 11.016
|  | do |  | 2 | 4.25 |  | 0.9 | 7.65
|  | do |  | 2 | 1.5 |  | 0.9 | 2.7
Lintels
X-direction
|  | Left portion |  | 5 | 6.49 |  | 0.3 | 9.735
|  | do |  | 1 | 3.47 |  | 0.3 | 1.041
|  | Right portion |  | 1 | 6.2 |  | 0.3 | 1.86
|  | do |  | 1 | 5.9 |  | 0.3 | 1.77
|  | do |  | 1 | 2.97 |  | 0.3 | 0.891
|  | do |  | 1 | 1.1 |  | 0.3 | 0.33
|  | Y-direction |  | 2 | 5.22 |  | 0.3 | 3.132
|  | do |  | 2 | 3 |  | 0.3 | 1.8
|  | do |  | 1 | 2 |  | 0.3 | 0.6
|  | do |  | 2 | 5.22 |  | 0.3 | 3.132
|  | do |  | 1 | 5.89 |  | 0.3 | 1.767
|  | do |  | 2 | 2.01 |  | 0.3 | 1.206
|  | do |  | 1 | 2.15 |  | 0.3 | 0.645
|  | duct |  | 4 | 2.55 |  | 0.3 | 3.06
|  | Half brick wall and lintel |  |  |  |  | 0.3 | 0
|  | X-direction |  | 1 | 6.49 |  | 0.3 | 1.947
|  | do |  | 1 | 6.2 |  | 0.3 | 1.86
|  | do |  | 2 | 1.5 |  | 0.3 | 0.9
|  | Y-direction |  | 2 | 2.52 |  | 0.3 | 1.512
|  | do |  | 1 | 1.05 |  | 0.3 | 0.315
basement floor Roof beams
|  | All round |  | 1 | 61.84 |  | 1.16 | 71.7344
Inner beams
|  | Horizontal |  | 2 | 13.22 |  | 1.16 | 30.6704
|  | Extra beams |  | 1 | 6.2 |  | 1.16 | 7.192
|  | Toilets |  | 2 | 6.12 |  | 0.79 | 9.6696
|  | Y-direction |  | 1 | 17.7 |  | 1.16 | 20.532
|  | do |  | 2 | 5.7 |  | 1.16 | 13.224
|  | do cabin |  | 1 | 3.35 |  | 0.79 | 2.6465
|  | duct beam |  | 4 | 2.55 |  | 0.79 | 8.058
|  | Stair landing beams |  | 1 | 3.53 |  | 0.83 | 2.9299
|  | do |  | 1 | 3.07 |  | 0.79 | 2.4253
Ground floor
Lintels
X-direction
|  | Left portion |  | 4 | 6.49 |  | 0.3 | 7.788
|  | do |  | 1 | 3.47 |  | 0.3 | 1.041
|  | Right portion |  | 2 | 6.2 |  | 0.3 | 3.72
|  | do |  | 1 | 5.9 |  | 0.3 | 1.77
|  | do |  | 1 | 2.97 |  | 0.3 | 0.891
|  | do |  | 1 | 1.1 |  | 0.3 | 0.33
|  | Y-direction |  | 3 | 5.22 |  | 0.3 | 4.698
|  | do |  | 3 | 5.17 |  | 0.3 | 4.653
|  | do |  | 4 | 5.22 |  | 0.3 | 6.264
|  | do |  | 2 | 1.5 |  | 0.3 | 0.9
|  | do |  | 1 | 2.15 |  | 0.3 | 0.645
|  | duct |  | 4 | 2.55 |  | 0.3 | 3.06
|  | Half brick wall and lintel |  |  |  |  | 0.3 | 0
|  | Toilets |  | 2 | 2.52 |  | 0.3 | 1.512
|  | do |  | 2 | 1.5 |  | 0.3 | 0.9
|  | Cabin |  | 1 | 3.37 |  | 0.3 | 1.011
|  | do |  | 1 | 1.2 |  | 0.3 | 0.36
|  | duct |  | 1 | 1.05 |  | 0.3 | 0.315
Ground floor Roof beams
|  | All round |  | 1 | 61.84 |  | 1.16 | 71.7344
Inner beams
|  | Horizontal |  | 2 | 13.22 |  | 1.16 | 30.6704
|  | Extra beams |  | 1 | 6.2 |  | 1.16 | 7.192
|  | Toilets |  | 2 | 6.12 |  | 0.79 | 9.6696
|  | Y-direction |  | 1 | 17.7 |  | 1.16 | 20.532
|  | do |  | 2 | 5.7 |  | 1.16 | 13.224
|  | do cabin |  | 1 | 3.35 |  | 0.79 | 2.6465
|  | duct beam |  | 4 | 2.55 |  | 0.79 | 8.058
|  | Stair landing beams |  | 1 | 3.53 |  | 0.83 | 2.9299
|  | do |  | 1 | 3.07 |  | 0.79 | 2.4253
|  | Car porch |  | 2 | 4.5 |  | 1.2 | 10.8
|  | do |  | 1 | 5.77 |  | 1.2 | 6.924
First floor
Lintels
X-direction
|  | Left portion |  | 2 | 6.49 |  | 0.3 | 3.894
|  | Right portion |  | 2 | 6.2 |  | 0.3 | 3.72
|  | do |  | 1 | 2.97 |  | 0.3 | 0.891
|  | do |  | 1 | 1.1 |  | 0.3 | 0.33
|  | Y-direction |  | 3 | 5.22 |  | 0.3 | 4.698
|  | do |  | 3 | 5.17 |  | 0.3 | 4.653
|  | do |  | 4 | 5.22 |  | 0.3 | 6.264
|  | duct |  | 4 | 2.55 |  | 0.3 | 3.06
|  | Half brick wall and lintel |  |  |  |  | 0.3
|  | Front of library |  | 1 | 6.27 |  | 0.3 | 1.881
|  | duct |  | 1 | 1.05 |  | 0.3 | 0.315
First floor Roof beams
|  | All round |  | 1 | 61.84 |  | 1.16 | 71.7344
Inner beams
|  | Horizontal |  | 2 | 13.22 |  | 1.16 | 30.6704
|  | Extra beams |  | 1 | 6.2 |  | 1.16 | 7.192
|  | Y-direction |  | 1 | 17.7 |  | 1.16 | 20.532
|  | do |  | 1 | 5.7 |  | 1.16 | 6.612
|  | duct beam |  | 4 | 2.55 |  | 0.79 | 8.058
|  | Stair landing beams |  | 1 | 3.53 |  | 0.83 | 2.9299
|  | do |  | 1 | 3.07 |  | 0.79 | 2.4253
Terrace floor
|  | Stair room Lintels all round |  | 2 | 5.22 |  | 0.3 | 3.132
|  | do |  | 1 | 2.92 |  | 0.3 | 0.876
|  | Beam all round |  | 1 | 16.28 |  | 0.83 | 13.5124
Over Head Tank
|  | Beams | 2 | 3 | 3.3 |  | 0.43 | 4.257
|  |  | 2 | 3 | 3 |  | 0.3 | 2.7
|  |  | 2 | 2 | 3 |  | 0.43 | 2.58
|  |  | 2 | 2 | 3 |  | 0.3 | 1.8
|  | Total | [5 empty] | 792.1466
|  | Say | [5 empty] | 795 | m2
e | 5.9.6 | Columns, Pillars, Piers, Abutments, Posts and Struts.
Basement floor
|  | column |  | 12 | 1.7 |  | 3.45 | 70.38
Ground floor
|  | column |  | 16 | 1.7 |  | 3.15 | 85.68
|  | Do carshed |  | 2 | 1.7 |  | 3.15 | 10.71
First floor
|  | column |  | 16 | 1.7 |  | 3.15 | 85.68
Terrace floor
|  | Column |  | 4 | 1.7 |  | 2.7 | 18.36
Over Head Tank
|  | Columns | 2 | 4 | 0.3 |  | 3.15 | 3.78
|  |  | 2 | 4 | 0.55 |  | 3.15 | 6.93
|  | Total | [5 empty] | 281.52
|  | Say | [5 empty] | 285 | m2
f | 5.9.7 | Stairs, (excluding landings) except spiral-staircases.
Basement floor
|  | Stair slab |  | 1 | 8.9 | 1.5 |  | 13.35
|  | Edge |  | 1 | 8.9 | 0.3 |  | 2.67
|  | Steps |  | 25 | 1.5 | 0.15 |  | 5.625
Ground floor
|  | Stair slab |  | 1 | 8.25 | 1.5 |  | 12.375
|  | Edge |  | 1 | 8.25 | 0.3 |  | 2.475
|  | Steps |  | 23 | 1.5 | 0.15 |  | 5.175
First floor
|  | Stair slab |  | 1 | 8.25 | 1.5 |  | 12.375
|  | Edge |  | 1 | 8.25 | 0.3 |  | 2.475
|  | Steps |  | 23 | 1.5 | 0.15 |  | 5.175
|  | Total | [5 empty] | 61.695
|  | Say | [5 empty] | 62 | m2
g | 5.9.16.1 | Edges of slabs and breaks in floors and walls.Under 20 cm wide
Basement floor
|  | Right portion |  | 1 | 63.04 |  |  | 63.04
|  | edge of stair room opening |  | 1 | 14.6 |  |  | 14.6
|  | Landing slab |  | 1 | 10.72 |  |  | 10.72
|  | Counter slab to toilet |  | 1 | 11.2 |  |  | 11.2
|  | Grade slab |  | 1 | 63.04 |  |  | 63.04
|  | do Work shop |  | 1 | 93.1 |  |  | 93.1
Ground floor
|  | Right portion |  | 1 | 63.04 |  |  | 63.04
|  | edge of stair room opening |  | 1 | 14.6 |  |  | 14.6
|  | Landing slab |  | 1 | 10.72 |  |  | 10.72
|  | Car porch slab |  | 1 | 21.74 |  |  | 21.74
|  | Counter slab to toilet |  | 1 | 11.2 |  |  | 11.2
First floor
|  | Right portion |  | 1 | 63.04 |  |  | 63.04
|  | edge of stair room opening |  | 1 | 14.6 |  |  | 14.6
|  | Landing slab |  | 1 | 10.72 |  |  | 10.72
Terrace floor
|  | slab |  | 1 | 20.04 |  |  | 20.04
|  | Overhead Tank - Bottom Slab |  | 1 | 12.6 |  |  | 12.6 |  |  | 12.6
|  | Overhead Tank - Top Slab |  | 1 | 12.6 |  |  | 12.6
|  | Total | [5 empty] | 510.6
|  | Say | [5 empty] | 515 | m
h | 5.9.19 | Weather shade, Chajjas, corbels etc., including edges.
Basement floor
Sunshades
|  | Front side |  | 1 | 11.52 | 0.87 |  | 10.0224
|  | Rear side |  | 1 | 11.52 | 0.87 |  | 10.0224
Ground floor
Sunshades
|  | Front side |  | 1 | 11.52 | 0.87 |  | 10.0224
|  | Rear side |  | 1 | 11.52 | 0.87 |  | 10.0224
|  | Right side |  | 1 | 2.4 | 0.7 |  | 1.68
|  | do |  | 1 | 3 | 0.7 |  | 2.1
First floor
Sunshades
|  | Front side |  | 1 | 11.52 | 0.87 |  | 10.0224
|  | Rear side |  | 1 | 11.52 | 0.87 |  | 10.0224
|  | Right side |  | 1 | 2.4 | 0.7 |  | 1.68
|  | do |  | 1 | 3 | 0.7 |  | 2.1
Terrace floor
|  | sunshade |  | 2 | 2.92 | 0.7 |  | 4.088
|  | Total | [5 empty] | 71.7824
|  | Say | [5 empty] | 75 | m2
15 | 5.11.1 | Extra for additional height in centering, shuttering where ever required with adequate bracing, propping etc. including cost of de-shuttering and decentering at all levels, over a height of 3.5 m, for every additional height of 1 metre or part thereof (Plan area to be measured) Suspended floors, roofs, landing, beams and balconies (Plan area to be measured).
|  | Basement floor |  | 1 | 243 |  |  | 243
|  | Ground floor |  | 1 | 243 |  |  | 243
|  | First floor |  | 1 | 243 |  |  | 243
|  | Total | [5 empty] | 729
|  | Say | [5 empty] | 730 | m2
16 | 5.22.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete Thermo-Mechanically Treated bars.
Qty of concrete of piles
|  | 700 mm piles | 0.785 | 1 | 240 | 0.7 | 0.7 | 92.316
|  | Total | [5 empty] | 92.316
|  | Say | [5 empty] | 83 | m3
|  | Qty of Steel for pile |  |  | 83 | 100 | kg/m3 | 8300
|  | Qty of steel for RCC items |  |  | 593 | 130 | kg/m3 | 77090
|  | Total qty of reinforcement | [5 empty] | 85390 | kg
17 | 7.1.1 | Random rubble masonry with hard stone in foundation and plinth including levelling up with cement concrete 1:6:12 (1 cement : 6 coarse sand : 12 graded stone aggregate 20mm nominal size) upto plinth level with :Cement mortar 1:6 (1 cement : 6 coarse sand).
Foundation
|  | For rubble masonry foundation to the sides of work shop- Northern side |  | 1 | 15.5 | 0.6 | 0.6 | 5.58
|  | Do Southern side |  | 1 | 23.9 | 0.6 | 0.6 | 8.604
|  | Do Western side |  | 1 | 18.75 | 0.6 | 0.6 | 6.75
|  | Machine centre and store sides |  | 1 | 27 | 0.6 | 0.6 | 9.72
|  | Cross wall |  | 2 | 4.38 | 0.6 | 0.6 | 3.1536
|  | Retaining wall at Southern side |  | 1 | 60 | 0.6 | 0.6 | 21.6 |  | 21.6
Basement
|  | For rubble masonry foundation to the sides of work shop- Northern side |  | 1 | 41.9 | 0.45 | 0.6 | 11.313
|  | Do Southern side |  | 1 | 41.9 | 0.45 | 0.6 | 11.313
|  | Do Western side |  | 1 | 18.75 | 0.45 | 0.6 | 5.0625
|  | Machine centre and store sides |  | 1 | 27 | 0.45 | 0.6 | 7.29
|  | Cross wall |  | 2 | 4.38 | 0.45 | 0.6 | 2.3652
|  | Retaining wall at Southern side |  | 1 | 60 | 0.55 | 1.2 | 39.6
|  | Total | [5 empty] | 132.3513
|  | Say | [5 empty] | 135 | m3
18 | 6.4.2 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in : Cement mortar 1:6 (1 cement : 6 coarse sand)
Basement floor
X-direction
|  | Left portion |  | 4 | 6.49 | 0.23 | 3.45 | 20.5993
|  | do |  | 1 | 6.49 | 0.23 | 3.6 | 5.3737
|  | do |  | 1 | 3.47 | 0.23 | 3.6 | 2.8732
|  | Right portion |  | 1 | 6.2 | 0.23 | 3.45 | 4.9197
|  | do |  | 1 | 5.9 | 0.23 | 3.45 | 4.6817
|  | do |  | 1 | 2.97 | 0.23 | 3.45 | 2.3567
|  | do |  | 1 | 1.1 | 0.23 | 3.6 | 0.9108
|  | Y-direction |  | 2 | 5.22 | 0.23 | 3.45 | 8.2841
|  | do |  | 2 | 3 | 0.23 | 3.45 | 4.761
|  | do |  | 1 | 2 | 0.23 | 3.45 | 1.587
|  | do |  | 2 | 5.22 | 0.23 | 3.45 | 8.2841
|  | do |  | 1 | 5.89 | 0.23 | 3.45 | 4.6737
|  | do |  | 2 | 2.01 | 0.23 | 3.6 | 3.3286
|  | do |  | 1 | 2.15 | 0.23 | 3.6 | 1.7802
|  | duct |  | 4 | 2.55 | 0.23 | 3.6 | 8.4456
Deduction
|  | Door Do |  | -3 | 1.8 | 0.23 | 2.25 | -2.7945
|  | D3 |  | -4 | 1 | 0.23 | 2.25 | -2.07
|  | FD |  | -1 | 0.9 | 0.23 | 1.5 | -0.3105
|  | DD |  | -4 | 0.9 | 0.23 | 1.5 | -1.242
|  | RS-1 |  | -1 | 4 | 0.23 | 2.4 | -2.208
|  | Window W |  | -3 | 1.8 | 0.23 | 1.5 | -1.863
Ground floor
X-direction
|  | Left portion |  | 3 | 6.49 | 0.23 | 3.15 | 14.106
|  | do |  | 1 | 6.49 | 0.23 | 3.3 | 4.9259
|  | do |  | 1 | 3.47 | 0.23 | 3.3 | 2.6337
|  | Right portion |  | 1 | 6.2 | 0.23 | 3.15 | 4.4919
|  | do |  | 1 | 5.9 | 0.23 | 3.15 | 4.2746
|  | do |  | 1 | 6.27 | 0.23 | 3.3 | 4.7589
|  | do |  | 1 | 2.97 | 0.23 | 3.15 | 2.1518
|  | do |  | 1 | 1.1 | 0.23 | 3.3 | 0.8349
|  | Y-direction |  | 3 | 5.22 | 0.23 | 3.15 | 11.3457
|  | do |  | 3 | 5.17 | 0.23 | 3.15 | 11.237
|  | do |  | 4 | 5.22 | 0.23 | 3.15 | 15.1276
|  | do |  | 2 | 1.5 | 0.23 | 3.3 | 2.277
|  | do |  | 1 | 2.15 | 0.23 | 3.3 | 1.6319
|  | duct |  | 4 | 2.55 | 0.23 | 3.3 | 7.7418
|  | Parapet of car porch |  | 1 | 14.91 | 0.23 | 0.9 | 3.0864
Deduction
|  | Opening |  | -1 | 2 | 0.23 | 2.25 | -1.035
|  | Front of cabin |  | -1 | 4.95 | 0.23 | 2.25 | -2.5616
|  | Door SD |  | -1 | 2 | 0.23 | 2.4 | -1.104
|  | TD |  | -1 | 1.8 | 0.23 | 2.25 | -0.9315
|  | TD2 |  | -2 | 1 | 0.23 | 2.25 | -1.035
|  | D3 |  | -4 | 1 | 0.23 | 2.25 | -2.07
|  | FD |  | -1 | 0.9 | 0.23 | 1.5 | -0.3105
|  | DD |  | -4 | 0.9 | 0.23 | 1.5 | -1.242
|  | Window W |  | -6 | 1.8 | 0.23 | 1.5 | -3.726
First floor
X-direction
|  | Left portion |  | 2 | 6.49 | 0.23 | 3.15 | 9.404
|  | Right portion |  | 2 | 6.2 | 0.23 | 3.15 | 8.9838
|  | do |  | 1 | 2.97 | 0.23 | 3.15 | 2.1518
|  | do |  | 1 | 1.1 | 0.23 | 3.3 | 0.8349
|  | Y-direction |  | 3 | 5.22 | 0.23 | 3.15 | 11.3457
|  | do |  | 3 | 5.17 | 0.23 | 3.15 | 11.237
|  | do |  | 4 | 5.22 | 0.23 | 3.15 | 15.1276
|  | duct |  | 4 | 2.55 | 0.23 | 3.3 | 7.7418
|  | Parapet |  | 1 | 52.33 | 0.23 | 1.2 | 14.4431
Deduction
|  | Door D0 |  | -2 | 1.8 | 0.23 | 2.25 | -1.863
|  | D3 |  | -1 | 1 | 0.23 | 2.25 | -0.5175
|  | FD |  | -1 | 0.9 | 0.23 | 1.5 | -0.3105
|  | DD |  | -4 | 0.9 | 0.23 | 1.5 | -1.242
|  | Window W |  | -8 | 1.8 | 0.23 | 1.5 | -4.968
Terrace floor
|  | All round |  | 1 | 19.1 | 0.23 | 2.7 | 11.8611
|  | Parapet |  | 1 | 19.1 | 0.23 | 0.8 | 3.5144
|  | deduction Door D3 |  | -1 | 1 | 0.23 | 2.25 | -0.5175
|  | Total | [5 empty] | 236.2072
|  | Say | [5 empty] | 240 | m3
19 | 6.12.2 | Half brick masonry with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundations and plinth in.cement mortar 1:4 (1 cement : 4 coarse sand)
Basement floor
|  | X-direction |  | 1 | 6.49 |  | 3.88 | 25.1812
|  | do |  | 1 | 6.2 |  | 3.88 | 24.056
|  | do |  | 2 | 1.5 |  | 3.88 | 11.64
|  | Y-direction |  | 2 | 2.52 |  | 3.88 | 19.5552
|  | do |  | 1 | 1.05 |  | 3.88 | 4.074
Deduction
|  | Door Do |  | -3 | 1.8 |  | 2.25 | -12.15
|  | D6 |  | -4 | 0.8 |  | 2.1 | -6.72
Ground floor
|  | Toilets |  | 2 | 2.52 |  | 3.58 | 18.0432
|  | do |  | 2 | 1.5 |  | 3.58 | 10.74
|  | Cabin |  | 1 | 3.37 |  | 3.58 | 12.0646
|  | do |  | 1 | 1.2 |  | 3.58 | 4.296
|  | duct |  | 1 | 1.05 |  | 3.58 | 3.759
First floor
|  | Front of library |  | 1 | 6.27 | 0.12 | 3.58 | 22.4466
|  | duct |  | 1 | 1.05 | 0.12 | 3.58 | 3.759
|  | Total | [5 empty] | 140.7448 | m2
|  | Say | [5 empty] | 142 | m2
20 | 6.15 | Extra for providing and placing in position 2 Nos. 6mm dia. M.S. bars at every third course of half brick masonry.
|  | Qty same as above | [5 empty] | 142 | m2
21 | 4.7.2 | Providing and fixing up to floor five level precast cement concrete solid block including hoisting and setting in position with cement mortar 1:3 (1 cement : 3 coarse sand), cost of required centering, shuttering complete :1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20mm nominal size).
|  | Long sides |  | 2 | 41.9 | 0.2 | 3 | 50.28
|  | short side |  | 1 | 17.5 | 0.2 | 3 | 10.5
|  | Machine centre & store |  | 1 | 26.92 | 0.2 | 3 | 16.152
|  | Cross |  | 2 | 4.38 | 0.2 | 3 | 5.256
|  | Total | [5 empty] | 82.188
|  | Say | [5 empty] | 83 | m3
22 | 8.2.2.2 | Providing and fixing 18mm thick gang saw cut mirror polished premoulded and prepolished) machine cut for kitchen platforms, flooring, vanity counters, window sills , facias and similar locations of required size of approved shade, colour and texture laid over 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) with joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels. Granite of any colour and shade: Area of slab over 0.50 sqm.(Lowest retails price not less than Rs. 2000/m2)
Basement floor
|  | Stair step tread |  | 25 | 1.53 | 0.33 |  | 12.6225
|  | riser |  | 27 | 1.5 | 0.15 |  | 6.075
|  | Landing |  | 1 | 3.4 | 1.75 |  | 5.95
|  | Counter slab |  | 1 | 0.65 | 2.4 |  | 1.56
|  | do |  | 1 | 0.65 | 2.4 |  | 1.56
Ground floor
|  | Stair step tread |  | 23 | 1.53 | 0.33 |  | 11.6127
|  | riser |  | 25 | 1.5 | 0.15 |  | 5.625
|  | Landing |  | 1 | 3.4 | 1.75 |  | 5.95
|  | Counter slab |  | 1 | 0.65 | 2.4 |  | 1.56
|  | do |  | 1 | 0.65 | 2.4 |  | 1.56
|  | Front side step tread |  | 2 | 6.3 | 0.33 |  | 4.158
|  | Riser |  | 3 | 6.3 | 0.15 |  | 2.835
|  | Platform |  | 1 | 6.3 | 1.2 |  | 7.56
First floor
|  | Stair step tread |  | 23 | 1.53 | 0.33 |  | 11.6127
|  | riser |  | 25 | 1.5 | 0.15 |  | 5.625
|  | Landing |  | 1 | 3.4 | 1.75 |  | 5.95
Terrace floor
|  | stair room |  | 1 | 3.4 | 1.8 |  | 6.12
|  | Total | [5 empty] | 97.9359
|  | Grand Total | [5 empty] | 100 | m2
23 | 8.5 | Extra for providing opening of required size & shape for wash basins/ kitchen sink in kitchen platform, vanity counters and similar location in marble/Granite/stone work including necessary holes for pillar taps etc. including moulding, rubbing and polishing of cut edges etc. complete.
For counter wash basin
|  | Ground floor |  | 4 |  |  |  | 4
|  | Total | [5 empty] | 4 | nos
24 | 9.48.2 | Providing and fixing M.S. grills of required pattern in frames of windows etc. with M.S. flats, square or round bars etc. including priming coat with approved steel primer all complete.Fixed to openings /wooden frames with rawl plugs screws etc.
|  | Window W |  | 17 | 1.8 |  | 1.5 | 45.9
|  | Ventilator V |  | 9 | 0.9 |  | 0.6 | 4.86
|  | Total | [5 empty] | 50.76 | m2
|  | Weight of grill 22 kg/m2 |  |  | 50.76 | 15 |  | 761.4
|  | Say | [5 empty] | 762 | kg
25 | 9.84 | Providing and fixing aluminium extruded section body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 36 kg to 80 kg and door width from 701 mm to 1000 mm) with double speed adjustment with necessary accessories and screws etc. complete.
|  | D0 | 2 | 6 |  |  |  | 12
|  | D3 | 1 | 10 |  |  |  | 10
|  | Total | [5 empty] | 22 | Nos
26 | 9.117.1 | Providing and fixing factory made UPVC door frame made of UPVC extruded sections having an overall dimension as below (tolerance ±1mm), with wall thickness 2.0 mm (± 0.2mm), corners of the door frame to be Jointed with galvanized brackets and stainless steel screws, joints mitred and Plastic welded. The hinge side vertical of the frames reinforced by galvanized M.S. tube of size 19 X 19mm and 1mm (± 0.1 mm) wall thickness and 3 nos. stainless steel hinges fixed to the frame complete as per manufacturers specification and direction of Engineer-in-charge: Extruded section profile size 48x40 mm.
|  | D6 |  | 8 | 5 |  |  | 40
|  | Total | [5 empty] | 40 | m
27 | 9.118.2 | 30 mm thick factory made Polyvinyl Chloride (PVC) door shutter made of styles and rails of a UPVC hollow section of size 60x30 mm and wall thickness 2 mm (± 0.2 mm), with inbuilt decorative moulding edging on one side. The styles and rails mitred and joint at the corners by means of M.S. galvanised/plastic brackets of size 75x220 mm having wall thickness 1.0 mm and stainless steel screws. The styles of the shutter reinforced by inserting galvanised M.S. tube of size 25x20 mm and 1 mm (± 0.1 mm) wall thickness.
The lock rail made up of 'H' section, a UPVC hollow section of size 100x30 mm and 2 mm (± 0.2 mm) wall thickness fixed to the shutter styles by means of plastic/ galvanised M.S. 'U' cleats. The shutter frame filled with a UPVC multi-chambered single panel of size not less than 620 mm, having over all thickness of 20 mm and 1 mm (± 0.1 mm) wall thickness . The panels filled vertically and tie bar at two places by inserting horizontally 6 mm galvanised M.S. rod and fastened with nuts and washers, complete as per manufacturer's specification and direction of Engineer-in-charge.
|  | D5 |  | 6 | 0.8 |  | 2.1 | 10.08
|  | Say | [5 empty] | 10.5 | m2
29 | 10.17 | Providing and fixing M.S. fan clamp type I or II of 16 mm dia M.S. bar bent to shape with hooked ends in R.C.C. slabs, beams during laying including painting the exposed portion of loop, all as per standard design complete.
|  | Basement floor |  | 30 |  |  |  | 30
|  | Ground floor |  | 7 |  |  |  | 7
|  | Terrace floor |  | 6 |  |  |  | 6
|  | Total | [5 empty] | 43
|  | Say | [5 empty] | 45 | nos
30 | 10.28 | Providing and fixing stainless steel ( Grade 304) railing made of Hollow tubes, channels, plates etc. including welding, grinding, buffing, polishing and making curvature (wherever required) and fitting the same with necessary stainless steel nuts and bolts complete i/c fixing the railing with necessary accessories & stainless steel dash fasteners , stainless steel bolts etc., of required size, on the top of the floor or the side of waist slab with suitable arrangement as per approval of Engineer-in-charge. ( for payment purpose only weight of stainless steel members shall be considered excluding fixing accessories such as nuts, bolts, fasteners etc.)
Hand rails of stair case
|  | Newel post 90mm dia. | 8 | 2 | 1 | 4.35 | kg/m | 69.6
|  | Basement floor Hand rails 50mm dia | 1 | 1 | 9 | 2.4 | kg/m | 21.6
|  | Balusters | 60 | 1 | 0.9 | 0.9 | kg/m | 48.6
|  | Horizontals | 2 | 1 | 9 | 0.9 | kg/m | 16.2
|  | Ground and first floor hand rails | 1 | 2 | 8.4 | 2.4 | kg/m | 40.32
|  | do | 1 | 1 | 1.6 | 2.4 | kg/m | 3.84
|  | Balusters | 55 | 2 | 0.9 | 0.9 | kg/m | 89.1
|  | do | 10 | 1 | 0.9 | 0.9 | kg/m | 8.1
|  | Horizontals | 2 | 2 | 8.4 | 0.9 | kg/m | 30.24
|  | do | 1 | 2 | 1.6 | 0.9 | kg/m | 2.88
|  | 100mm dia. Dom | 8 | 1 |  | 1.5 | kg/each | 12
|  | Total | [5 empty] | 342.48
|  | Say | [5 empty] | 350 | kg
31 | 11.36 | Providing and fixing Ist quality ceramic glazed wall tiles 300x450mm size conforming to IS : 15622 (thickness to be specified by the manufacturer ) of approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados over 12 mm thick bed of cement Mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm including pointing in white cement mixed with pigment of matching shade complete.(Lowest retail price not less than Rs. 400/m2)
Basement floor
|  | Closets | 2 | 4 | 1.5 |  | 2.1 | 25.2
|  | do | 2 | 4 | 1.2 |  | 2.1 | 20.16
|  | PH toilet | 2 | 1 | 2.01 |  | 2.1 | 8.442
|  | do | 2 | 1 | 1.5 |  | 2.1 | 6.3
|  | Gents toilet | 2 | 1 | 4.25 |  | 2.1 | 17.85
|  | do | 2 | 1 | 2.51 |  | 2.1 | 10.542
|  | Partitian | 2 | 2 | 0.7 |  | 1.3 | 3.64
|  | Ladies toilet | 2 | 1 | 4.25 |  | 2.1 | 17.85
|  | do | 2 | 1 | 1.51 |  | 2.1 | 6.342
Ground floor
|  | Closets | 2 | 4 | 1.5 |  | 2.1 | 25.2
|  | do | 2 | 4 | 1.2 |  | 2.1 | 20.16
|  | PH toilet | 2 | 1 | 2.01 |  | 2.1 | 8.442
|  | do | 2 | 1 | 1.5 |  | 2.1 | 6.3
|  | Gents toilet | 2 | 1 | 4.25 |  | 2.1 | 17.85
|  | do | 2 | 1 | 2.51 |  | 2.1 | 10.542
|  | Partitian | 2 | 2 | 0.7 |  | 1.3 | 3.64
|  | Ladies toilet | 2 | 1 | 4.25 |  | 2.1 | 17.85
|  | do | 2 | 1 | 1.51 |  | 2.1 | 6.342
|  | Near cabin | 2 | 1 | 1.2 |  | 2.1 | 5.04
|  | do | 2 | 1 | 1.8 |  | 2.1 | 7.56
Deduction
|  | D3 | 0.5 | -6 | 1.5 |  | 2.25 | -10.125
|  | D6 | 1 | -8 | 1.2 |  | 2.25 | -21.6
|  | Total | [5 empty] | 213.527 | m2
|  | Say | [5 empty] | 215 | m2
32 | 11.4 | Providing and laying rectified antiskid Ceramic floor tiles 300x300 mm or more (thickness to be specified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make in all colours, shades, except White, Ivory, Grey, Fume Red Brown, laid on 20 mm thick Cement Mortar 1:4 (1 Cement : 4 Coarse sand) including pointing the joints with white cement and matching pigments etc., complete (Lowest retail price not less than Rs. 500/m2) Make: NITKO, KAJARIA, ORIENT.
Basement floor
|  | Toilet |  | 4 | 1.5 | 1.2 |  | 7.2
|  | PH toilet |  | 1 | 2.01 | 1.5 |  | 3.015
|  | Ladies toilet |  | 1 | 1.5 | 4.25 |  | 6.375
|  | Gents toilet |  | 1 | 1.5 | 4.25 |  | 6.375
|  | do |  | 1 | 1 | 1.5 |  | 1.5
First floor
|  | Toilet |  | 4 | 1.5 | 1.2 |  | 7.2
|  | PH toilet |  | 1 | 2.01 | 1.5 |  | 3.015
|  | Ladies toilet |  | 1 | 1.5 | 4.25 |  | 6.375
|  | Gents toilet |  | 1 | 1.5 | 4.25 |  | 6.375
|  | do |  | 1 | 1 | 1.5 |  | 1.5
|  | Toilet near cabin |  | 1 | 1.2 | 1.8 |  | 2.16
|  | Door portion |  | 8 | 0.8 | 0.13 |  | 0.832
|  | do |  | 6 | 1 | 0.23 |  | 1.38
|  | Total | [5 empty] | 53.302
|  | Say | [5 empty] | 54 | m2
33 | 11.41.2 | Providing and laying vitrified floor tiles in different sizes (thickness to be specified by the manufacturer) with water absorption's less than 0.08% and conforming to IS : 15622 of approved make in all colours and shades, laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand) including grouting the joints with white cement and matching pigments etc., complete.Size of Tile 600x600 mm: (Lowest retail price not less than Rs. 900/m2)
Basement floor
|  | Electrical room |  | 1 | 6.49 | 5.6 |  | 36.344
|  | Utility room |  | 1 | 6.49 | 3.42 |  | 22.1958
|  | Cafeteria |  | 1 | 6.2 | 9.24 |  | 57.288
|  | Passage |  | 1 | 12.92 | 2 |  | 25.84
|  | Front portion of toilet |  | 1 | 6.5 | 1.48 |  | 9.62
|  | Store |  | 1 | 2.97 | 4.75 |  | 14.1075
|  | do |  | 1 | 1.88 | 1.2 |  | 2.256
|  | Stair room |  | 1 | 3 | 6.18 |  | 18.54
Ground floor
|  | Left hall |  | 1 | 6.49 | 11.35 |  | 73.6615
|  | Front portion of toilet |  | 1 | 6.49 | 1.48 |  | 9.6052
|  | Cabin |  | 1 | 4.95 | 3.6 |  | 17.82
|  | do |  | 1 | 1.2 | 1.45 |  | 1.74
|  | Passage |  | 1 | 6.5 | 2 |  | 13
|  | Reception |  | 1 | 6.57 | 5.77 |  | 37.9089
|  | Waiting area |  | 1 | 2.97 | 4.75 |  | 14.1075
|  | do |  | 1 | 1.88 | 1.2 |  | 2.256
|  | Stair room |  | 1 | 3 | 1.9 |  | 5.7
|  | First floor | [5 empty] | 0
|  | Fab lab |  | 1 | 6.49 | 17.54 |  | 113.8346
|  | Library and display room |  | 1 | 6.27 | 9.24 |  | 57.9348
|  | Testing area |  | 1 | 2.97 | 4.75 |  | 14.1075
|  | do |  | 1 | 1.88 | 1.2 |  | 2.256
|  | Passage |  | 1 | 6.27 | 2 |  | 12.54
|  | Stair room |  | 1 | 3 | 1.9 |  | 5.7
Door portion
|  | SD |  | 1 | 2 | 0.25 |  | 0.5
|  | TD |  | 1 | 1.8 | 0.25 |  | 0.45
|  | TD2 |  | 2 | 1 | 0.25 |  | 0.5
|  | D0 |  | 6 | 1.8 | 0.25 |  | 2.7
|  | D3 |  | 3 | 1 | 0.25 |  | 0.75
|  | Total | [5 empty] | 573.2633
|  | Say | [5 empty] | 580 | m2
34 | 11.46.2 | Providing and laying Vitrified tiles in different sizes (thickness to be specified by manufacturer) with water absorption less than 0.08 % and conforming to I.S. 15622, of approved make in all colours & shade in skirting, riser of steps, over 12 mm thick bed of cement mortar 1:3 (1 cement: 3 coarse sand), including grouting the joint with white cement & matching pigments etc. complete.Size of Tile 600x600 mm: (Lowest retail price not less than Rs. 900/m2) Make: NITKO, KAJARIA, ORIENT.
Basement floor
|  | Electrical room |  | 1 | 24.18 |  | 0.15 | 3.627
|  | Utility room |  | 1 | 19.82 |  | 0.15 | 2.973
|  | Cafeteria |  | 1 | 30.88 |  | 0.15 | 4.632
|  | Passage |  | 1 | 29.84 |  | 0.15 | 4.476
|  | Front portion of toilet |  | 1 | 15.96 |  | 0.15 | 2.394
|  | Store |  | 1 | 17.84 |  | 0.15 | 2.676
|  | Stair room |  | 1 | 15.36 |  | 0.15 | 2.304
|  | Ground floor |  |  |  |  | 0.15 | 0
|  | Left hall |  | 1 | 35.68 |  | 0.15 | 5.352
|  | Front portion of toilet |  | 1 | 15.96 |  | 0.15 | 2.394
|  | Cabin |  | 1 | 12.15 |  | 0.15 | 1.8225
|  | do |  | 1 | 5.3 |  | 0.15 | 0.795
|  | Passage |  | 2 | 6.5 |  | 0.15 | 1.95
|  | Reception |  | 2 | 6.57 |  | 0.15 | 1.971
|  | Waiting area |  | 1 | 17.84 |  | 0.15 | 2.676
|  | Stair room |  | 2 | 1.9 |  | 0.15 | 0.57
|  | First floor |  |  |  |  | 0.15 | 0
|  | Fab lab |  | 1 | 48.06 |  | 0.15 | 7.209
|  | Library and display room |  | 1 | 31.02 |  | 0.15 | 4.653
|  | Testing area |  | 1 | 17.84 |  | 0.15 | 2.676
|  | Passage |  | 1 | 6.27 |  | 0.15 | 0.9405
|  | do |  | 1 | 3.2 |  | 0.15 | 0.48
|  | Stair room |  | 2 | 1.9 |  | 0.15 | 0.57
|  | Total | [5 empty] | 57.141
|  | Say | [5 empty] | 58 | m2
| 16.75 | Providing and laying C.C. pavement of mix M-25 with ready mixed concrete from batching plant. The ready mixed concrete shall be laid and finished with screed board vibrator , vacuum dewatering process and finally finished by floating, brooming with wire brush etc. complete as per specifications and directions of Engineer-incharge. (The panel shuttering work shall be aid for separately).
(Note:- Cement content considered in this item is @ 330 kg/cum. Excess/ less cement used as per design mix is payable/ recoverable separately).
|  |  |  | 1 | 42 | 17.5 | 0.065 | 47.775
|  | TOTAL | [5 empty] | 47.775
|  | Say | [5 empty] | 50 | m3
| LMR | Groove cutting over VDF Flooring 5x25mm deep, clean the groove with air blower |  | 5 | 42 |  |  | 210
|  |  |  | 13 | 17.5 |  |  | 227.5
|  | Total | [5 empty] | 437.5
|  | Say | [5 empty] | 440 | RM
35 | 10.6.1 | Supplying and fixing rolling shutters of approved make, made of required size M.S. laths, interlocked together through their entire length and jointed together at the end by end locks, mounted on specially designed pipe shaft with brackets, side guides and arrangements for inside and outside locking with push and pull operation complete, including the cost of providing and fixing necessary 27.5 cm long wire springs manufactured from high tensile steel wire of adequate strength conforming to IS: 4454 – part 1 and M.S. top cover of required thickness for rolling shutters.80x1.25mm M.S. laths with 1.25 mm thick top cover.
|  | RS |  | 1 | 6 |  | 2.4 | 14.4
|  | RS1 |  | 1 | 4 |  | 2.4 | 9.6
|  | Total | [5 empty] | 24
|  | Say | [5 empty] | 24 | m2
36 | 10.7 | Providing and fixing ball bearing for rolling shutters.
|  | RS |  | 2 |  |  |  | 2
|  | RS1 |  | 2 |  |  |  | 2
|  | Total | [5 empty] | 4
|  | Say | [5 empty] | 4 | Nos
37 | 10.8.1 | Extra for providing mechanical device chain and crank operation for operating rolling shutters. Exceeding 10.00 sqm and upto 16.80 sqm in the area
|  | RS |  | 1 | 6 |  | 2.4 | 14.4
|  | Total | [5 empty] | 14.4
|  | Say | [5 empty] | 15 | m2
38 | 13.2.1 | 15 mm cement plaster of mix 1:4 (1 cement: 4 fine sand) for outside walls upto 10.0m height
|  | walls all around including parapet |  | 1 | 63 |  | 12.15 | 765.45
|  | Parapet inside |  | 1 | 62.34 |  | 1.45 | 90.393
|  | Terrace floor outside |  | 1 | 20.04 |  | 3.6 | 72.144
|  | Parapet inside |  | 1 | 19.12 |  | 1.05 | 20.076
|  | Wor shop Long sides |  | 2 | 41.9 |  | 3.2 | 268.16
|  | Short side |  | 1 | 18 |  | 3.2 | 57.6
|  | Parapet of parapet over car porch |  | 2 | 14.9 |  | 1.02 | 30.396
Deduction
|  | Window W | 0.5 | -17 | 1.8 |  | 1.5 | -22.95
|  | D0 | 0.5 | -2 | 1.8 |  | 2.25 | -4.05
|  | D3 | 0.5 | -1 | 1 |  | 2.25 | -1.125
|  | RS1 | 0.5 | -1 | 6 |  | 2.4 | -7.2
|  | RS1 | 0.5 | -1 | 4 |  | 2.4 | -4.8
|  | Total | [5 empty] | 1264.094
|  | Say | [5 empty] | 1270 | m2
39 | 13.22 | Extra for plastering exterior walls of height 10m to 13m
|  | walls all around including parapet |  | 1 | 63 |  | 2.15 | 135.45
|  | Parapet inside |  | 1 | 62.34 |  | 0.85 | 52.989
|  | Terrace floor outside |  | 1 | 20.04 |  | 0.85 | 17.034
|  | Total | [5 empty] | 205.473
|  | Say | [5 empty] | 210 | m2
40 | 13.22 +13.22 | Extra for plastering exterior walls of height 13m to 16m
|  | Parapet inside |  | 1 | 62.34 |  | 0.6 | 37.404
|  | Terrace floor outside |  | 1 | 20.04 |  | 2.75 | 55.11
|  | Parapet inside |  | 1 | 19.12 |  | 1.05 | 20.076
|  | Total | [5 empty] | 112.59
|  | Say | [5 empty] | 115 | m2
41 | 13.5.1 | 15 mm cement plaster on rough side of single or half brick wall of mix : 1:4 (1 cement: 4 coarse sand) inside walls
Basement floor
|  | Electrical room |  | 2 | 6.49 |  | 3.88 | 50.3624
|  | do |  | 2 | 5.59 |  | 3.88 | 43.3784
|  | Cafeteria |  | 2 | 6.2 |  | 3.88 | 48.112
|  | do |  | 2 | 9.24 |  | 3.88 | 71.7024
|  | Utility room |  | 2 | 6.49 |  | 3.88 | 50.3624
|  | do |  | 2 | 3.42 |  | 3.88 | 26.5392
|  | Passage |  | 2 | 12.92 |  | 3.88 | 100.2592
|  | do |  | 2 | 2 |  | 3.88 | 15.52
|  | Store |  | 2 | 2.97 |  | 3.88 | 23.0472
|  | do |  | 2 | 5.95 |  | 3.88 | 46.172
|  | stair room |  | 2 | 6.19 |  | 4.05 | 50.139
|  | Front porton of toilet |  | 2 | 6.49 |  | 3.88 | 50.3624
|  | do |  | 2 | 1.48 |  | 3.88 | 11.4848
|  | PH toilet |  | 2 | 2.01 |  | 3.88 | 15.5976
|  | do |  | 2 | 1.5 |  | 3.88 | 11.64
|  | WC |  | 8 | 1.5 |  | 3.88 | 46.56
|  | do |  | 8 | 1.2 |  | 3.88 | 37.248
|  | Gents toilet |  | 2 | 4.25 |  | 3.88 | 32.98
|  | do |  | 2 | 2.51 |  | 3.88 | 19.4776
|  | Ladies toilet |  | 2 | 4.25 |  | 3.88 | 32.98
|  | do |  | 2 | 1.51 |  | 3.88 | 11.7176
|  | Partition |  | 4 | 0.7 |  | 1.3 | 3.64
|  | Work shop long wall |  | 2 | 41.69 |  | 3 | 250.14
|  | short wall |  | 1 | 17.54 |  | 3 | 52.62
|  | Machine centre |  | 1 | 19.41 |  | 3 | 58.23
|  | Store |  | 1 | 20.41 |  | 3 | 61.23
|  | Outside |  | 1 | 31.42 |  | 3 | 94.26
Ground floor
|  | Conference room and work station |  | 2 | 6.49 |  | 3.58 | 46.4684
|  | do |  | 2 | 11.35 |  | 3.58 | 81.266
|  | Cabin |  | 2 | 4.95 |  | 3.58 | 35.442
|  | do |  | 2 | 3.37 |  | 3.58 | 24.1292
|  | Toilet |  | 2 | 1.2 |  | 3.58 | 8.592
|  | do |  | 2 | 1.8 |  | 3.58 | 12.888
|  | Front portion of toilet |  | 2 | 1.2 |  | 3.58 | 8.592
|  | do |  | 2 | 1.45 |  | 3.58 | 10.382
|  | Reception |  | 2 | 6.27 |  | 3.58 | 44.8932
|  | do |  | 2 | 7.75 |  | 3.58 | 55.49
|  | Stair room |  | 2 | 6.18 |  | 3.75 | 46.35
|  | Waiting area |  | 2 | 2.97 |  | 3.58 | 21.2652
|  | do |  | 2 | 5.95 |  | 3.58 | 42.602
|  | Front porton of toilet |  | 2 | 6.49 |  | 3.58 | 46.4684
|  | do |  | 2 | 1.48 |  | 3.58 | 10.5968
|  | PH toilet |  | 2 | 2.01 |  | 3.58 | 14.3916
|  | do |  | 2 | 1.5 |  | 3.58 | 10.74
|  | WC |  | 8 | 1.5 |  | 3.58 | 42.96
|  | do |  | 8 | 1.2 |  | 3.58 | 34.368
|  | Gents toilet |  | 2 | 4.25 |  | 3.58 | 30.43
|  | do |  | 2 | 2.51 |  | 3.58 | 17.9716
|  | Ladies toilet |  | 2 | 4.25 |  | 3.58 | 30.43
|  | do |  | 2 | 1.51 |  | 3.58 | 10.8116
|  | Partition |  | 4 | 0.7 |  | 1.3 | 3.64
First floor
|  | Fab Lab |  | 2 | 17.54 |  | 3.58 | 125.5864
|  | do |  | 2 | 6.49 |  | 3.58 | 46.4684
|  | Library & display room |  | 2 | 6.27 |  | 3.58 | 44.8932
|  | do |  | 2 | 9.24 |  | 3.58 | 66.1584
|  | Testing area |  | 2 | 2.97 |  | 3.58 | 21.2652
|  | do |  | 2 | 5.95 |  | 3.58 | 42.602
|  | Passage |  | 2 | 6.27 |  | 3.58 | 44.8932
|  | do |  | 2 | 2 |  | 3.58 | 14.32
|  | Stair room |  | 2 | 6.18 |  | 3.75 | 46.35
Terrace floor
|  | stair room |  | 2 | 5.95 |  | 2.7 | 32.13
|  | do |  | 2 | 3 |  | 2.7 | 16.2
|  | duct inside |  | 4 | 2.62 |  | 12.15 | 127.332
|  | Extra for solumn sides | [5 empty] | 60
Deduction
|  | SD | 0.5 | -1 | 2 |  | 2.4 | -2.4
|  | D0 | 0.5 | -2 | 1.8 |  | 2.25 | -4.05
|  | do |  | -4 | 1.8 |  | 2.25 | -16.2
|  | D3 |  | -9 | 1 |  | 2.25 | -20.25
|  | D6 |  | -8 | 0.8 |  | 2.1 | -13.44
|  | RS | 0.5 | -1 | 6 |  | 2.4 | -7.2
|  | RS1 | 0.5 | -1 | 4 |  | 2.4 | -4.8
|  | W | 0.5 | -17 | 1.8 |  | 1.5 | -22.95
|  | Total | [5 empty] | 2603.839
|  | Deduct dadoing area | [5 empty] | 213.527
|  | Less deduction | [5 empty] | 2390.312
|  | Say | [5 empty] | 2400 | m2
42 | 13.16.1 | 6 mm cement plaster of mix : 1:3 (1 cement: 3 fine sand) for under side of roof slab
Basement floor
|  | Electrical room |  | 1 | 6.49 | 5.59 |  | 36.2791
|  | Utility room |  | 1 | 6.49 | 3.42 |  | 22.1958
|  | Cafeteria |  | 1 | 6.2 | 9.24 |  | 57.288
|  | Passage |  | 1 | 12.92 | 2 |  | 25.84
|  | Front portion of toilet |  | 1 | 6.5 | 1.48 |  | 9.62
|  | Store |  | 1 | 2.97 | 4.75 |  | 14.1075
|  | do |  | 1 | 1.88 | 1.2 |  | 2.256
|  | Stair room |  | 1 | 3 | 1.9 |  | 5.7
|  | under side of stair slab |  | 1 | 8.9 | 1.5 |  | 13.35
|  | Under side of landing slab |  | 1 | 3 | 1.6 |  | 4.8
|  | Toilet |  | 4 | 1.5 | 1.2 |  | 7.2
|  | PH toilet |  | 1 | 2.01 | 1.5 |  | 3.015
|  | Ladies toilet |  | 1 | 1.5 | 4.25 |  | 6.375
|  | Gents toilet |  | 1 | 1.5 | 4.25 |  | 6.375
|  | do |  | 1 | 1 | 1.5 |  | 1.5
|  | sunshade |  | 2 | 11.52 | 0.77 |  | 17.7408
Ground floor
|  | Left hall |  | 1 | 6.49 | 11.35 |  | 73.6615
|  | Front portion of toilet |  | 1 | 6.49 | 1.48 |  | 9.6052
|  | Cabin |  | 1 | 4.95 | 3.6 |  | 17.82
|  | do |  | 1 | 1.2 | 1.45 |  | 1.74
|  | Passage |  | 1 | 6.5 | 2 |  | 13
|  | Reception |  | 1 | 6.57 | 5.77 |  | 37.9089
|  | Waiting area |  | 1 | 2.97 | 4.75 |  | 14.1075
|  | do |  | 1 | 1.88 | 1.2 |  | 2.256
|  | Stair room |  | 1 | 3 | 1.9 |  | 5.7
|  | under side of stair slab |  | 1 | 8.25 | 1.5 |  | 12.375
|  | Under side of landing slab |  | 1 | 3 | 1.6 |  | 4.8
|  | WC |  | 4 | 1.5 | 1.2 |  | 7.2
|  | PH toilet |  | 1 | 2.01 | 1.5 |  | 3.015
|  | Ladies toilet |  | 1 | 1.5 | 4.25 |  | 6.375
|  | Gents toilet |  | 1 | 1.5 | 4.25 |  | 6.375
|  | do |  | 1 | 1 | 1.5 |  | 1.5
|  | Toilet near cabin |  | 1 | 1.2 | 1.8 |  | 2.16
|  | Portico |  | 1 | 4.49 | 6.37 |  | 28.6013
|  | beams |  | 2 | 6.49 | 0.43 |  | 5.5814
|  | do |  | 4 | 6.27 | 0.43 |  | 10.7844
|  | sunshade |  | 2 | 11.52 | 0.77 |  | 17.7408
|  | First floor | [5 empty] | 0
|  | Fab lab |  | 1 | 6.49 | 17.54 |  | 113.8346
|  | Library and display room |  | 1 | 6.27 | 9.24 |  | 57.9348
|  | Testing area |  | 1 | 2.97 | 4.75 |  | 14.1075
|  | do |  | 1 | 1.88 | 1.2 |  | 2.256
|  | Passage |  | 1 | 6.27 | 2 |  | 12.54
|  | Stair room |  | 1 | 3 | 1.9 |  | 5.7
|  | under side of stair slab |  | 1 | 8.25 | 1.5 |  | 12.375
|  | Under side of landing slab |  | 1 | 3 | 1.6 |  | 4.8
|  | beams |  | 4 | 6.49 | 0.43 |  | 11.1628
|  | do |  | 4 | 6.27 | 0.43 |  | 10.7844
|  | Sides of beams | [5 empty] | 10
|  | sunshade |  | 2 | 11.52 | 0.77 |  | 17.7408
Terrace floor
|  | Stair room |  | 1 | 3 | 5.96 |  | 17.88
|  | Total | [5 empty] | 807.0651
|  | Say | [5 empty] | 808 | m2
43 | 13.9.1 + 13.21 | Cement plaster 1:3 (1 cement: 3 coarse sand) finished with a floating coat of neat cement.12 mm cement plaster including providing and mixing water proofing material in cement plaster work in proportion recommended by the manufacturers. to the top surface of slab & sunshade
|  | Top of slab |  | 1 | 13 | 17.54 |  | 228.02
|  | Top of sunshade |  | 6 | 11.52 | 0.77 |  | 53.2224
|  | Top of portico |  | 1 | 4.49 | 6.37 |  | 28.6013
Septic tank
|  | Bottom |  | 1 | 2.3 | 1.1 |  | 2.53
|  | Side walls |  | 1 | 6.8 |  | 2.1 | 14.28
|  | Out side |  | 1 | 8 |  | 2.35 | 18.8
|  | Baffle wall |  | 1 | 1.1 |  | 1 | 1.1
Over Head Tank
|  | Bottom |  | 1 | 3.3 | 3 |  | 9.9
|  | Side wall (inside) |  | 1 | 3.3 |  | 1.65 | 5.445
|  | Out side |  | 1 | 11.8 |  | 1.85 | 21.83
|  | Total | [5 empty] | 383.7287
|  | Say | [5 empty] | 385 | m2
44 | 13.8 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete.
|  | Quantity same as inside wall plastering & under slab plastering | [5 empty] | 3208
Deduct
|  | Work shop long wall |  | -2 | 41.69 |  | 3 | -250.14
|  | short wall |  | -1 | 17.54 |  | 3 | -52.62
|  | Machine centre |  | -1 | 19.41 |  | 3 | -58.23
|  | Store |  | -1 | 20.41 |  | 3 | -61.23
|  | do |  | -1 | 31.42 |  | 3 | -94.26
|  | Total | [5 empty] | 2691.52
|  | Say | [5 empty] | 2695 | m2
45 | 13.43.1 | Applying one coat of water thinnable cement primer of approved brand and manufacture on wall surface :
|  | Quantity same as inside wall plastering & under slab plastering | [5 empty] | 2695 | m2
46 | 13.47.1 | Finishing walls with Premium Acrylic Smooth exterior paint with Silicone additives of required shade New work (Two or more coats applied @ 1.43 ltr/ 10 sqm. over and including priming coat of exterior primer applied @ 2.20 kg/ 10 sqm).
|  | Quantity same as outside plastering | [5 empty] | 1270 | m2
47 | 13.60.1 | Wall painting with acrylic emulsion paint of approved brand and manufacture to give an even shade: Two or more coats on new work. Inside of walls
|  | Quantity same as inside wall plastering & under slab plastering | [5 empty] | 3208 | m2
48 | 13.61.1 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade :Two or more coats on new work.
|  | Qty same as grill area | [5 empty] | 50.76
|  | RS | 2.2 | 1 | 6 |  | 2.4 | 31.68
|  | RS1 | 2.2 | 1 | 4 |  | 2.4 | 21.12
|  | Total | [5 empty] | 103.56
|  | Say | [5 empty] | 115 | m2
49 | 16.68 | Providing and laying 60mm thick factory made cement concrete interlocking paver block of M -30 grade made by block making machine with strong vibratory compaction, of approved size, design & shape, laid in required colour and pattern over and including 50mm thick compacted bed of fine sand, filling the joints with fine sand etc. all complete as per the direction of Engineer-in-charge.
|  | Front portion |  | 1 | 20 | 7 |  | 140 | m2
50 | 16.69 | Providing and laying at or near ground level factory made kerb stone of M-25 grade cement concrete in position to the required line, level and curvature, jointed with cement mortar 1:3 (1 cement: 3 coarse sand) including making joints with or without grooves (thickness of joints except at sharp curve shall not to more than 5mm), including making drainage opening wherever required complete etc. as per direction of Engineer-in-charge (length of finished kerb edging shall be measured for payment). (Precast C.C. kerb stone shall be approved by Engineer-in-charge).
|  | Around interlocking |  | 1 | 34 | 0.15 | 0.35 | 1.785
|  | Say | [5 empty] | 2 | m3
51 | 11.20.3 | Chequerred precast cement concrete tiles 22 mm thick in footpath & courtyard, jointed with neat cement slurry mixed with pigment to match the shade of tiles including rubbing and cleaning etc. complete, on 20 mm thick bed of cement mortar 1:4 (1 cement: 4 coarse sand). Dark shade using ordinary cement.
|  | Porch |  | 1 | 4.5 | 6.4 |  | 28.8
|  | Total | [5 empty] | 28.8
|  | Say | [5 empty] | 30 | m2
52 | 21.1.1.2 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) : For fixed portion Powder coated aluminium (minimum thickness of powder coating 50 micron)
|  | Door D0 |  | 6 | 1.8 |  | 2.25 | 24.3
|  | Door D3 |  | 10 | 1 |  | 2.25 | 22.5
|  | Window W |  | 17 | 1.8 |  | 1.5 | 45.9
|  | Ventilators V |  | 9 | 0.9 |  | 0.6 | 4.86
|  | Duct door DD |  | 12 | 0.9 |  | 1.5 | 16.2
|  | Fire door FD |  | 3 | 0.9 |  | 1.5 | 4.05
|  | Total | [5 empty] | 117.81
|  | Weight of frame 12kg/m2 |  | 12 | 117.81 | kg/m2 |  | 1413.72
|  | Say | [5 empty] | 1415 | kg
53 | 21.1.2.2 | For shutters of doors, windows & ventilators including providing and fixing hinges/ pivots and making provision for fixing of fittings wherever required including the cost of EPDM rubber / neoprene gasket required (Fittings shall be paid for separately). Powder coated aluminium (minimum thickness of powder coating 50 micron)
|  | For fixed glass |  | 1 | 5.17 |  | 2.4 | 12.408
|  | Door D0 |  | 6 | 1.8 |  | 2.25 | 24.3
|  | Door D3 |  | 10 | 1 |  | 2.25 | 22.5
|  | Window W |  | 17 | 1.8 |  | 1.5 | 45.9
|  | Ventilators V |  | 9 | 0.9 |  | 0.6 | 4.86
|  | Duct door DD |  | 12 | 0.9 |  | 1.5 | 16.2
|  | Fire door FD |  | 3 | 0.9 |  | 1.5 | 4.05
|  | Total | [5 empty] | 130.218
|  | Weight of frame 8kg/m2 |  | 8 | 130.218 | kg/m2 |  | 1041.744
|  | Say | [5 empty] | 1045 | kg
54 | 21.2.2 | Providing and fixing 12mm thick prelaminated particle board flat pressed three layer or graded wood particle board conforming to IS: 12823 Grade l Type ll, in panelling fixed in aluminum doors, windows shutters and partition frames with C.P. brass / stainless steel screws etc. complete as per architectural drawings and directions of engineer-in-charge. Pre-laminated particle board with decorative lamination on both sides.
|  | Door D0 |  | 6 | 1.8 |  | 1.13 | 12.204
|  | Door D3 |  | 10 | 1 |  | 1.13 | 11.3
|  | Duct door DD |  | 12 | 0.9 |  | 0.75 | 8.1
|  | Fire door FD |  | 3 | 0.9 |  | 0.75 | 2.025
|  | Total | [5 empty] | 33.629
|  | Say | [5 empty] | 35 | m2
55 | 21.3 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 5.50 mm thickness
(a) | 21.3.2 | With float glass panes of 5.50 mm thickness
|  | Door D0 |  | 6 | 1.8 |  | 1.13 | 12.204
|  | Door D3 |  | 10 | 1 |  | 1.13 | 11.3
|  | Window W |  | 17 | 1.8 |  | 1.5 | 45.9
|  | Ventilators V |  | 9 | 0.9 |  | 0.6 | 4.86
|  | Duct door DD |  | 12 | 0.9 |  | 0.75 | 8.1
|  | Fire door FD |  | 3 | 0.9 |  | 0.75 | 2.025
|  | Total | [5 empty] | 84.389
|  | Say | [5 empty] | 85 | m2
(b) | 21.3.2 | With float glass panes of 8 mm thickness
|  | For fixed glass |  | 1 | 5.17 |  | 2.4 | 12.408
|  | Say | [5 empty] | 13 | m2
56 | 21.4.2 | Providing and fixing double action hydraulic floor spring of approved brand and manufacture conforming to IS : 6315, having brand logo embossed on the body / plate with double spring mechanism and door weight upto 125 kg., for doors, including cost of cutting floors , embedding in floors as required and making good the same matching to the existing floor finishing and cover plates with brass pivot and single piece M.S. sheet outer box with slide plate etc. complete as per the direction of Engineer-in-charge. With brass cover plate minimum 1.25 mm thickness.
|  | MD |  | 2 |  |  |  | 2 | nos
57 | 21.11 | Providing and fixing stainless steel (SS 304 grade) adjustable friction windows stays of approved quality with necessary stainless steel screws etc. to the side hung windows as per direction of Engineer-in-charge complete.
a | 21.11.1 | 205 X 19 mm
|  | Ventilators | 2 | 9 |  |  |  | 18 | nos
b | 21.11.2 | 255 X 19 mm
|  | Window W | 3 | 17 |  |  |  | 51
|  | Total | [5 empty] | 51
|  | Say | [5 empty] | 51 | nos
58 | 21.12.2 | Providing and fixing aluminium tubular handle bar 32 mm outer dia, 3.0 mm thick & 2100 mm long with SS screws etc .complete as per direction of Engineer-in-Charge.Powder coated minimum thickness 50 micron aluminium tubular handle bar
|  | D0 | 4 | 6 |  |  |  | 24
|  | D3 | 2 | 10 |  |  |  | 20
|  | Total | [5 empty] | 44
|  | Say | [5 empty] | 44 | nos
59 | 21.13 | Providing and fixing 100mm brass locks (best make of approved quality) for aluminium doors including necessary cutting and making good etc. complete
|  | D0 |  | 6 |  |  |  | 6
|  | D3 |  | 10 |  |  |  | 10
|  | Total | [5 empty] | 16
|  | Say | [5 empty] | 16 | nos
60 | 21.15.2 | Providing and fixing aluminium casement windows fastener of required length for aluminium windows with necessary screws etc. complete. Powder coated minimum thickness 50 micron aluminium
|  | Window W | 3 | 17 |  |  |  | 51
|  | Ventilators | 2 | 9 |  |  |  | 18
|  | Total | [5 empty] | 69
|  | Say | [5 empty] | 69 | nos
61 | 21.18 | Providing and fixing 12 mm thick frameless toughened glass door door shutter of approved brand and manufacture, including providing and fixing top & bottom pivot & spring type fixing arrangement and making necessary holes etc. for fixing required door fittings, all complete as per direction of Engineer-in-charge (Door handle, lock and stopper etc.to be paid separately).
|  | TD |  | 1 | 1.8 |  | 2.25 | 4.05
|  | TD2 |  | 2 | 1 |  | 2.25 | 4.5
|  | Total | [5 empty] | 8.55
|  | Say | [5 empty] | 9 | m2
62 | LMR | Propviding and fixing 12mm thick toughened glass automatic sliding door (DORMA make) of size 200x240cm size (two side sliding ) including Aluminum Channel DC Brush less Motor Micro Computer 130 ~ 300 Volt wide AC Input SMPS Power Supply 2 nos Microwave Sensors All Accessories 2 nos GLASS holding clamps Electronic Lock Switch and all other accessories etc complete. The sensor consists of backup battery support for ensuring normal running of automatic sliding electro-mechanical lock for ensuring safe usage of automatic sliding door system, radar and sensors are highly sensitive which provides safety from accidental squeezing and striking, 32-bit control chip for ensuring higher processing speeds, .
|  | Door SD |  | 1 |  |  |  | 1
|  | Say | [5 empty] | 1 | No
63 | 21.18 | Providing and fixing 12 mm thick frameless toughened glass partition of approved brand and manufacture, including providing and fixing top & bottom etc.all complete as per direction of Engineer-in-charge
|  | Reception |  | 1 | 6.57 |  | 2.7 | 17.739
|  | Sides of conference hall |  | 1 | 5.77 |  | 2.7 | 15.579
|  | do |  | 1 | 3.25 |  | 2.7 | 8.775
|  | Cabin |  | 1 | 4.95 |  | 2.7 | 13.365
|  | deduction door TD2 |  | -2 | 1 |  | 2.25 | -4.5
|  | deduction door TD |  | -1 | 1.8 |  | 2.25 | -4.05
|  | Total | [5 empty] | 46.908
|  | Say | [5 empty] | 48 | m2
64 | 22.5 | Providing and laying water proofing treatment in sunken portion of WCs, bathroom etc., by applying cement slurry mixed with water proofing cement compound consisting of applying : a) First layer of slurry of cement @ 0.488 kg/sqm mixed with water proofing cement compound @ 0.253 kg/sqm. This layer will be allowed to air cure for 4 hours. b) Second layer of slurry of cement @ 0.242 kg/sqm mixed with water proofing cement compound @ 0.126 kg/sqm. This layer will be allowed to air cure for 4 hours followed with water curing for 48 hours. The rate includes preparation of surface, treatment and sealing of all joints, corners, junctions of pipes and masonry with polymer mixed slurry
First floor
|  | Toilet |  | 4 | 1.5 | 1.2 |  | 7.2
|  | PH toilet |  | 1 | 2.01 | 1.5 |  | 3.015
|  | Ladies toilet |  | 1 | 1.5 | 4.25 |  | 6.375
|  | Gents toilet |  | 1 | 1.5 | 4.25 |  | 6.375
|  | do |  | 1 | 1 | 1.5 |  | 1.5
|  | Toilet near cabin |  | 1 | 1.2 | 1.8 |  | 2.16
|  | Door portion |  | 8 | 0.8 | 0.13 |  | 0.832
|  | do |  | 6 | 1 | 0.23 |  | 1.38
|  | Total | [5 empty] | 28.837
|  | Say | [5 empty] | 29 | m2
65 | 12.52.2 | Providing and fixing tiled false ceiling of approved materials of size 595x595 mm in true horizontal level suspended on inter locking metal grid of hot dipped galvanized steel sections ( galvanized @ 120 gsm/sqm, both side inclusive) consisting of main "T" runner with suitably spaced joints to get required length and of size 24x38mm made from 0.30mm thick (minimum) sheet, spaced at 1200mm center to center and cross "T" of size 24x25mm made of 0.30mm thick (minimum) sheet, 1200mm long spaced between main "T" at 600mm center to center to form a grid of 1200x600 mm and secondary cross "T" of length 600mm and size 24x25mm made of 0.30 mm thick (minimum) sheet to be interlocked at middle of the 1200x600mm panel to form grids of 600x600mm
and wall angle of size 24x24x0.3 mm and laying false ceiling tiles of approved texture in the grid including, wherever, required, cutting/making, opening for services like diffusers, grills, light fittings, fixtures, smoke detectors etc. Main "T" runners to be suspended from ceiling using GI slotted cleats of size 27 x 37 x 25 x1.6 x mm fixed to ceiling with 12.5 mm dia and 50 mm long dash fasteners, 4mm GI adjustable rods with galvanised butterfly level clips of size 85 x 30 x 0.8 mm spaced at 1200mm center to center along main T, bottom exposed width of 24 mm of all T-sections shall be pre-painted with polyester paint, all complete at all heights as per specifications drawings and as directed by Engineer-in-charge.
GI Metal Ceiling Lay in perforated Tegular edge global white color tiles of size 595x595 mm and 0.5mm thick with 8mm drop; made of GI sheet having galvanizing of 100 gms/sqm (both sides inclusive) and 20% perforation area with 1.8mm dia holes and having NRC (Noise Reduction Coefficient ) of 0.5, electro statically polyester powder coated of thickness 60 microns (minimum), including factory painted after bending and perforation, and backed with a black Glass fiber acoustical fleece.
Ground floor
|  | Cabin |  | 1 | 6.27 | 3.37 |  | 21.1299
|  | Passage |  | 1 | 6.5 | 2 |  | 13
|  | do |  | 1 | 1.88 | 1.43 |  | 2.6884
|  | Toilet |  | 4 | 1.5 | 1.2 |  | 7.2
|  | PH toilet |  | 1 | 2.01 | 1.5 |  | 3.015
|  | Ladies toilet |  | 1 | 1.5 | 4.25 |  | 6.375
|  | Gents toilet |  | 1 | 1.5 | 4.25 |  | 6.375
|  | do |  | 1 | 1 | 1.5 |  | 1.5
|  | Front portion of toilet |  | 1 | 6.49 | 1.48 |  | 9.6052
First floor
|  | Passage |  | 1 | 6.27 | 2 |  | 12.54
|  | Library and display room |  | 1 | 6.27 | 9.24 |  | 57.9348
|  | Fab lab |  | 1 | 6.5 | 17.54 |  | 114.01
|  | Testing Area |  | 1 | 2.97 | 6 |  | 17.82
|  | Total | [5 empty] | 273.1933
|  | Say | [5 empty] | 300 | m2
| 12.45.1 | 12.5 mm thick tapered edge gypsum plain board conforming to IS: 2095- Part I
Basement Floor
|  | Machine Centre |  | 1 | 15 | 4.38 |  | 65.7
|  | Store |  | 1 | 11.65 | 4.38 |  | 51.027
Ground floor
|  | Conference hall and workstation |  | 1 | 6.49 | 11.35 |  | 73.6615
|  | Reception |  | 1 | 6.2 | 5.7 |  | 35.34
|  | Waiting area |  | 1 | 2.97 | 4.75 |  | 14.1075
|  | do |  | 1 | 1.88 | 1.43 |  | 2.6884
|  | TOTAL | [5 empty] | 242.5244
|  | Say | [5 empty] | 250 | m2
66 | 26.1 | Providing and supplying aluminium extruded tubular and other aluminium sections as per the architectural drawings and approved shop drawings , the aluminium quality as per grade 6063 T5 or T6 as per BS 1474,including super durable powder coating of 60-80 microns conforming to AAMA 2604 of required colour and shade as approved by the Engineer-in-Charge. ( The item includes cost of material such as cleats, sleeves, screws etc. necessary for fabrication of extruded aluminium frame work. Nothing extra shall be paid on this account).
|  | Front side centre portion |  | 1 | 6.37 |  | 3.4 | 21.658
|  | Front Left and right |  | 2 | 4.82 |  | 7.75 | 74.71
|  | Total | [5 empty] | 96.368
|  | Say | [5 empty] | 100 | m2
|  | Weight of alumminium section @ 6.5kg/m2 | 6.5 |  | 100 |  |  | 650
|  | Say | [5 empty] | 650 | kg
67 | 26.2 | Designing, fabricating, testing, protection, installing and fixing in position semi (grid) unitized system of structural glazing (with open joints) for linear as well as curvilinear portions of the building for all heights and all levels, including:
a) Structural analysis & design and preparation of shop drawings for the specified design loads conforming to IS 875 part III (the system must passed the proof test at 1.5 times design wind pressure without any failure), including functional design of the aluminum sections for fixing glazing panels of various thicknesses, aluminium cleats, sleeves and splice plates etc. gaskets, screws, toggles, nuts, bolts, clamps etc., structural and weather silicone sealants, flashings, fire stop (barrier)-cum-smoke seals, microwave cured EPDM gaskets for water tightness, pressure equalisation & drainage and protection against fire hazard including
b) Fabricating and supplying serrated M.S. hot dip galvanised/Aluminium alloy of 6005 T5 brackets of required sizes, sections and profiles etc. to accommodate 3 Dimentional movement for achieving perfect verticality and fixing structural glazing system rigidly to the RCC/ masonry/structural steel framework of building structure using stainless steel anchor fasteners/ bolts, nylon seperator to prevent bimetallic contacts with nuts and washers etc. of stainless steel grade 316, of the required capacity and in required numbers.
c) Providing and filling, two part pump filled, structural silicone sealant and one part weather silicone sealant compatible with the structural silicone sealant of required bite size in a clean and controlled factory / work shop environment , including double sided spacer tape, setting blocks and backer rod, all of approved grade, brand and manufacture, as per the approved sealant design, within and all around the perimeter for holding glass.
d) Providing and fixing in position flashings of solid aluminium sheet 1 mm thick and of sizes, shapes and profiles, as required as per the site conditions, to seal the gap between the building structure and all its interfaces with curtain glazing to make it watertight.
e) Making provision for drainage of moisture/ water that enters the curtain glazing system to make it watertight, by incorporating principles of pressure equalization, providing suitable gutter profiles at bottom (if required), making necessary holes of required sizes and of required numbers etc. complete. This item includes cost of all inputs of designing, labour for fabricating and installation of aluminium grid, installation of glazed units, T&P, scaffolding and other incidental charges including wastages etc., enabling temporary structures and services, cranes or cradles etc. as described above and as specified.
The item includes the cost of getting all the structural and functional design including shop drawings checked by a structural designer, dully approved by Engineer-in-charge. The item also includes the cost of all mock ups at site, cost of all samples of the individual components for testing in an approved laboratory, field tests on the assembled working structural glazing as specified, cleaning and protection till the handing over of the building for occupation. In the end, the Contractor shall provide a water tight structural glazing having all the performance characteristics etc. all complete as required, as per the Architectural drawings, as per item description, as specified as per the approved shop drawings and as directed by the Engineerin-, Charge.
Note:- 1. The cost of providing extruded aluminium frames, shadow boxes, extruded aluminium section capping for fixing in the grooves of the curtain glazing and vermin proof stainless steel wire mesh shall be paid for separately under relevant items under this subhead However, for the purpose of payment, only the actual area of structural glazing (including width of grooves ) on the external face shall be measured in sqm. up to two decimal places.
Note:-2. The following performance test are to be conducted on structural glazing system if area of structural glazing exceeds 2500 Sqm from the certified laboratories accreditated by NABL(National Accreditation Board for Testing and Calibration Laboratories), Department of Science & Technologies, India. Cost of testing is payable separately. The NIT approving authority will decide the necessity of testing on the basis of cost of the work, cost of the test and importance of the work. Performance Testing of Structural glazing system Tests to be conducted in the NBL Certified laboratories
1. Performance Laboratory Test for Air Leakage Test (-50pa to – 300pa) & (+50pa to +300pa) as per ASTM E-283-04 testing method for a range of testing limit 1 to 200 mVhr”
2. Static Water Penetration Test. (50pa to 1500pa) as per ASTME- 331-09 testing method for a range up to 2000 ml.”
3. Dynamic Water Penetration (50pa to 1500pa) as per AAMA 501.01- 05 testing method for a range upto 2000 ml”
4. Structural Performance Deflection and deformation by static air pressure test (1.5 times desing wind pressure without any failure) as per ASTME-330-10 testing method for a range upto 50 mm”
5. Seismic Movement Test (upto 30 mm) as per AAMA 501.4-09 testing method for Qualitative test” Tests to be conducted on site
6. Onsite Test for Water Leakage for a pressure range 50 kpa to 240 kpa (35psi) upto 2000ml”
|  | Area same as above | [5 empty] | 100 | m2
68 | 26.3 | Providing, assembling and supplying vision glass panels (IGUs) comprising of hermetically-sealed 6-12- 6 mm insulated glass (double glazed) vision panel units of size and shape as required and specified, comprising of an outer heat strengthened float glass 6mm thick, of approved colour and shade with reflective soft coating on surface # 2 of approved colour and shade, an inner Heat strengthned clear float glass 6mm thick, spacer tube 12mm wide, dessicants, including primary seal and secondary seal (structural silicone sealant) etc. all complete for the required performances, as per the Architecturaldrawings, as per the approved shop drawings, as specified and asdirected by the Engineer-in-Charge.
The IGUs shall be assembled inthe factory/ workshop of the glass processor. (Payment for fixing ofIGU Panels in the curtain glazing is included in cost of item No.26.2)For payment, only the actual area of glass on face # 1 of the glasspanels (excluding the areas of the grooves and weather siliconesealant) provided and fixed in position, shall be measured in sqm.
(i) Coloured tinted float glass 6mm thick substrate with reflective soft coating on face # 2, + 12mm Airgap + 6mm Heat Strengthened clear Glass of approved make having properties as visible Light transmittance (VLT) of 25 to 35 %, Light reflection internal 10 to 15%, light reflection external 10 to 20 %, shading coefficient (0.25- 0.28) and U value of 3.0 to 3.3 W/m2 degree K etc. The properties of performance glass shall be decided by technical sanctioning authority as per the site requirement.
|  | Area same as above | [5 empty] | 100 | m2
69 | LMR | Extra for openable side / top hung vision glass panels (IGUs) including providing and supplying at site all accessories and hardwares for the openable panels as specified and of the approved make such as heavy duty stainless steel friction hinges, min 4 -point cremone locking sets with stainless steel plates, handles, buffers etc. including necessary stainless steel screws/ fasteners, nuts, bolts, washers etc. all complete as per the Architectural drawings, as per the approved shop drawings, as specified and as directed by the Engineerin- Charge.
|  | 1/10 area of above item |  | 0.1 | 100 |  |  | 10 | m2