TENDER DOCUMENT

FOR

PROVIDING LAMINAR FLOW AIR CONDITIONER AT THQH THODUPUZHA

PART-III

PRICE BID

TENDER NO. HLL / ID / 13 / 38

May 2013

HLL LIFECARE LIMITED.

INFRASTRUCTURE DEVELOPMENT DIVISION

Contents    			  	                                   Page No.

- Commercial Conditions		                              03

- Special Conditions                      	                              06

3              Bill of Quantities                                                              08

  - COMMERCIAL CONDITIONS

  - The tendered rate shall inter alia be deemed to include for the provision of  all  materials , process, operation and special requirements detailed in the  particular specification irrespective of whether these are mentioned in the description of equipment schedule and Bill of quantities or not. It is an express condition of the contract that the tendered rates for various items in the Bill of Quantities shall be deemed to include for the full, entire and final condition of the contractor respective items of the works in accordance with the provision of the contract.

  - The tendered rate shall include for all taxes, duties, etc. as applicable and shall be quoted on the works contract basis for Providing Laminar Flow Air Conditioner at THQH Thodupuzha

1.3	The tendered rate shall remain firm and free from variation due to rise in the cost of materials/equipment labour or any other reasons whatsoever during the contract period and valid extension.

1.4	The quantum of excise duty included in the tendered price, the rate at which they were assumed etc. shall be indicated in the tender.

  - UNIT RATES

  - Only approved work will be measured on completion and priced as per rates quoted against the respective items.

3.     BRIEF DESCRIPTION OF PRICING

  - The tenderer shall furnish duly certified breakup of material and labour separately for each item of work. The same shall be attached separately along with the price bid.

  - The quoted price shall be inclusive of all taxes and duties whether payable by the contractor or to be deducted at source. This shall include those applicable among VAT, Sales Tax, Income Tax, Customs Duty, Excise Duty, Turnover Tax, Service Tax, Work Contract Tax, Octroi, Labour Welfare Cess or any other Taxes and Duties prevailing in respect of this contract. ANY BID STATING THAT TAXES ARE EXTRA WILL BE SUMMARILY REJECTED.

- PRO-RATA VALUE

The detailed break up of prices for various items of equipments and materials of the full system should be provided by successful tenderers within fifteen days from the date of letter of intent to facilitate the Employer for assessment and verification and to certify payment.

- INCOME TAX

Any payment to the contractor as per contract, will be made after deducting income tax as per the rules and regulations.

6. 	 SALES TAX AND EXCISE DUTY

The tenderer shall clearly indicate sales tax, Excise and works contract tax and other duties as applicable in his offer for carrying out this work.

7.      SUBMISSION OF BILL

  - The contractor shall from time to time prepare and submit interim bills of the work executed and on completion of the contract, he shall prepare and submit the final bill. The measurements sheets in support of the interim and final bills shall be prepared by the contractor on the basis of measurements taken by him jointly with the project engineer and the said measurement sheets shall be submitted by him with the relevant bill.

- EXTRA ITEMS

        - The contractor is bound to carry out any items of work necessary for the completion of the job even though such items may not have been included in the schedule of probable quantities or rates, such items being necessary or essential for completing the job. Variation order in respect of such additional items and their quantities will be issued in writing by the Employer.

          - All shavings, cuttings and other rubbish as it accumulates from time to    time during the progress of work and on completion including that of the sub-contractors and special tradesman and all materials condemned by the project engineer shall be cleared and removed from the site by the contractor without any extra charge.

  - All measuring steel taps, scaffolding, ladders instruments and tools that may be required for taking measurements shall be supplied by the contractor.

- OVER TIME WORK

  - If the contractor is required to work night or on holidays in order to maintain the time schedule he shall take prior approval from the Employer. He should also provide and maintain at his own cost sufficient lights as may be necessary to enable the work to proceed satisfactorily during the night.

  - The contractor shall give full facilities to all other contractors working on site. He shall also arrange his programme of work so as not hinder the progress of other trades. The decision of the Employers on any point of dispute between the various parties shall be final and binding.

  - It is specifically pointed out that the contractor shall not be entitled to any compensation whatsoever on account of delay in procurement or supply of controlled materials and the rates quoted in the contract are fixed till the completion of the contract.

  - The contractor shall co-operate with other agencies appointed by the Employer for the work to proceed smoothly with the least possible delay and to the satisfaction.

  - The owners shall provide a source for power supply at one convenient point at    site. The contractor shall at his own cost install a separate meter at the said source and lay additional cables from the said source also at his own cost. For the electricity consumed by the contractor he shall pay the owner the actual cost at the rate charged by the local authority for power for constructional purposes. The contractor shall also obtain the necessary permit for utilizing power for constructional purposes.

- TERMS OF PAYMENT

  - For equipments delivered and sorted at the site for the installation, the payment will be made by the HLL in accordance of this contract.

  - The rate of payment for the contract value under this contract shall be regulated   and detailed below:

  - 70% of the contract value on pro-rata basis against open delivery of material at site and stored as directed by the HLL and after initial inspection.

  - 20% of the contract value on satisfactory installation of the complete system.

  - 10% of the contract value will be paid after testing, commissioning trial run & handing over to HLL.

11. SPECIAL CONDITIONS

11.1	EXECUTION WORK

11.1.1 The whole of the work as described in the contract (including bills of materials, specification and all drawings pertaining thereto) and as advised by the Owners/Employers from time is to be carried out and completed in all parts to the entire satisfaction of the Owners/Employers. Any minor details of construction which are obviously and fairly intended, or which may not have been definitely referred to in this contract, but which are usual construction practice and essential to the work, shall be included in this contact.

11.2	MAINTENANCE & TRAINNING FOR PERSONNEL

11.2.1	The contractor shall without any extra cost carry out for a period of 12 months after the installation is taken over by the owners, all routine and special maintenance and attend to any difficulties and defects that may arise in the operation of the system.

11.2.2	The contractor shall associate with the Employers’ staff during erection and the maintenance period, in the maintenance/operation of the system..

11.2.3	If required, by the Employers, the contractor shall also train members of the Employers’ staff at their works/service station without any extra charge.

11.3	CERTIFICATE OF COMPLETION

11.3.1	The contractor shall intimate to HLL in writing as and when the works are completed and put into beneficial use in order to enable HLL to check certify to the Employer to take over the plants.

11.3.2	The work shall not be considered as completed and put into beneficial use until HLL have certified in writing that the same has been completed and put into beneficial use.

11.3.3	The defects liability period of one year shall commence from date of such completion or any specific date mentioned therein.

11.4	OPERATIONAL AND MAINTENANCE MANUALS

11.4.1	The contractor shall also furnish the prints of all up-dated handing over along with required set of operating/maintenance manuals/instructions.

11.5   STATUTARY APPROVALS

All statuary approvals pertaining to the installations including electrical inspector approvals shall be in the scope of the supplier.

TECHNICAL SPECIFICATIONS

Air conditioning System

SECTION - I

BRIEF DESCRIPTION OF WORK

1.1	Scope of Work

The scope of work covers supply, installation, testing and commissioning of Air-conditioning System at OT Block, THQH, Thodupuzha

1.2	Space to be Air conditioned

The space to be air-conditioned is as per the drawings attached. Tenderers are advised to visit the site before submitting their bids.

1.3	Bill of Quantities & Equipment

The details of equipment and the bill of quantities required are furnished in relevant sections of this document.  The technical specifications are also described.  The tenderers are required to fill in the prices item wise all inclusive, as per format and submit the Bill of Quantities.  The rate quoted should be inclusive of taxes, duties, freight, packing and forwarding, Octroi entry tax, loading, unloading, handling at site, etc.  The tenderer shall not be eligible for any extra amount due to change in taxes, duties, etc.

1.4	Technical Data

The tenderers are required to submit technical data documents as per the format.  The data proposal sheets are enclosed in the tender document.   The tenderer shall fill in all the data required.

Section- II

TECHNICAL DETAILS

2.1      	SCOPE OF WORK

The complete scope of work shall cover supply, installation, testing and commissioning of Air Conditioning System at new building for OT Block, THQH, Thodupuzha including sizing of ducts, pipes routing & exhaust ventilation for toilets including ducting. The contractor shall submit the design & drawings for approval and obtain approval from 	Consultant/Client before commencement of works.

2.2    	Basis of Design

The entire system has been designed based on climatological data available as given under the section basis of Design.  The technical requirements given under here are only indicative and not descriptive and the contractor shall ensure that the whole system supplied is complete in all respects for the smooth operation of the plant and should be suitable for the rated performance.

2.3    	Terms and Definitions

The following terms have been used in the tender specifications, drawings, etc.

BIS	Bureau of Indian Standards

ASHRAE 	American society of Heating, Refrigeration and Air-conditioning Engineers, USA.

ASME		American Society of Mechanical Engineers.

ASA			American Standard Association.

B.S         	 British Standards

CMH  		Cubic Meter per Hour

CFM  		Cubic Feet per Minute

US GPM  	US Gallons per Minute

IGPM		Imperial Gallons per Minute.

RPM  		Revolutions per Minute

BTU/Hr. 	British Thermal Unit per Hour

KCal/Hr. 	Kilo Calories per Hour

HZ   		Hertz

H.P.  		Horse Power

Kg/CM2 	Kilo Gram per Square Centimeter

SG  			Supply Air Grilles

SD  			Supply Air Diffuser

SAF   		Supply Air Filters

FD 			Fire Damper

VCD  		Volume Control Damper

RG          	Return Air Grilles

RD			Return air diffuser

FAD   		Fresh Air Damper

RH   		Relative Humidity

DB   		Dry Bulb Temperature

WB   	Wet Bulb Temperature

MV  		Mechanical Ventilation

DP  			Drain Point.

RO         	Rate Only

The design, manufacture, identification of material and testing of the equipment covered in this specification shall comply with the latest edition of the appropriate standard of the following:

1)	Duct Work -   IS:655 (latest edition)

2)   	Welding -  IS:3589

3)   	Refrigeration and Air-conditioning - As per ASHRAE/ISI air-conditioning and refrigeration institute standards.

4)	Sluice Valves for Water Lines - IS:778-1980

5)	Copper alloy Gate/ Globe / Check Valve for water lines - 	IS:778

6)	Colour code for the identification of pipe lines - IS:2379-1963

7)	Specific requirements for the direct switching of the individual motors - 
IS:4064 (Part-II)-1978

8)	PVC insulated (HD) Electric Cables for working voltage up including 1100 Volts - 	IS:1554 (Part I)

9)	Starters - IS:8554 (Part-I) 1979

10)	HRC Cartridge fuse links upto 650 Volts  - IS:2208

11)	Inspection and testing of installation
IS:732 (Part-III) 1979

12)	Galvanized steel wire for fencing - IS:277-1977

13)	Three phase induction motors - IS:325

14)	Horizontal centrifugal pumps - IS:1620

15) 	Wrought aluminum and aluminum alloy sheet and strip for general engineering purposes  - IS:737

16)	Bourdan tube pressure & vacuum gauges - IS:3624

17)	Glossary of terms used in refrigeration and air-conditioning - IS:3615

18)	Code for practice for standard for selection of standard worm and helical gears - IS:7403

19)	PVC insulated (heavy duty) electric cables for working voltage upto and 			including 1100 watts: -IS:1554 (Part-I)

- Expanded Polystyrene (EPS) : -	IS 4671.

- Resin bonded glass wool: - IS 8183.

2.4	Safety Codes

The following IS codes shall be followed:

- Safety code for mechanical refrigeration - IS:660

- Safety code for air-conditioning - IS:659

- Safety code for scaffolds & ladders  -IS:3696

- Code of practice for fire precautions in welding & cutting operations - IS:3016

- Code for safety procedures and practices in electrical works - IS:5216

- Code of practice for safety and health requirements in electrical & gas welding and cutting operations - IS:3696

- Indian Electricity Act 1910

- Electricity Supply Act and Indian Electricity Rules.

2.5	MACHINERY

AIR COOLED PACKAGED/DUCTABLE AIR CONDITIONING UNIT

- Cabinet

The packaged split air conditioning units shall have metal cabinet of min 1.6mm thick (16 gauge) galvanized sheet steel. The body should be machine pressed and adequately stiffened. The body should be chemically treated for corrosion resistance and Polyester powder coated.

- Compressor

All compressors shall be hermetically sealed scroll type of suitable capacities.  Compressor shall be suitable for R22 refrigerant. The compressor shall be electrically interlocked with indoor and outdoor fan motors, HP/LP cutouts and thermostat in the evaporator. The compressor shall be housed inside the Condenser.

- Condenser (Air cooled)

The coils shall be made of copper hydraulically bonded with aluminium fins. The tubes shall have a minimum of 9.5 mm outer diameter, firmly bonded with aluminium fins spaced at 12-14 fins/inch.  The air velocity across the face of the coil shall not exceed 200 m/min.  The coils shall be designed for a maximum working pressure of 35 kg./sq.cm.  The condenser coil shall be protected on the open end by a wire mesh duly powder coated/plastic coated.

- Evaporator coil

The coils shall be made of copper hydraulically bonded with aluminium fins.  The coils shall be hydrophilic in nature.  The tubes shall have a minimum of 9.5 mm outer diameter, firmly bonded with aluminium fins spaced at 12-14 fins/inch.  The air velocity across the face of the coil shall not exceed 170 m/min.  The coils shall be designed for a maximum working pressure of 35 kg/sq.cm.  The circuit should include a thermostatic expansion valve/capillary tube, distributor, liquid strainer, suction line shut off valve and liquid line shut off valve.

- Condenser motor

The condenser motor shall be of IP-55 rating.

- Refrigeration piping and accessories

Only hard drawn copper shall be used in piping with brass fittings wherever required.  Brazing shall be with silver copper phosphorous alloy.  Horizontal lines shall have a grading of at least 1:250 away from the compressor and towards condenser to prevent gravity draining of oil to compressor.  Liquid lines shall be sized to ensure that flashing of liquid refrigerant does not occur.  The circuit should include a thermostatic expansion valve, distributors, liquid strainer, de-hydrator and liquid lines shut off valve and suction lien shut off valve.

Leaks shall be tested with soap solution at a minimum pressure of 21 kg/sq.cm.  After all leaks have been repaired, system shall be tested with the test pressure maintained for a period of not less than 8 hours.  No measurable drop in pressure should be detected after the pressure readings are adjusted for temperature changes.  After satisfactory completion of the pressure test, the system shall be evacuated to reduce the pressure to 0.1 Kg/Sq.cm. for a period of 6 hours and vacuum broken.  A vacuum pump connected to the refrigeration system shall be used to create the vacuum and the installed compressor shall not be used to create the purpose.  The system shall again be evacuated and a vacuum of 0.01 Kg/Sq.cm. maintain for 24 hours before charging with correct quantity of refrigerant and oil.  The system shall be operated for 12 hours and then again tested for leaks.

- Drain Piping

Drain pipe shall be of 32mm dia.  PVC pipes. All Ductable Split units shall be provided with independent drain lines. And all the drain line above false ceiling shall be insulated. The drain shall be taken to the nearest exit points.

- Fan

Fan section including wheel and housing shall be of heavy gauge steel/aluminium.  Fans shall be centrifugal, forward curved multi-blade type.  Fan housing shall have inlets and guide vanes for smooth air flow.  Fans shall be complete with drive motor.  The fans should be statically and dynamically balanced.  The fan motor should be resilient mounted.  The fan should deliver a static pressure of 125 mm.

- Dampers

All fresh air intakes shall be provided with dampers. The fan outlets should be controllable with a damper. The supply collars, wherever mentioned, shall be provided with collar dampers.

- Filters

All evaporator units shall be provided with air filters capable for filtration unto 20 microns.  The filters shall be of washable synthetic fibre type.

- Control Panel

All units shall have independent electrical control panels housing contactors, overload relays, voltage cutouts, time delays, interlocks, strip connectors, indication lamps, and control fuse.  All these have to be housed inside the Outdoor unit of each circuit.

- Thermostat

The Thermostat shall be control wired with the control panel and shall be placed in the return air path inside the boxing.

- Installation

Adequate vibration isolation using rubber/neoprene pads/vibration springs in order to reduce transmission of vibrations to the floor shall be provided for all condensing units.

- Testing

Ductable units after installation shall be tested for its conformity to specifications.  Units shall also be tested for the rated capacity and power consumption.

- Electric motor

The electric motor driving the compressor shall be as per manufacturer’s standard for this compressor and motor shall be suitable for operation on A.C. supply.  The motor shall be continuous duty rated for the application. The motor shall be selected such a way that the motor rating is for actual requirement.

The motor shall be provided with suitable bearing to take care of loads/thrust.  Necessary lubricators shall be provided to enable the bearings to be correctly greased as required. The tenderer shall also calculate KW/TR.

16.	AHU

The AHU shall be AR certified floor mounted/ceiling suspended type, double skinned type made of 0.6mm pre-coated GI sheets on both sides min 25mm thick PUF CFC free, 40kg/m3 between sheets, SS 304 drain pan with nitrile rubber insulation, GSS base channel. Suitable for DX coil of copper 6 rows min,  Aluminum fins, with synthetic non woven type pre (EU4) and fine filters (EU 7) filtration up to 3microins. The AHU shall be with suitable static blower DIDW, centrifugal, forward curved blade, belt driven for hepa filter application comprising of suitable rated motor min EFF2 rated. The AHU shall also be provided with manual volume control damper on supply, return and fresh air sides to control the air volume. The AHU shall be UL certified for safety. The AHU shall be provided with access doors for filter cleaning and maintenance etc.

2.6	DUCTING SYSTEM

This section deals with supply, erection, testing and commissioning of all sheet metal ductwork conforming to specifications given below. The ducts shall be of factory fabricated.

2.6.1	Material for Ducting

All ducts shall be fabricated from galvanized sheet of 120 gm/sq.m (Class VIII) confirming to IS 277-1962 (revised). The fabrication of duct shall strictly conform to ISS 655-1963.  The thickness of the sheet shall be as follows:

| Maximum size (mm) | Thickness of sheet (mm) | Type of transverse joint connections | Bracing (if any) |
| --- | --- | --- | --- |
| Upto 300 | 0.63 24 G | S-drive, pocket or bar slips, on 2.5m centres | None |
| 301 to 600 601 to 750 | 0.63 24 G | S-drive, pocket or bar slips, on 2.5m centres S-drive, 25mm pocket or 25mm bar slips on 2.5m centres drive | None 25x25x3mm angle 1.2m from joint |
| 751 to 1000 1001 to 1500 | 0.80 22 G | 40x40mm angle connections, or 40mm pocket or 40mm bar slips, with 35x3mm bar reinforcing on 2.5m centres | 40x40x2mm angle 1.2m from joint |
| 1501 to 2250 | 1.00 20 G | 40x40mm angle connections, or 40mm pocket or 40mm bar slips, 1 m maximum centres with 35x3mm bar reinforcing | 40x40x3mm angle / 40x40x3mm angle 60mm from joint. |
| 2251 & above | 1.25 18 G | 50x50mm angle connections, or 40mm pocket or 40mm bar slips, 1 m maximum centres with 35x3mm bar reinforcing | 40x40x3mm angle / 40x40x3mm angle 60mm from joint. |

The following points shall be also taken into account while fabrication of ducts.

a)	All ducts shall be as per gauges, etc. indicated on the approved drawings.

b)	All ducts of size larger than 450 mm shall be cross broken.

c) 	All ducts shall be supported from RCC/truss by means of MS rods, angles, etc.

d)	The ductwork shall not extend outside and beyond height limits as specified on the approved drawings.

e)	All ducts shall be reinforced, if necessary and must be secured in place so as to avoid shifting of the ducts on its supports.

f)	The vanes shall be provided and securely fastened to prevent noise and vibration.

g)		The rubber gasket shall be installed between duct flanges in all connections and joints.

h) 		The ductwork can be modified in consultation with Purchaser to suit actual conditions in the building.

i)		All flanges and supports should be primer coated on all surfaces before erection and painted with aluminum paint thereafter.

j)		The flexible joints are to be fitted to the suction and delivery of all fans with double heavy canvass.  The length of flexible joints should not be less than 150 mm.

- All sheet metal gauges and fabrication procedure as given in BIS specification shall be strictly adhered to. The BIS specification shall form part of this contract.

2.6.2	Grilles/Diffusers

Material of construction - Extruded Aluminum

Supply air and return air grilles shall be continuous type and shall be fixed as given in the approved drawing.  The square/rectangular diffusers shall be flush or step down type to match false ceiling pattern. The diffuser blades shall be die formed, flush mounted with single or double direction airflow.  	Supply of frames for fixing the grilles/diffusers, if required, is also in the scope of the contractor.

Return air grilles shall be with blanks and return air provisions. The size and appearance shall match with supply air grilles. The supply air grilles shall form part of the continuous return air grilles.  The fixing of grillers/diffusers should be done in close co-ordination with false ceiling work and as directed by Purchaser.

The aluminum grilles/diffusers, etc. shall be powder coated of colours to match the interiors.  However, successful bidder shall have to obtain prior approval regarding colour, finish, shape, etc. of grilles/diffusers and sample should be submitted to Purchaser for approval.

2.6.3	Testing

The complete duct system shall be tested for air leakage and complete air distribution systems shall be balanced in accordance with the approved drawings for achieving designed values inside the building.

2.7		THERMAL / ACOUSTIC INSULATION

2.7.1	Material

- Insulation material shall be Closed Cell Elastomeric Nitrile Butadiene Rubber.

- Insulation material shall have anti-microbial product protection. The antimicrobial product protection shall be an integral part of insulation that is built-in during the manufacturing process and the product protection should not allow the microbes to function, grow and reproduce.

- Resistance towards microbiological growth on insulation surface should confirm to following standards: Fungi Resistance – ASTM G21 where the fungal growth on the surface is NIL after 28 days of incubation at 28 – 30 deg C and Bacterial resistance – ASTM E 2180 where the reduction of bacterial growth is minimum 99.9% after 24 hours of incubation at 34 – 38 deg C.

- Thermal conductivity of Elastomeric Nitrile rubber shall not exceed 0.035 W/mK at an average temperature of 20C in accordance to EN12667

- The insulation shall have fire performance such that it passes Class 1 as per BS476 Part 7 for surface spread of flame as per BS 476 and also pass Fire Propagation requirement as per BS476 Part 6 to meet the Class ‘O’ Fire category as per 1991 Building Regulations (England & Wales) and the Building Standards (Scotland) Regulations 1990.

- Water vapour permeability shall not exceed 1.74 x 10-14 Kg/m.s.Pa, i.e. Moisture Diffusion Resistance Factor or ‘µ’ value should be minimum 10,000 according to EN 12086

- Density of Material shall be between 40 to 60 Kg/m3.

2.7.2	Duct Insulation

External thermal insulation shall be provided as follow:

- The thickness of Nitrile rubber shall be as shown on drawing or identified in the  schedule of quantity. Following procedure shall be adhered to:

- Duct surfaces shall be cleaned to remove all grease, oil, dirt, etc. prior to carrying out insulation work. Measurement of surface dimensions shall be taken properly to cut closed cell elastomeric rubbers sheets to size with sufficient allowance in dimension.

- Material shall be fitted under compression and no stretching of material shall be permitted. A thin film of adhesive shall be applied on the back of the insulating material sheet and then on to the metal surface. When adhesive is tack dry, insulating material sheet shall be placed in position and pressed firmly to achieve a good bond. All longitudinal and transverse joints shall be sealed as per manufacturer recommendations. The adhesive shall be strictly as recommended by the manufacturer.

- The detailed Application specifications are mentioned separately.

2.7.3	Insulation of Ducts Exposed Directly to Sunlight

For installations exposed to sunlight, after giving 36 hours curing time for the adhesive apply manufacturer’s recommended UV/Mechanical Protection. Please refer the separate detailed guidelines on UV/Mechanical Protection.

2.7.4	Piping Insulation

All chilled water, refrigerant and condensate drain pipe shall be insulated in the manner specified herein. An air gap of 25 mm shall be present between adjacent insulation surfaces carrying chilled water or refrigerant.  Before applying insulation, all pipes shall be brushed and cleaned. All Pipe surfaces shall be free from dirt, dust, mortar, grease, oil, etc. Nitrile Rubber insulation shall be applied as follows:

- Insulating material in tube form shall be sleeved on the pipes.

- On existing piping, slit opened tube of the insulating material (slit with a 	very sharp knife in a straight line) shall be placed over the pipe and 	adhesive shall be applied as suggested by the manufacturer.

- Adhesive must be allowed to tack dry and then press surface firmly 	together starting from butt ends and working towards centre.

- Wherever flat sheets shall be used it shall be cut out in correct dimension. 	All longitudinal and transverse joints shall be sealed as per manufacturer 	recommendations.

- The insulation shall be continuous over the entire run of piping, fittings and 	valves.

- All valves, fittings, joints, strainers, etc. in chilled water piping shall be 	insulated to the same thickness as specified for the main run of piping and 	application shall be same as above. Valves bonnet, yokes and spindles 	shall be insulated in such a manner as not to cause damage to insulation 	when the valve is used or serviced.

The detailed application specifications are as mentioned separately. The 	manufacturer’s trained installer should only be used for installation.

2.7.5 	Recommended Adhesive

In all cases, the manufacturer’s recommended Adhesive should be used for the specified purpose.

2.7.6	Acoustic Insulation

Material shall be engineered Nitrile Rubber open cell foam.

The Random Incidence Sound Absorption Coefficients (RISACs) across the octave band frequencies; tested as per ISO 354, and Noise Reduction Coefficients (NRCs) for the Acoustic Insulation should be minimum as per the below chart:

| Freq (Hz) | 125 | 250 | 500 | 1000 | 2000 | 4000 | NRC |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 10 mm | 0.03 | 0.04 | 0.14 | 0.40 | 0.88 | 1.00 | 0.40 |
| 15 mm | 0.01 | 0.09 | 0.29 | 0.74 | 1.08 | 0.83 | 0.55 |
| 20 mm | 0.04 | 0.13 | 0.40 | 0.90 | 1.04 | 0.90 | 0.60 |
| 25 mm | 0.05 | 0.25 | 0.86 | 1.14 | 0.88 | 0.99 | 0.80 |
| 30 mm | 0.07 | 0.32 | 0.99 | 1.16 | 0.93 | 1.08 | 0.85 |
| 50 mm | 0.23 | 0.73 | 1.29 | 0.99 | 1.09 | 1.11 | 1.05 |

- The material should be fibre free.

- The density of the acoustic insulation should be minimum 140 Kg/m3

- The insulation should have Microban®*; Built-in Anti-Microbial Product 	Protection, and should pass Fungi Resistance as per ASTM G 21 and 	Bacterial Resistance as per ASTM E 2180.

- The insulation should be non-eroding & should pass Air Erosion 	Resistance Test in accordance to ASTM Standard C 1071-05 (section 	12.7).

- The material should have a thermal conductivity not exceeding 0.047 	W/m.K @ 20 Deg. C

- The material should withstand maximum surface temperature of +850C 	and minimum surface temperature of -200C

- The material should confirm to Class 1 rating for surface spread of Flame 	in accordance to BS 476 Part 7 & UL 94 (HBF, HF 1 & HF 2) in 	accordance to UL 94, 1996.

- The acoustic insulation should be tested and approved by Sound 	Research Laboratories Ltd., U.K.

- Thickness shall be 10mm for Duct Acoustic Lining

- Duct so identified and marked on Drawings and included in Schedule of 	Quantities shall be provided with internal acoustic lining for a distance of 	minimum 6 meters (or 30% of the duct length whichever is more)

- Thickness of the insulation material shall be as specified for the individual 	application. The insulation should be installed as per manufacturer’s 	recommendation.

2.7.7	Accessories

Adhesive to adhere insulation to the inside walls of the duct shall be from the Insulation manufacturer only.

2.7.8	Under deck insulation

- Insulation material shall be Closed Cell Elastomeric Nitrile Rubber

- Density of Material shall be between 40 to 60 Kg/m3

- Thermal conductivity of elastomeric nitrile rubber shall not exceed 0.035 	W/mK at an average temperature of 0C

- The insulation shall have fire performance such that it passes Class 1 as 	per BS476 Part 7 for surface spread of flame as per BS 476 and also pass Fire Propagation requirement as per BS476 Part 6 to meet the Class ‘O’ Fire category as per 1991 Building Regulations (England & Wales) and the 	Building Standards (Scotland) Regulations 1990

- Material should be FM (Factory Mutual), USA approved.

- Water vapour permeability shall not exceed 0.017 Perm inch (2.48 x 10-14 	Kg/m.s.Pa), i.e. Moisture Diffusion Resistance Factor ‘µ’ value should be 	minimum 7000.

2.7.9	Installation procedure:

- The ceiling surface shall be cleaned with brush to remove all dirt, cement etc. If surface is uneven it should be made smooth prior to carrying out insulation work.

- A layer of synthetic rubber adhesive should be applied on the ceiling with the help of brush so that all the pores are filled and surface becomes smooth and allow it to dry.

- Allow an additional 5 mm to the total dimensions while cutting Insulation sheet.  Ensure you measure the cutting dimensions on the top surface of the insulation sheet. This can be identified by the products markings; “they are always on the top surface. This surface is the one you will see after installation.

- All Insulation sheet and ceiling surfaces shall have all-over adhesive coverage. Adhesive should be applied on the side that has no product markings and identification printing. This side is the one that curves inwards.

- During installation avoid air bubbles. Always apply pressure while fixing the Insulation sheet, this action will ensure maximum bond strength.

- All cut Insulation sheet edges shall be of a “clean cut nature and not cut rough”.

- All seams and joint shall be sealed with synthetic rubber adhesive.

- Measurement of surface dimensions shall be taken properly to cut closed cell elastomeric rubbers sheets to size with sufficient allowance in dimension. Material shall be fitted under compression and no stretching of material shall be permitted. A thin film of adhesive shall be applied on the ceiling with brush and then on to the back of the insulating material sheet with brush/small piece of sheet metal having smooth edges. When adhesive is tack dry, insulating material sheet shall be placed in position and pressed firmly to achieve a good bond. All joints shall be sealed. The adhesive shall be strictly as recommended by the manufacturer. There is no need to make holes for wires etc. as no supporting wires/screws are required.

While doing installation on the metal roofing, it is important to ensure that metal roof should not face direct sun light, as metal sheets becomes very hot and adhesive may not work. In such conditions work should be done in the evening / night

2.8	FIRE DAMPERS

This section deals with supply, erection, testing and commissioning of fire dampers and box type dampers, conforming to general specification and suitable for duty selected, indicated in schedule of equipment/material.

2.8.1 	Dampers

a)  	The fire dampers of at least two hour rating shall be provided in all return air ducts at wall crossing. All fire dampers shall be fire tested by CBRI Roorkee for 120 minutes fire rating as per UL555-1995.

b)	6G GSS sheet blade and frame with 165mm casing, heavy duty interlocking blades and fuly enclosed bade linkage mechanism, SS lateral seal blade seals, self lubricating sintered bronze bushes, fire rating as per UL555-1995 tested as per BS-476 part 20 with 18G extended sleeve 450mm and with fusible link, spring mechanism control panel temp sensor, smoke sensor, limit swith with lever for auto shut off in case of fire/smoke

c)	In the normal position the blades of the dampers shall remain open to allow maximum air to flow.  The dampers shall be actuated using fusible link and spring mechanism.  The fire damper shall also close due to temperature rise above 74oC.

d)	All fire dampers shall be mounted on wall with a duct sleeve 400 mm long depending on the wall thickness.  The sleeve shall be factory fitted on the fire damper.  The joint at the sleeve end shall be slip on type.  Minimum thickness of GI sheet used for sleeves shall be 18G.

2.8.2 		Exhaust Air Blowers

line exhaust air flow duct blowers suitable for single phase operations with direct driven class F motor, IP 54 insulation, max 1400rpm, necessary steel frame, and complete with GI box, with an operating sound level not exceeding 60dB at 3m distance.

2.8.3	Hepa Filter

Hepa Filter shall be of efficiency 99.97%. HEPA filters shall be aluminium corrugated and Mini pleat style. All filters shall made up of high quality mico-fine glass fiber media. Filter frames shall made up of Galvanized steel. Hepa  filter shall ensure low pressure drop even at high airflows & with Antimicrobial protection.

All filters shall be made in accordance and tested to EN 1822 / ASHRAE 52.2 standards. These filters shall be tested at factory and test cetrtificates from OEM’s shall be produced. The Hepa filter shall be fixed in a plenum constructed at the AHU mouth.

2.9	PAINTING WORK

2.9.1	All equipment shall be painted as specified under respective headings. Grilles/ diffusers shall be powder coated as per approved colour matching with interiors. The contractor has to get approval of the quality and colour of paints for all types of painting work.

All pipes for chilled water shall be painted as per standard code of practice and arrows indicating direction of flow of water shall be marked.

2.9.2	Colour scheme for the plant and equipment

i) 	Compressor                      		..  Battle ship grey

ii)	Condenser                       		..  Battle ship grey

iii)	Refrigerant discharge line      		..  Red

iv) 	Refrigerant liquid line         		..  Yellow

v) 	Steel supports                  		..  Black

vi) 	Direction of flow of water      		..  White arrows

vii) 	Electrical panels/sub-panel/remote control console 	..  Light grey or any approved

viii) 	Cable trays                     		.. Black

xi) 	Supports for ducts/open ducts              		.. Black.

Section- III

MODE OF MEASUREMENT

The following measurement code shall apply to this contract:-

3.1	Mechanical Items

3.1.1	Ducting

- All sheet metal ducting work shall be measured in terms of final sheet area installed in Sq. m.

Eg:- 	Measurement of 600 mm x 300 mm duct of 1 m length =  [(600+300)x2x1]  = 1.80 Sq.m.

1000

- Duct fittings such as bends, elbows, tap-offs, collars, transformation pieces etc. shall be treated as ordinary duct pieces with their length measured along their centre line as mentioned in point (i).

- Vanes, splitters, duct dampers, deflectors, access doors, etc. which are required to be installed in the duct work shall not be measured    separately as it shall form part of the duct work.

- Duct supports, stiffening members, etc. shall not be measured separately. All such supports/hangers shall form part of duct work.

- Equipment connections such as canvas/asbestos/rexine shall be deemed to be part of the duct work, and no separate measurement shall be allowed.

- No separate special measurement shall be made for bends, transformation pieces, tap offset, elbows, etc.

3.1.2  Grilles:

All grills will be measured in terms of effective area in Sq.m.

3.1.3  Diffusers:

Diffusers will be measured in terms of effective area in Sq.m.

3.1.4	Ducting Insulation

- Ducting insulation will be measured on the basis of centerline of insulation 	and not the outer line of insulation.

Eg:- Measurement of 25mm thick insulation on 600 mmx300mm   duct of 1m length = [(600+25)+(300+25)]x2x1] Sq.m

1000

- No separate special measurement shall be made for insulation of bends, transformation pieces, tap offs, elbows, etc.  All such insulation shall be treated as standard duct insulation.

- Insulation item shall include all accessories and finishes as specified.  No separate measurement will be made for such items.

3.2	Electrical items

Mode of Measurement of Electrical Items

The Works shall be measured, as prescribed in the specification of work, notwithstanding any general or local custom, except where otherwise specifically described or prescribed in the Contract.  Wherever not specifically mentioned in the Contract, the mode of measurement as prescribed in the relevant IS codes shall be applicable and binding to the Contract.  Only the latest editions of all the codes of practices including all latest official amendments and revisions shall be applicable.

Section-IV

TESTING OF AIR-CONDITIONING SYSTEM

4.1	Routine and type tests for the various items of equipment of the system shall be performed at the Contractor’s own cost and test certificates are to be submitted.

4.2	The performance tests to determine whether or not the full intent of the specification is met shall be conducted by the contractor.  After notification to Purchaser that the installation has been completed and the system has run continuously for a period of at least one week, the contractor shall conduct under the direction and the presence of Purchaser such tests as specified to establish the capacity of various equipment supplied and installed by the contractor.

4.3	The contractor shall operate, test and adjust the air-conditioning system units, fan, motors, all air handling appliances including adjustment of regulators, dampers, etc.  All testing equipments, labour, operating personnel, oil, refrigerant or any other item required for these tests shall be provided by the contractor to enable the plant to be put in a continuous running test.

4.4	Test procedure:

4.4.1	Design Conditions:

The inside and outside conditions shall be recorded on hourly basis.  The outside and inside dry bulb and wet bulb temperatures shall be recorded by means of a sling psychrometer with mercury thermometers.  The relative humidity shall be computed from the psychometric chart.  The inside dry bulb temperature and relative humidity shall fall within the specified limits.

The contractor should conduct performance such tests as indicated in the rated Technical Part and produce sufficient documentary proof that the plant is operating at the rated capacity.

4.5	The following readings shall be recorded hourly during the tests and capacity of the plant shall be computed.

1.   	Compressor

a.   Suction pressure         	- 	Kg/cm2 (psi)

b.   Suction temperature      	-  	oC (oF)

c.   Discharge pressure       	-  	Kg/cm2 (psi)

d.   Condensing Tempr.        	-  	oC (oF)

e.   Oil pressure             	-  	Kg/cm2  (psi)

f.   Compressor Speed         	-  	RPM

2.   	Compressor motor

a. Rated capacity           	-  HP

b. Rated volts              	- 	Volts

c. Rated current            	- 	Amps

d. Starting current         	-	Amps

3.   	Inside unit

a.   Air velocity             	- 	M/Hr. (FPM)

b.   Face area           	- 	M2 (SFT)

c.   Air quantity             	-	M3/Hr. (CFM)

d. Entering air temp. DB    	- 	oC (oF)

e.  Entering air temp. WB    	- 	oC (oF)

f.  Leaving air temp. DB    	- 	oC (oF)

g.  Leaving air temp.  WB    	- 	oC (oF)

4.   	Air Grilles

a.  Area of Grilles           	-  	M2  (Sft)

b.  Velocity                  	- 	M/Hr (FPM)

c.  Air flow rate             	-  	M3 (FPM)

d. Temperature DB            	-  	oC (oF)

e. Temperature WB            	-  	oC (oF)

5.   	Air Diffusers

a.  Area            	-  	M2  (Sft)

b. Velocity                  	- 	M/Hr (FPM)

c. Air flow rate             	-  	M3 (FPM)

d. Temperature DB            	-  	oC (oF)

e. Temperature WB            	-  	oC (oF)

6.   	Filters

a. Total area               	- 	M2 (Sft)

b. Effective area           	- 	M2 (Sft)

c. Velocity of air          	- 	M/Hr (FPM)

d. Quantity of air          	- 	M3 (CFM)

Section-v

TECHNICAL DATA

(To be submitted along with the tender)

5.0	The following data shall be furnished along with the offer: (REFER LIST OF APPROVED MAKES)

(Attach catalogues, brochures, etc.)

1.  	Ductable Split unit

Manufacturer

Model

Actual capacity  TR

Overall dimensions

Over all weight

Operating weight

Refrigerant

Compressor

Manufacturer

Model

Type

Capacity at the specified water temp. and flow rates -  in TR

Type of capacity control provided

Type of lubrication

KW / TR

Motor

Model

Manufacturer

Number of motors

Capacity HP

Whether provided with part winding

Type

Class of insulation

Speed    RPM

Characteristics

Type of starter

Rating

Whether the following protections are provided.

i) 	Overload        						Yes/No

ii) 	Under voltage   						Yes/No

- Single phase protection

(for three phase motor starters)       			Yes/No

2.   	Inside units

Manufacturer

Model

Type of fan

Fan speed (R.P.M.)

No. of fans.

Fan wheel diameter (mm)

Drive arrangement

Material and thickness of fan wheel and blades.

Materials and thickness of housing.

Fan outlet area

Outlet velocity.

Total air quantity

Static pressure at outlet. (mm. of water)

Whether statically and dynamically balanced.

B.H.P. Consumed

Total weight of all items

## Cooling Coil

Material of Tubes

Material of fins

Tube diameter

Tube thickness

Fin thickness

Method of bonding of fins

No. of fins/cm.

Total tube surface outside

Test pressure

Coil face area

Filter

Manufacturer

Type of filters

Filter medium

Material of frame work and its thickness

Face area

Face velocity across filters

Pressure drop across filters (mm of water)

## Motor

Manufacturer

Model

Number of motors

Capacity   HP

Type

Class of insulation

Speed    RPM

Characteristics

Type of starter

Rating

Whether the following protections are provided.

i) 	Overload        						Yes/No

ii) 	Under voltage   					Yes/No

iii) 	Single phase protection 
(for three phase motor starters)  	                  	Yes/No

3.   	Ducting

Material

Manufacturer

4.  	Insulation (for ducting)

Manufacturer

Material

‘k’ Value at 10 (oC) mean temperature

Thickness.

Density

Fire Retardant property

Note : Any other data relevant to each equipment shall also be furnished.

Approved make of items –HVAC

| 1. | AC Condensing Outdoor Units/Ductable Units /Split AC | - | Blue star/ Voltas/ Carrier /Hitachi/ ETA/Daikin/Samsung/General |
| --- | --- | --- | --- |
| 2. | AC Compressor | - | Danfoss/Koplan/Emerson |
| 3. | AC AHU’s& IDU’s | - | Blue star/ Voltas/ Carrier /Hitachi/ LG/ETA/Daikin/General/VTS/Zeco |
| 4. | De-humidifier | - | Bry Air/Dessicant Rotor |
| 5. | Air- curtain |  | Almonard, Russel |
| 6. | Copper Pipes | - | Totaline/Mandev/Piyush |
| 7. | ### Three phase motors | - | Siemens/Kirloskar/Crompton/Bharath Bijlee /ABB /Alsthom |
| 8. | ### Aluminium Conductor Cables | - | Finolex/NICCO/Havells//Gloster |
| 9. | ### Stabilizer | - | V Guard/VOLTAS/Everest |
| 10 | ### GI/Al Sheets | - | SAIL/TATA/JINDAL/HINDALCO/NACL |
| 11 | ### Resin bonded Glass wool | - | UPTWIGA /Owens Coning/KIMMCO |
| 12 | ### Nitrile Rubber Insulation | - | Armaflex/K Flex |
| 13. | ### Grilles/Diffusers | - | Airmaster/Carryaire/Air Flow/Sachins Ravistar |
| 14 | ### Pressure gauges | - | Feibig/H-Guru/Jaspin |
| 15 | ### Industrial type thermometers | - | Feibig/H-Guru/Jaspin |
| 16 | ### Fire/Volume Control Dampers | - | Carryaire/Airmaster/Air Flow/ Ravistar |
| 17 | ### Exhaust/ Duct Fans | - | System Air/Kruger/Nicotra |
| 18 | ### Paints | - | ICI/Asian/Berger |
| 19 | ### PVC pipe | - | Any ISI marked |
| ### 20 | ### Motors | - | Siemens, Kirloskar, Crompton, Bharath, Bijlee, ABB, Alsthom, NGEF |
| ### 21 | ### Hepa Filter | - | Aerofoil/Pyramid/AAF |
| 22 | ### Valves | - | Audco, Leader, Kirloskar, Advance, |
| 23 | ### Factory Fabricated Ducts | - | ZECO, Western Air Ducts, Rolstar, Camduct |
| 24 | ### Double Skin Aluminum Panel | - | Lloyd, Rinac |

LIST OF APPROVED MAKES FOR ELECTRICAL WORKS

| S.No. | #### MATERIALS | #### PREFERED MAKE |
| --- | --- | --- |
| 1 | #### LT UG cables | Gloster / Torrent/ Polycab |
| 2 | #### LT cable gland, lugs | #### Comet / Dowell / Jainson |
| 3 | #### MCCB | L&T / Siemens / Schneider / BCH |
| 4 | #### SDFU, Isolators, Change over switch | L&T / Siemens / Schneider / BCH |
| 5 | Relays | L&T / BCH / Schneider / Siemens. |
| 6 | Resin cast CTs | Intrans / Resitech / PGR Powertech |
| 7 | Measuring Instruments | AE / IMP / Rishab / Schneider / L&T |
| 8 | #### MCBs, DBs, Industrial plugs | Legrand / Panasonic / Siemens |
| 9 | #### Wiring cables | RR Kables / Finolex/ Anchor |
| 10 | PVC Conduit & accessories, Casing & capping | Precision / Avon Plast / /Konseal / Balco |

BILL OF QUANTITIES

ABSTRACT

| SL. NO | ITEM | AMOUNT (Rs.) |
| --- | --- | --- |
| 1 | Laminar Flow A/c Works |  |
| 2 | Electrical works |  |
|  | Grand Total |  |

| Providing laminar Flow Air-conditioners at THQH Thodupuzha, Idukki District. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Sl No | Description of items | Unit | Qty | Rate (in words and figures) | Amount |
|  | PART A - MACHINERY |  |  |  |  |
| 1 | Supply, installation, testing and commissioning (SITC) of 5.5 TR capacity aircooled Outdoor condensing unit with scroll compressor as per specifications complete with suitable capacity drive motor, air cooled condenser with all accessories, hermetically sealed scroll compressor, electronic microprocessor pendant controller with digital display, first charge R 22 refrigerant gas, vibration isolator pads and saftey devices like thermal protector, pressure relief valve, over load relays single phase preventor, high-low pressure cut out, suitable for three phase 440V supply. | No | 3 |  |  |
| 2 | Supply, installation, testing and commissioning of suitable hard drawn copper refrigerant piping for 5.5TR machine with 13 mm nitrile rubber insulation interconnecting the condensing unit to evaporating unit for packaged units as per site condition | RM | 53 |  |  |
| 3 | SITC of DX type double skinned air handling units, ceiling suspended/floor mounting type 5.5 TR, 1200 lps capcity complete with suitable DIDW blower (asper approved make), blower section, static pressure of 125mm of water column, built in pre filter(EU4), fine filter(EU7) and controls connected to condensing units, insulated SS drain pan, 6 row cooling coil, electric motor, belt drive package with TEFC motor class 'B' insulation, suitable for 3 phase, 415 V, 50Hz supply, suitable AHU panel, ARI certified, belt guards, thermometers and pressure gauges at the inlet & outlet, suitable supports for suspending from slab, vibration isolator, etc. conforming to specifications. The air handling units shall have 1 inlet refrigerant coils and 1 outlet refrigerant coils suitable for 1 numbers of 5.5 TR capacity ODU and shall conform to specifications. | No | 3 |  |  |
| 4 | Supply, installation, testing and commissioning of Air Cooled High Wall mounted Split Air Conditioner of following capacity consisting of high wall mounted type room unit (fan coil) with cordless remote control and one number outdoor condensing unit comprising of enegy efficient suitable rotary compressor for operation on single phase, 230 V, 50Hz supply, fixing the outdoor unit on a raised platform as per manufacturers recommendation and fixing of room (fan coil) unit on wall, standard 4 m distance refrigerant copper piping with 13mm nitrile rubber insulation, providing and making interconnection between room & condenser as per site conditions, comprising of 1" dia drain PVC pipe with insulation 4m, canvas connections, full electrical cabling from power plug near indoor unit and to outdoor unit, ODU MS stand, first charge refrigarant gas, suitable stabilizer etc complete as required. |  |  |  |  |
| 4.1 | 2 TR 4 star rated as per BEE | Each | 2 |  |  |
| 4.2 | 1.5 TR 5 star rated as per BEE | Each | 2 |  |  |
| 5 | Supply, Laying and Fixing of 4C 4Sq.mm size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Aluminium conductor cable conforming to IS 7098 (Part 1) amended upto date with brass compression glands on surface/ cable tray/ wall / build in trench etc as required from the Indoor to outdoor units of all units for control wiring. | RM | 40 |  |  |
| 6 | Supply, installation, testing and commissioning PVC drain pipe of 25mm dia ISI marked, connecting the drain lines from the indoor units to floor sump, with 9mm nitrile rubber insulation as per specification | RM | 43 |  |  |
| 7 | Supply and fixing Heater package with Humidistat and contactor for humidity control | No | 3 |  |  |
|  | TOTAL FOR PART A |  |  |  |  |
| PART B | AIR DISTRIBUTION |  |  |  |  |
| 8 | Supply, installation, testing and commissioning of factory fabricated rectangular GSS sheet metal ducting for Supply/return/fresh air duct/collar connecting to indoor unit as per ducting specifications and with suitable supports using MS angles, channels, rods, anchor bolts, etc to roof /truss as per IS 655 and as per specifications. |  |  |  |  |
| 8.1 | 20 G | SQM | 5 |  |  |
| 8.2 | 22 G | SQM | 20 |  |  |
| 8.3 | 24 G | SQM | 379 |  |  |
| 9 | SITC of External thermal insulation on supply air ducts using min 12mm thick nitrile rubber class "O" closed cell type with antimicrobial protection as per specifications | SQM | 322 |  |  |
| 10 | Supply, installation, testing and commissioning of Acoustic duct lining using 10mm nitrile rubber insulation open cell type inside the ducts, antimicrobial protection at the outlets of all indoor units upto 4m distance from fan outlet as per spec provided. | SQM | 25 |  |  |
| 11 | Supply, fabrication, installation, testing of flexible connections made out of fire resistant flexible double canvas sleeve. | Set | 2 |  |  |
| 12 | Supply, installation, testing and comissioning of Powder coated extruded aluminimum Continuous grilles 16mm frame, 15deg deflection for supply / return air 150mm wide as per spec | SQM | 6 |  |  |
| 13 | SITC of Powder coated extruded aluminimum supply air diffusers 4 way both side coated with collar damper aluminuim extruded black anodized . (300mmX300mm/600mmx600mm) | SQM | 2 |  |  |
| 14 | SITC of Powder coated extruded aluminium return air diffusers 4 way both side coated without VCD.(300mmX300mm/600mmx600mm) | SQM | 2 |  |  |
| 15 | SITC of Fire Control Damper made of 16G GSS sheet blade and frame with 165mm casing, heavy duty interlocking blades and fuly enclosed bade linkage mechanism, SS lateral seal blade seals, self lubricating sintered bronze bushes, fire rating as per UL555-1995 tested as per BS-476 part 20 with 18G extended sleeve 450mm and with fusible link, spring mechanism control panel temp sensor, smoke sensor, limit swith with lever for auto shut off in case of fire/smoke as per specifications. | SQM | 1 |  |  |
| 16 | SITC of multi blade type volume control dampers made of extruded auminium for ducts/ collars to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distributions system in main ducts, return ducts & other area as per specification. | SQM | 3 |  |  |
| 17 | SITC of Fresh air GI louvers of size 350x350 mm with wire mesh and birds screen for IDUs/AHUs as per specifications. | SQM | 3 |  |  |
| 18 | Supply and fixing of Terminal HEPA Filters having filtering efficiency of 99.7% down to 0.3 microns with aluminum frame works, suitable for fixing in the Supply air plenum boxes |  |  |  |  |
| 18.1 | 610 x 610 x305 | Nos | 12 |  |  |
| 18.2 | 450 x 450 x305 | Nos | 2 |  |  |
| 19 | SITC of Plenum box made of 18G GI sheet with frame work for fixing HEPA filters at terminals and provision of access door for removing the HEPA Filters for cleaning and replcaement .The size shall be to suit |  |  |  |  |
| 19.1 | 610 x 610 x305 mm | Nos | 12 |  |  |
| 19.2 | 450 x 450 x305 mm | Nos | 2 |  |  |
| 20 | Supply installation testing and balancing of continous Perforated Stainless Steel Grilles for supply and return air grilles in accordance with the approved shop drawings size 610 x 610 mm & 450 x 450 mm | SQM | 8 |  |  |
| 21 | Supply fabrication & erection of 24G aluminium cladding for exposed ducting with necessary fittings, sealants etc | SQM | 259 |  |  |
| 22 | SITC of Iso wall boxing for AHU's at terrace with double skinned preinsulated sheet with prepainted galvanized Aluminium sheet 24G on both sides, 60mm PUF insulation density not less than 38kg/m3, CFC/HCFC free, water and air tight, sealants, access door for maintenance, necessary channels, self and floor supports, rigid construction etc complete as per specification | SQM | 164 |  |  |
| 23 | Supply, installation, testing and comissioning of Inline Centrifugal duct fan with dynamically balanced impeller of 700cfm capacity, min 15 mm static , complete with GI box, with single phase direct driven motor with class B, IP44 protection with an internal automatic safety thermal overload protection, dynamically balanced impeller of following capacity, with an operating sound level of less than 55dB at 3 m distance. | Nos | 1 |  |  |
|  | TOTAL FOR PART B |  |  |  |  |
|  | Grand Total |  |  |  |  |

| Providing laminar Flow Air-conditioners at THQH Thodupuzha, Idukki District. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Sl No. | Description of item | Unit | Qty | Rate (in words and figures) | Amount |
| 1 | S/F 40A Metal Clad FP Switch disconnector (Isolator) on wall: Supply and fixing 40A Metal clad FP Switch disconnector, ISI marked in sheet steel enclosure, outdoor type, IP56, mounted on suitable angle iron frame work / directly to wall, giving connection, testing and commissioning etc complete as required. | Each | 3 |  |  |
| 2 | S/F 63A Metal Clad FP Switch disconnector Isolator on wall: Supply and fixing 63A Metal clad FP Switch disconnector, ISI marked in sheet steel enclosure, outdoor type, IP56, mounted on suitable angle iron frame work / directly to wall, giving connection, testing and commissioning etc complete as required. | Each | 3 |  |  |
| 3 | Supply of Aluminium cable. Supply of the following size 1.1kV grade XLPE insulated PVC sheathed, armoured Aluminium conductor power cable confirming to IS 7098 (part 1) ammended upto date including transporting and stacking charges at work site.. |  |  |  |  |
| 3.1 | 4 x 10 Sq mm | m | 60 |  |  |
| 3.2 | 4 x 16 Sq mm | m | 100 |  |  |
| 3.3 | 3.5 x 25 Sq mm | m | 20 |  |  |
| 3.4 | 3.5 x 240 Sq mm | m | 96 |  |  |
| 4 | Supply, Installation, Testing & Commissioning of AC panel, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP42, free standing, floor mounting, dust and vermin proof, powder coated, indoor, compartmentalised, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system, including internal wiring with suitable size wires, spreaders, 3mm thick gland plate, hinged type door with neoprene gasket etc. The panel shall include supply & installation of following switchgears, metering instruments and accessories as per specification. |  |  |  |  |
|  | Incomer |  |  |  |  |
|  | 1 No. 250A, TP, MCCB with neutral link, adjustable thermal & magnetic setting, 415V, 36kA , 50Hz unit complete with extended terminals and spreader links etc as required. |  |  |  |  |
|  | Busbar |  |  |  |  |
|  | 1 Set of 300A TPN busbars of high conductivity electrolytic quality Aluminium alloy. |  |  |  |  |
|  | 1 Set of 25 x 3 mm copper busbars of high conductivity electrolytic quality shall be provided throught out the panel for its earthing. |  |  |  |  |
|  | Instruments |  |  |  |  |
|  | 1 Set of phase indicating lamps, LED type, RYB. |  |  |  |  |
|  | 1 Set of 2A 10kA C curve SP control MCB |  |  |  |  |
|  | (0-500)V voltmeter, Acc. class 1 with 90 deg defl. scale - 1 no. |  |  |  |  |
|  | Volmeter selector switch - 1 no. |  |  |  |  |
|  | (0-250)A ammeter Acc. class 1 with 240 deg defl. Scale - 1 no. |  |  |  |  |
|  | Ammeter selector switch - 1 no. |  |  |  |  |
|  | 250/5A 10VA class 1 resin cast CT - 3 set |  |  |  |  |
|  | Outgoing |  |  |  |  |
|  | 1 Nos. 100A, TPN, AC23, 415V Switch disconnector fuse unit. |  |  |  |  |
|  | 4 Nos. 63A, TPN, AC23, 415V Switch disconnector fuse unit. |  |  |  |  |
|  | 4 Nos. 32A, TPN, AC23, 415V Switch disconnector fuse unit. |  |  |  |  |
|  | 3 Nos 100A Din type HRC fuse |  |  |  |  |
|  | 12 Nos 63A Din type HRC fuse |  |  |  |  |
|  | 9 Nos 32A Din type HRC fuse | Set | 1 |  |  |
| 5 | Supply and fixing FP sheet steel enclosure, IP56, on surface / recess along with 40/63 amps 415 Volts "C" curve FP MCB complete with connections, testing & commissioning etc as required. | nos | 6 |  |  |
| 6 | Supply & fixing glass framed standard shock treatment chart in three different languages. | Job | 1 |  |  |
| 7 | Supply & fixing of fire retardant/extinguishing electrical insultated synthetic mat of 2.0mm thick, +/- 10% confirming to BIS: DOC No. ET-02 (5440) meeting requirements of IS:15652:2006 (with upto date amendment), suitable for all voltages not exceeding 3.3kV and having minimum width of 1000mm +/- 20mm and including supply of required quantity of adhensive / compound and fixing the same at site as per site requirement. | sqm | 2 |  |  |
| 8 | Power plug wiring in PVC conduit ( 2x4 sq mm ): Wiring for light/ power plug with 2x4 sq. mm FR PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 1 No 4 sq. mm FR PVC insulated copper conductor single core cable for loop earthing as required. | m | 40 |  |  |
| 9 | Power plug wiring in PVC conduit ( 4x4 sq mm ): Wiring for power plug with 4x4 sq. mm FR PVC insulated copper conductor single core cable in surface/ recessed medium class PVC conduit alongwith 2 Nos 4 sq. mm FR PVC insulated copper conductor single core cable for loop earthing as required. | m | 60 |  |  |
| 10 | Circuit Sub main wiring in PVC Conduit: Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FR PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required |  |  |  |  |
| 10.1 | 4 x 6 sq. mm + 2 x 6 sq. mm earth wire | m | 45 |  |  |
| 11 | S/F PVC conduit:Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. |  |  |  |  |
| 11.1 | 20 mm | m | 40 |  |  |
| 11.2 | 25 mm | m | 100 |  |  |
| 12 | S/F Vertical Type TP MCB DB: Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 amps tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's (but without MCB's and incomer ) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.) |  |  |  |  |
| 12.1 | 4 way (4 + 12), Double door | Each | 1 |  |  |
| 13 | S/F 'C' series, MCB: Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  |  |
| 13.1 | Single pole | Each | 2 |  |  |
| 13.2 | Triple pole | Each | 2 |  |  |
| 14 | S/F S P MCB blanking plate: Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | Each | 12 |  |  |
| 15 | S/F FP MCB Isolator: Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. |  |  |  |  |
| 15.1 | 40 amps | Each | 3 |  |  |
| 15.2 | 63 amps | Each | 3 |  |  |
| 16 | S/F DP MCB with Enclosure: Supplying and fixing DP sheet steel enclosure on surface/ recess along with 25/32amps 240 volts "C" curve DP MCB complete with connections, testing and commissioning etc. as required. | each | 3 |  |  |
| 17 | S/F TP MCB with Enclosure: Supplying and fixing TP sheet steel enclosure on surface/ recess along with 16/25/32amps 415 volts "C" curve TP MCB complete with connections, testing and commissioning etc. as required. | each | 3 |  |  |
| 18 | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | Each | 2 |  |  |
| 19 | G.I.Earth plate Electrode with Salt & Charcoal: Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | Set | 2 |  |  |
| 20 | Supplying and laying 6 SWG G.I. wire in ground: Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including connection/ termination with GI thimble etc. as required. | m | 100 |  |  |
| 21 | Supplying and laying 25 mm X 5 mm G.I strip in ground: Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | m | 20 |  |  |
| 22 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess: Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | m | 1 |  |  |
| 23 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess: Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | m | 30 |  |  |
| 24 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess: Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | m | 200 |  |  |
| 25 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. |  |  |  |  |
| 25.1 | Upto 35 sq. mm (clamped with 1mm thick saddle) | Metre | 120 |  |  |
| 25.2 | Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | Metre | 60 |  |  |
| 26 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. |  |  |  |  |
| 26.1 | Upto 35 sq. mm (clamped with 1mm thick saddle) | Metre | 80 |  |  |
| 26.2 | Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | Metre | 50 |  |  |
| 27 | Supplying and fixing cable route marker with 10 cm X 10 cm X 5 mm thick G.I. plate with inscription there on, bolted /welded to 35 mm X 35 mm X 6 mm angle iron, 60 cm long and fixing the same in ground as required. | each | 6 |  |  |
| 28 | Supplying and making end termination with brass compression gland and aluminium lugs: Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. |  |  |  |  |
| 28.1 | 3½ X 25 sq. mm (28mm) | Each | 2 |  |  |
| 28.2 | 3½ X 240 sq. mm (62mm) | Each | 2 |  |  |
| 28.3 | 4 X 10 sq. mm (25mm) | Each | 6 |  |  |
| 28.4 | 4 X 16 sq. mm (28mm) | Each | 6 |  |  |
|  | Total Electrical |  |  |  |  |
|  | Total Laminar Flow Air Conditioner |  |  |  |  |
|  | Grand Total |  |  |  |  |